## site_tech_info
Site Name | PV Capacity (W) | PV Inverter Size (kW) | Battery Size (Wh) | Battery Name | Battery Inverter/Hybrid Size | Generator Size | Genset/Grid set point kit | Country | Province | Location | Meter | Contract Type | Business Type | Operational Satus | Sales Type | Investment Party | Project Number | Commisioned Date | Installer Name | Platform | Offtake Guarantee | Age | Soiling Intensity | Shading | Power Limit
21 Melrose | 14000 | 36 | 35808 | Sunsynk | 3x12kW | None | None | South Africa | Gauteng | 21 Melrose St Melrose | N/A | RTO | Residential | Reduced Demand |  | Anuva | P00062 | 2023-02-06 | SA Energy | Sunsynk | NO | 3.7207 | Low | Low | Zero Export
African Global Plastics | 178000 | 160 | 0 | N/A | N/A | None | None | South Africa | Gauteng | 1st St & 11th road, Kew, Sandton, 2090 | Alester Meter | PPA | Manufacture | Producing |  | SSI | P00008 | 2023-09-27 | SA Energy | mypower24 | NO | 3.0828 | Medium | Low | Zero Export
Alpine Heath Residential | 36000 | 33 | 0 | N/A | N/A | None | None | South Africa | KZN | Busingatha, South Africa | Eastron Meter | PPA | Residential | Reduced Demand |  | 12B Fund | null | 2025-01-01 | SA Energy | isolarCloud | YES | 1.8179 | Low | Low | Zero Export
Alpine Heath Resort | 217000 | 220 | 0 | N/A | N/A | N/A | N/A | South Africa | KZN | Busingatha, South Africa | Eastron Meter | PPA | Residential | Producing |  | 12B Fund | null | 2026-04-28 | SA Energy | IsolarCloud | YES | 0.49829 | Low | Low | Zero Export
Bendstore Plaza Shops | 110000 | 110 | 0 | N/A | N/A | N/A | N/A | South Africa | Limpopo | Stand 87, Bendstore Plaza, Giyani Main Rd, Giyani-BA, Giyani, 0832 | null | PPA | Retail | Reduced Demand |  | Anuva | P00072 | 2022-12-13 | SA Energy | null | NO | 3.8713 | Low | Unknown | Zero Export
Bendstore Spar | 400000 | null | 0 | N/A | N/A | null | null | South Africa | Limpopo | null | null | PPA | Retail | Producing |  | Anuva | null | 2023-12-12 | SA Energy | null | NO | 2.8747 | Low | Unknown | Zero Export
Beyerskloof | 78000 | null | 0 | N/A | N/A | null | null | South Africa | Western Cape | Koelenhof Street, R304, Koelenhof, Stellenbosch, 7600 | null | PPA | Manufacture | Reduced Demand |  | SSI | null | 2023-12-12 | Solar Synergy | null | NO | 2.8747 | Low | Low | Zero Export
BP Parys | 544000 | 50 | 0 | N/A | N/A | N/A | N/A | South Africa | Free state | 63 Bree St, Parys, 9585 | Eastron Meter | RTO | Retail | Reduced Demand |  | SSI | null | 2024-11-14 | SA Energy | null | NO | 1.9493 | Low | Unknown | Zero Export
Buffalo Rock | 15000 | N/A | 57200 | null | 2x12kW | N/A | N/A | South Africa | Mpumalanga | Hazyview Ehlanzeni District Municipality MP | null | RTO | Residential | Reduced Demand |  | SSI | P00054 | 2023-09-14 | SA Energy | Sunsynk | NO | 3.1184 | Low | Unknown | Zero Export
Checkers De Aar | 154000 | 125 | 0 | N/A | N/A | N/A | NuVo | South Africa | Northern Cape | 21 Alexander St, De Aar, 7000, South Africa |  | PPA | Retail | Producing |  | 12B Fund | P00038 | 2024-06-06 | SA Energy | iSolarCloud & NuVo | NO | 2.3901 | Low | Low | Zero Export
Checkers Lichtenburg | 161000 | 150 | 0 | N/A | N/A | N/A | N/A | South Africa | North West | 33 Nelson Mandela Dr, Lichtenburg, 2740 | Eastron Meter | PPA | Retail | Producing |  | SSI | null | 2026-04-17 | SA Energy | IsolarCloud | NO | 0.52841 | Unknown | Low | Zero Export
Checkers Silverlakes Gen | 152000 | 125 | 0 | N/A | N/A | 500 | Nuvo | South Africa | Gauteng | Chamberlain Shopping Cntr (Six Fountains Cnr Solomon Mahlangu Dr, Bendeman Blvd, &, Pretoria, 0081 | Eastron Meter | PPA | Retail | Producing |  | 12B Fund | null | 2025/02/29 | SA Energy | isolarCloud | NO |  | Low | Low | Zero Export
Checkers Silverlakes No Gen | 142000 | 125 | 0 | N/A | N/A | N/A | N/A | South Africa | Gauteng | Chamberlain Shopping Cntr (Six Fountains Cnr Solomon Mahlangu Dr, Bendeman Blvd, &, Pretoria, 0081 | Eastron Meter | PPA | Retail | Producing |  | 12B Fund | null | 2025/02/29 | SA Energy | isolarCloud | NO |  | Low | Low | Zero Export
Checkrite Inanda | 70000 | 66 | 0 | N/A | N/A | N/A | N/A | South Africa | Gauteng | 6th Ave, Springs New, Springs, 1560 | null | PPA | Retail | Producing |  | 12B Fund | P00056 | 2024-06-28 | SA Energy | iSolarCloud | YES | 2.3299 | Low | Low | Zero Export
Club Houghton | 60000 | N/A | 84000 | N/A | 6x12kW Sunsynk Inverters | N/A | null | South Africa | Gauteng | Osborn Rd, Houghton Estate, Johannesburg, 2198, South Africa | N/A | PPA | Residential | Reduced Demand |  | Anuva | P00067 | 2022-04-14 | SA Energy | Sunsysnk;SolarMd | NO | 4.5366 | Low | Low | Zero Export
Coldstar International | 41000 | 36 | 0 | N/A | N/A | N/A | N/A | South Africa | KZN | Coldstar International, 3 Rana Rd, Isipingo Rail, Isipingo, 4110 ¦ client miss use data | N/A | PPA | Commercial | Reduced Demand |  | Anuva | P00051 | 2022-03-23 | SA Energy | iSolarCloud | NO | 4.5969 | Low | Low | Exporting
Cultura Fresh | 65000 | 110 | 171600 | Atess | ATESS PCS250 | N/A | null | South Africa | Western Cape | null | null | PPA | Agricultural | Reduced Demand |  | 12B Fund | null | 2024-08-05 | Solar Synergy | null | NO | 2.2259 | Low | Low | Zero Export
Demco | 235000 | 220 | 0 | N/A | N/A | N/A | N/A | South Africa | Gauteng | Industries East, 12 -14 Moller Street, Germiston. 1401 | Alester Meter | PPA | Manufacture | Reduced Demand |  | 12B Fund | P00035 | 2024-06-17 | SA Energy | iSolarCloud | YES | 2.36 | Low | Low | Zero Export
Engen Kaalfontein | 114070 | 125 | 0 | N/A | N/A | N/A | N/A | South Africa | Gauteng | 3117 Angelfish St, Kaalfontein, Midrand, 1632 | Eastron Meter | PPA | Retail | Producing |  | SSI | null | 2026-05-20 | SA Energy | IsolarCloud | YES | 0.43806 | High | Low | Zero Export
Engen Lotus Gardens | 23010 |  | 0 | N/A | N/A | N/A | N/A | South Africa | Gauteng | 63WC+CQ4 Pretoria | Eastron Meter | PPA | Retail | Producing |  | SSI | null | 2025-10-21 | SA Energy | IsolarCloud | YES | 1.0157 | Low | Low | Zero Export
Giba Gorge Main | 123360 | 160 | 0 | N/A | N/A | N/A | N/A | South Africa | KZN | 5QCJ+XM2 Clifton Canyon, Pinetown Rural | Alester Meter | PPA | Manufacture | Reduced Demand |  | SSI | P00069 | 2021-10-10 | SA Energy | soliscloud | NO | 5.0459 | Low | Low | Zero Export
Giba Gorge Storage | 106000 | null | 0 | N/A | N/A | N/A | null | South Africa | KZN | 5QCJ+XM2 Clifton Canyon, Pinetown Rural | Alester Meter | PPA | Commercial | Reduced Demand |  | SSI | null | 2021-10-10 | SA Energy | SolisCloud | NO | 5.0459 | Low | Low | Zero Export
Golden Spot Resort | 30000 | 33 | 0 | N/A | N/A | N/A | N/A | South Africa | Mpumalanga | HR2M+GQ7 Alkmaar (-25.4487127, 30.8344204) | null | PPA | Residential | Reduced Demand |  | SSI | P00071 | 2023-05-27 | SA Energy | iSolarCloud | YES | 3.4196 | Low | Low | Zero Export
Golden Spot Shops | 30000 | 33 | 0 | N/A | N/A | N/A | N/A | South Africa | Mpumalanga | HR2M+GQ7 Alkmaar (-25.4487127, 30.8344204) | null | PPA | Retail | Producing |  | SSI | P00060 | 2023-05-26 | SA Energy | iSolarCloud | YES | 3.4223 | Low | Low | Zero Export
Grootpan | 170000 | 200 | 491520 | Deye | Daye | N/A | N/A | South Africa | North West | 2G4H+RXQ Ga-Motlatla | N/A | RTO | Agricultural | Reduced Demand |  | SSI | null | 2026-03-05 | OTG 4 U | Deye Cloud | NO | 0.64613 | Low | Low | Zero Export
HB Dunn | 24000 | N/A | 127400 | N/A | 1x50 kW | N/A | N/A | South Africa | Mpumalanga | Kriel Nkangala District Municipality MP | null | RTO | Residential | Reduced Demand |  | SSI | P00045 | 2024-04-25 | SA Energy | Sunsynk | NO | 2.5051 | Low | Low | Zero Export
Helderberg Collage | 223000 | null | 0 | N/A | N/A | N/A | null | South Africa | Western Cape | null | null | PPA | Residential | Producing |  | SSI | null | 2019-08-23 | SA Energy | null | NO | 7.1786 | Low | Low | Zero Export
Hilston Rotoflo | 240000 | 240 | 0 | N/A | N/A | N/A | N/A | South Africa | Gauteng | 28 Hilston Rd, Kya Sand, Randburg, 2163 | null | PPA | Residential | Producing |  | Anuva | P00055 | 2023-05-10 | SA Energy | isolarCloud | YES | 3.4661 | Low | Low | Zero Export
Huis Herfsblaar | 215000 | 220 | 0 | N/A | N/A | N/A | N/A | South Africa | Gauteng | Edging Pretoria, 1244 Webb Rd, Queenswood, Pretoria, 0186, South Africa | Eastron Meter | PPA | Commercial | Producing |  | 12B Fund | P00034 | 2024-06-20 | SA Energy | iSolarCloud | YES | 2.3518 | Low | Low | Zero Export
IPID - Floor 4 | 54740 | null | 0 | N/A | N/A | N/A | N/A | South Africa | Gauteng | 7633+M46 Pretoria | Eastron Meter | PPA | Commercial | Producing |  | SSI | null | 2025-10-04 | SA Energy | IsolarCloud | YES | 1.0623 | Low | Low | Zero Export
IPID - Floor 6 | 47600 | null | 0 | N/A | N/A | N/A | N/A | South Africa | Gauteng | 7633+M46 Pretoria | Eastron Meter | PPA | Commercial | Producing |  | SSI | null | 2025-10-04 | SA Energy | IsolarCloud | YES | 1.0623 | Low | Low | Zero Export
Kool Village | 79000 | null | 0 | N/A | N/A | N/A | null | South Africa | Northern Cape | Kool Village, 89 Virginia Way, Virginia, 9430 | null | null | Commercial | Producing |  | Anuva | null | 2022/16/12 | SA Energy | null | NO |  | Low | Low | Zero Export
Makalali | 120000 | null | 171600 | N/A | 250 | N/A | N/A | South Africa | Limpopo | Makalali game reserve Road D202 Harmony Block 33, Gravelotte |  |  | Agriculural | Reduced Demand |  | SSI | null | 2023-05-04 | SA Energy |  |  | 3.4825 | Low | Low | Zero Export
Mambha Cash & Carry | 184000 | null | 0 | N/A | N/A | N/A | null | South Africa | KZN | null | null | PPA | Retail | Producing |  | Anuva | P00015 | 2022-11-14 | SA Energy | mypower24 | NO | 3.9507 | High | Low | Zero Export
Mathe Group Company | 518000 | 440 | 0 | N/A | N/A | N/A | N/A | South Africa | KZN | 4/160 Buckman Blvd, Cato Ridge, 3699, South Africa | null | PPA | Manufacture | Producing |  | Anuva | P00059 | 2022-05-11 | SA Energy | iSolarCloud |  | 4.4627 | Low | Low | Zero Export
Mdluli | 114000 | null | 457600 | N/A | N/A | N/A | null | South Africa | Mpumalanga | Makoko, South Africa,1251 | null | PPA | Residential | Reduced Demand |  | 12B Fund | P00083 | 2024-04-17 | SA Energy | mypower24&IsolarCloud | YES | 2.527 | Low | Low | Zero Export
Medipost | 330000 | null | 0 | N/A | N/A | N/A | N/A | South Africa | Western Cape | 593 Nico Smith St, Gezina, Pretoria, 0084 | Eastron Meter | PPA | Commercial | Producing |  | 12B Fund | null | 2025-02-25 | SA Energy | null |  | 1.6674 | Low | Low | Zero Export
Meredale Heights | 33000 | 33 | 0 | N/A | N/A | N/A | N/A | South Africa | Gauteng | 40 thomas street | null | PPA | Residential | Producing |  | Anuva | P00052 | 2023-11-18 | SA Energy | iSolarCloud | YES | 2.9405 | Low | Low | Zero Export
Monument Park Checkers | 281000 | 250 | 0 | N/A | N/A | N/A | NuVo | South Africa | Gauteng | 242 Voortrekker Rd, Monument, Krugersdorp, 1739, South Africa | null | PPA | Retail | Producing |  | Anuva | P00037 | 2024-02-29 | SA Energy | isloarcloud &Nuvo | NO | 2.6585 | Low | Low | Zero Export
Nkambeni Industrial | 158400 | 125 | 0 | Solar MD | Atess PCS500 | N/A | null | South Africa | Mpumalanga | 139 Numbi Rd Numbi Gate Kruger National Park, Hazyview, 1350 | null | RTO | Residential | Reduced Demand |  | SSI | P00040 | 2023-09-13 | SA Energy | null | NO | 3.1211 | Low | Low | Zero Export
Olievenhoutbosch 1 | 300000 | null | 0 | N/A | N/A | N/A | N/A | South Africa | Gauteng | 33WW+C5W Centurion | Eastron Meter | PPA | Retail | Producing |  | SSI | null | 2025-09-24 | SA Energy | IsolarCloud | YES | 1.0897 | High | Low | Zero Export
Olievenhoutbosch 2 | 70000 | null | 0 | N/A | N/A | N/A | N/A | South Africa | Gauteng | 33WW+C5W Centurion | Eastron Meter | PPA | Retail | Producing |  | SSI | null | 2025-09-24 | SA Energy | IsolarCloud | YES | 1.0897 | High | Low | Zero Export
Opal Students | 35000 | 33 | 0 | N/A | N/A | N/A | N/A | South Africa | Gauteng | Opal students | null | RTO | Retail | Producing |  | Anuva | P00057 | 2023-09-05 | SA Energy | iSolarCloud | YES | 3.1431 | Low | Low | Zero Export
Orthochem Bethlehem | 220000 | null | 0 | N/A | N/A | N/A | null | South Africa | Free state | 6 Sauer Street Bethlehem Free State 9700 | null | PPA | Manufacture | Producing |  | SSI | P00063 | 2023-06-24 | SA Energy | isolarcloud, & NuVO | NO | 3.3429 | Low | Low | Zero Export
Plastiplate | 66000 | 66 | 0 | N/A | N/A | N/A | N/A | South Africa | Gauteng | 6 adderley, Roodepoort, 1724, South Africa | null | PPA | Manufacture | Producing |  | Anuva | P00061 | 2022-05-07 | SA Energy | iSolarCloud | YES | 4.4736 | Low | Low | Zero Export
PNB Unlimited | 95000 | null | 0 | N/A | N/A | N/A | null | South Africa | North West | 8X4H+VXW Amaoti | null | PPA | Commercial | Producing |  | SSI | null | 2020-11-26 | SA Energy | null | NO | 5.9165 | Low | Low | Zero Export
Q-lity Meat | 35000 | 30 | 0 | N/A | N/A | N/A | NuVo | South Africa | Gauteng | null | null | PPA | Retail | Producing |  | SSI | P00007 | 2023-06-15 | SA Energy | isloarcloud &Nuvo | NO | 3.3676 | Low | Low | Zero Export
Quintondale | 40000 | 33 | 0 | N/A | N/A | N/A | N/A | South Africa | Gauteng | 43 Orchards Street, Johannesburg, Johannesburg, Gauteng 2192, South Africa | null | PPA | Residential | Reduced Demand |  | SSI | P00065 | 2022-04-12 | SA Energy | null | NO | 4.5421 | Low | Low | Zero Export
Riverside Lodge | 110000 | 100 | 0 | N/A | N/A | N/A | N/A | South Africa | North West | Hartbeespoort, South Africa | null | PPA | Residential | Producing |  | Anuva | P00053 | 2023-05-12 | SA Energy | iSolarCloud | YES | 3.4606 | Low | Low | Zero Export
Roan Foods | 127440 | 100 | 246000 | Deye | Deye | N/A | N/A | Zambia | Lusaka | J8VC+WPJ, Lusaka, Zambia | N/A | RTO | Retail | Producing |  | SAWA | null | 2026-04-02 | Dorman Energy | Deye Cloud | NO | 0.56947 | Unknown | Low | Zero Export
Sakhumnotho | 38000 | 30 | 0 | N/A | N/A | N/A | N/A | South Africa | Gauteng | R3W5+96X Johannesburg | null | PPA | Commercial | Decommissioned |  | SSI | P00043 | null | SA Energy | null | NO |  | Low | Low | Zero Export
SaveMore Alldays - Store | 180000 | 100 | 0 | N/A | N/A | N/A | N/A | South Africa | Limpopo | R572, Alldays, 0909 | null | PPA | Retail | Reduced Demand |  | SSI | P00050 | 2023-07-03 | SA Energy | soliscloud | NO | 3.3183 | Low | Low | Zero Export
Savemore Liquor Alldays | 27300 | 30 | 0 | N/A | N/A | N/A | N/A | South Africa | Limpopo | 84C3+PG2 Alldays | null | PPA | Retail | Reduced Demand |  | SSI | null | 2023-07-04 | SA Energy | soliscloud | NO | 3.3155 | Low | Low | Zero Export
Saverite Durban | 95000 | null | 0 | N/A | N/A | N/A | null | South Africa | KZN | null | null | PPA | Retail | Producing |  | Anuva | null | 2023-07-04 | SA Energy | null | NO | 3.3155 | Low | Low | Zero Export
Saverite PMB | 96000 | null | 0 | N/A | N/A | N/A | null | South Africa | KZN | 457 Langalibalele St, Pietermaritzburg, 3200 | null | PPA | Retail | Producing |  | SSI | null | 2020-11-24 | SA Energy | null | NO | 5.922 | Low | Low | Zero Export
Secunda Plaza Choppies | 121000 | 110 | 0 | N/A | N/A | N/A | N/A | South Africa | Mpumalanga | 8337 Pichlerplien, Secunda, 2302, South Africa | null | PPA | Retail | Reduced Demand |  | SSI | P00076 | 2022-07-28 | SA Energy | iSolarCloud | NO | 4.2491 | Low | Low | Zero Export
Secunda Plaza Shops | 35000 | 33 | 0 | N/A | N/A | N/A | N/A | South Africa | Mpumalanga | 8309 Louwrens Muller St, Secunda, 2302, South Africa | null | PPA | Retail | Reduced Demand |  | SSI | P00075 | 2022-07-28 | SA Energy | iSolarCloud | NO | 4.2491 | Low | Low | Zero Export
Shoprite Dube | 153000 | 125 | 0 | N/A | N/A | N/A | N/A | South Africa | Gauteng | Shoprite Maponya Center, 1980 Mahalefele Rd, Dube, Soweto, 1801 | Eastron Meter | PPA | Retail | Producing |  | 12B Fund | null | 2025-01-09 | SA Energy | isolarCloud | NO | 1.796 | Low | Low | Zero Export
Shoprite Ekhaya | 175680 | 150 | 0 | N/A | N/A | N/A | N/A | South Africa | Mpumalanga | Ekhaya Mall, R546, Evander, 2285 | Eastron Meter | PPA | Retail | Producing |  | SSI | null | 2026-02-15 | SA Energy | IsolarCloud | NO | 0.69541 | Unknown | Low | Zero Export
Shoprite Hillbrow | 126000 | null | 0 | N/A | N/A | 500kVa | NuVo | South Africa | Gauteng | null | Eastron Meter | PPA | Retail | Producing |  | 12B Fund | null | 2024-10-25 | SA Energy | null | NO | 2.0041 | Low | High | Zero Export
Shoprite Ladybrand | 250000 | 110 | 0 | N/A | N/A | N/A | N/A | South Africa | Free state | 248 Voortrekkers Ave, CBD, Ladybrand, 9745, South Africa | Eastron Meter | PPA | Retail | Producing |  | 12B Fund | null | 2024-09-23 | SA Energy | null | NO | 2.0917 | Low | Low | Zero Export
Shoprite Mayfair | 132680 | 125 | 0 | N/A | N/A | N/A | N/A | South Africa | Gauteng | 1804 Albertina Sisulu Rd, Mayfair, Johannesburg, 2092 | Eastron Meter | PPA | Retail |  |  | SSI | null | 2026-08-17 | SA Energy | IsolarCloud | NO | 0.19439 | Unknown | Low | Zero Export
Shoprite Mini Ganyesa | 240000 | 110 | 0 | N/A | N/A | N/A | NuVo | South Africa | North West | Hartbeespoort, South Africa | Eastron Meter | PPA | Retail | Producing |  | 12B Fund | P00078 | 2024-08-27 | SA Energy | isloarcloud &Nuvo | NO | 2.1656 | Low | Low | Zero Export
Shoprite Naledi | 125000 | 125 | 0 | N/A | N/A | 500 | NuVo | South Africa | Gauteng | PRVC+MPW Soweto | Eastron Meter | PPA | Retail | Producing |  | 12B Fund | null | 2024-09-05 | SA Energy | Sunsynk | NO | 2.141 | High | Low | Zero Export
Shoprite Newlands | 200000 | null | 0 | N/A | N/A | N/A | N/A | South Africa | KZN | Newlands City Centre, 2 Marble Ray Drive, New Dawn Park, Durban, 4037 | Eastron Meter | PPA | Residential | Producing |  | SSI | null | 2025-12-01 | SA Energy | null | NO | 0.90349 | Low | Low | Zero Export
Shoprite SRH Bizana | 148800 | 150 | 0 | N/A | N/A | N/A | N/A | South Africa | Eastern Cape | 4VR3+G6F Mbizana | Eastron Meter | PPA | Retail | Producing |  | SSI | null | 2026-07-17 | SA Energy | IsolarCloud | NO | 0.27926 | Unknown | Low | Zero Export
Shoprite Thokoza | 115000 | 125 | 0 | N/A | N/A | N/A | N/A | South Africa | Gauteng | 9102 Khumalo St, Thokoza, 1426 | Eastron Meter | PPA | Retail | Producing |  | 12B Fund | null | 2025-04-01 | SA Energy | IsolarCloud | NO | 1.5715 | High | Low | Zero Export
Spring Glade | 116000 | 110 | 0 | N/A | N/A | N/A | N/A | South Africa | Gauteng | VR7R+269 Roodepoort | Alester Meter | PPA | Residential | Reduced Demand |  | SSI | null | 2021-12-02 | SA Energy | SolisCloud | NO | 4.9008 | Low | Low | Zero Export
SR Morula TF 1 | 57000 | 50 | 0 | N/A | N/A | N/A | N/A | South Africa | Gauteng | 8408 Mangope Rd, Mabopane Unit M, Mabopane, 0190, South Africa | Eastron Meter | PPA | Retail | Producing |  | SSI | P00091 | 2025-08-20 | SA Energy | IsolarCloud | YES | 1.1855 | High | Low | Zero Export
SR Morula TF 1 - Shoprite | 177000 | 125 | 0 | N/A | N/A | N/A | N/A | South Africa | Gauteng | 8409 Mangope Rd, Mabopane Unit M, Mabopane, 0190, South Africa | Eastron Meter | PPA | Retail | Producing |  | 12B Fund | P00091 | 2025-08-20 | SA Energy | IsolarCloud | NO | 1.1855 | High | Low | Zero Export
SR Morula TF 2 | 57000 | 50 | 0 | N/A | N/A | N/A | N/A | South Africa | Gauteng | 8410 Mangope Rd, Mabopane Unit M, Mabopane, 0190, South Africa | Eastron Meter | PPA | Retail | Producing |  | 12B Fund | P00091 | 2025-08-20 | SA Energy | IsolarCloud | YES | 1.1855 | High | Low | Zero Export
Thakadu Industrial | 61600 | null | 289000 | N/A | N/A | N/A | null | South Africa | North West | D53 Thakadu Gate, Madikwe Game Reserve Molatedi, 2838 | null | PPA | Residential | Reduced Demand |  | SSI | null | 2023-11-17 | SA Energy | null | NO | 2.9432 | Low | Low | Zero Export
The Alec | 55000 | 50 | 0 | N/A | N/A | N/A | NuVo | South Africa | Gauteng | 48 Goldreich St, Hillbrow, Johannesburg, 2198, South Africa | null | PPA | Residential | Reduced Demand |  | Anuva | null | 2023-05-22 | SA Energy | isolarCloud | YES | 3.4333 | Low | Low | Zero Export
Three Peaks | 40000 | 33 | 0 | N/A | N/A | N/A | N/A | South Africa | KZN | 22A Underwood Rd, Hatton Estate, Pinetown, 3610 |  | PPA | Residential | Reduced Demand |  | Anuva | P00064 | 2022-02-25 | SA Energy | iSolarCloud | NO | 4.668 | Low | Low | Exporting
TPF Foods | 34000 | 30 | 0 | N/A | N/A | N/A | null | South Africa | Limpopo | Q2R4+98G Johannesburg | Alester Meter | PPA | Retail | Reduced Demand |  | SSI | null | 2021-06-04 | SA Energy | null | NO | 5.3963 | Low | Low | Zero Export
Trouw Nutrition | 103000 | null | 0 | N/A | N/A | N/A | null | South Africa | Gauteng | null | Alester Meter | PPA | Manufacture | Producing |  | SSI | null | 2021-11-04 | SA Energy | null | NO | 4.9774 | Low | Low | Zero Export
U Save Botrivier | 33000 | 30 | 0 | N/A | N/A | N/A | N/A | South Africa | Western Cape | 3 8th Ave, Bot River, 7185, South Africa | Eastron Meter | PPA | Retail | Reduced Demand |  | SSI | null | 2025-07-23 | SA Energy | IsolarCloud | NO | 1.2621 | Low | Low | Zero Export
Usave Naboomspruit | 29760 | 30 | 0 | N/A | N/A | N/A | N/A | South Africa | Limpopo | 76 Thabo Mbeki St, Mookgophong, 0560 | Eastron Meter | PPA | Retail |  |  | SSI | null | 2026-06-12 | SA Energy | IsolarCloud | NO | 0.37509 | Unknown | Low | Zero Export
Vaal Maseru Klerksdorp | 40000 |  | 0 | Solar MD | Sunsynk | null | null | South Africa | Free state | Cnr of Mikro and Von Wielligh Streets, Klerksdorp | null | PPA | Commercial | Decommissioned |  | SSI | P00044 | null | SA Energy | null | NO |  | Unknown | Unknown | Zero Export
Watt Place Rotoflo | 197000 | 220 | 0 | N/A | N/A | N/A | NuVo | South Africa | Gauteng | 10 Watt Pl, Kya Sand, Randburg, 2163, South Africa | null | PPA | Manufacture | Producing |  | Anuva | P00048 | 2023-05-13 | SA Energy | isolarCloud & Nuvo | YES | 3.4579 | Low | Low | Zero Export
Zwartop Golf Course | 27000 | 33 | 0 | N/A | N/A | N/A | null | South Africa | Gauteng | ZwartKop Golf and Country club, 108 Golf Avenue Club view Centurion 0157 | null | RTO | Residential | Reduced Demand |  | SSI | null | 2023-09-19 | SA Energy | null | NO | 3.1047 | Low | Low | Zero Export
Molapo Crossing Mall | 1113000 | 785 | 480000 | Sigenergy | Sigenergy | N/A | N/A | Botswana | Gaborone | 9V4P+P5J, Gaborone, Botswana | null | PPA | Commercial |  |  | SSI | null |  | Alensys Solar |  |  |  | Unknown | Unknown | Zero Export
Formulas:
Age = IF(ISNUMBER([Commisioned Date]),(TODAY()-[Commisioned Date])/365.25,"")

## Simulated Production
Site Name | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec
21 Melrose | 2634 | 2978 | 2426 | 2082 | 2025 | 1810 | 2016 | 2352 | 2528 | 2675 | 2618 | 2758
African Global Plastics | 26489.3 | 23277.8 | 23704 | 19723.4 | 18790.7 | 16902.6 | 18714.9 | 21796.9 | 24005.1 | 26259.6 | 26494.9 | 27974.1
Alpine Heath Residential | 5335 | 4782 | 5051 | 5133 | 5545 | 5291 | 5201 | 5833 | 5216 | 5258 | 5358 | 5339
Bendstore Plaza Shops | 19132 | 16455 | 18192 | 17513 | 16955 | 15353 | 16159 | 18059 | 18155 | 17437 | 17289 | 19005
Bendstore Spar | 57016.3719 | 49003.6563 | 54154.7445 | 52055.4432 | 50303.5926 | 45493.302 | 47903.1144 | 53629.4475 | 54003.2127 | 51943.2342 | 51542.7573 | 56267.0127
Beyerskloof | 15319 | 12622 | 12090 | 8698 | 6615 | 5740 | 6183 | 7734 | 9940 | 12572 | 14126 | 15421
BP Parys | 9057 | 8039 | 7862 | 6394 | 6027 | 5319 | 5956 | 7070 | 8021 | 8710 | 9102 | 9142
Buffalo Rock | 2447 | 2204 | 2364 | 1964 | 1813 | 1645 | 1792 | 1960 | 2076 | 2112 | 2039 | 2207
Checkers De Aar | 29655 | 22972 | 22328 | 18096 | 15021 | 13183 | 15099 | 19010 | 21674 | 26757 | 28766 | 31103
Checkers Silverlakes Gen | 23450 | 20245 | 20409 | 16782 | 15700 | 14022 | 15558 | 18491 | 20696 | 22782 | 22890 | 24472
Checkers Silverlakes No Gen | 23450 | 20245 | 20409 | 16782 | 15700 | 14022 | 15558 | 18491 | 20696 | 22782 | 22890 | 24472
Checkrite Inanda | 9627 | 9000 | 8673 | 7260 | 6214 | 5622 | 5969 | 7206 | 7683 | 8926 | 8903 | 9497
Club Houghton | 6408 | 5365 | 5459 | 4611 | 4375 | 3848 | 4305 | 5067 | 5593 | 6237 | 6347 | 6697
Coldstar International | 5761.2 | 5289.7 | 5351.3 | 4476.7 | 4144.2 | 3750.5 | 4019 | 4537.7 | 4477.3 | 4986.7 | 5100.4 | 5950.6
Cultura Fresh | 13109 | 11411 | 11746 | 9262 | 7471 | 6511 | 7170 | 8324 | 9849 | 11513 | 12192 | 12923
Demco | 41895 | 35971 | 36483 | 30848 | 29226 | 26233 | 29069 | 34133 | 37890 | 41280 | 41518 | 43833
Engen Lotus Gardens | 2735 | 2556 | 2535 | 2442 | 2474 | 2756 | 2611 | 2800 | 2707 | 2695 | 2618 | 2708
Giba Gorge Main | 16980 | 15556.6 | 15927.6 | 13677.3 | 12351.6 | 11543.6 | 12195.1 | 13528 | 13644.6 | 15166.4 | 15407.4873 | 16842.3723
Giba Gorge Storage | 15179.5 | 13524.8 | 13861.9 | 11789.7 | 10618.3 | 9819.1 | 10486.9 | 11678.3 | 11941.8 | 13277 | 13346.2179 | 14828.6676
Golden Spot Resort | 4492 | 4056 | 4397 | 3644 | 3389 | 3100 | 3383 | 3665 | 3881 | 3899 | 3720 | 3991
Golden Spot Shops | 4020 | 3616 | 4009 | 3292 | 3026 | 2735 | 3002 | 3304 | 3497 | 3533 | 3348 | 3560
HB Dunn | 4706 | 4110 | 4209 | 3538 | 3392 | 3058 | 3366 | 3941 | 4346 | 4559 | 4578 | 4864
Helderberg Collage | 44000.9 | 36738.8 | 35799.5 | 26238.2 | 19947.3 | 16584 | 18638.7 | 23207.5 | 29655.5 | 36694.1 | 41235.3 | 44584.1
Hilston Rotoflo | 32657 | 28530 | 26894 | 23945 | 21446 | 18974 | 21123 | 24633 | 27402 | 30501 | 32028 | 31475
Huis Herfsblaar | 33572 | 29313 | 30629 | 26386 | 25077 | 22476 | 24838 | 29965 | 32045 | 33620 | 32645 | 34688
IPID - Floor 4 | 8415 | 7237.5 | 7601.5 | 6870 | 6583 | 5884 | 6428 | 7317 | 7798.5 | 8310.5 | 8392 | 8239
IPID - Floor 6 | 8415 | 7237.5 | 7601.5 | 6870 | 6583 | 5884 | 6428 | 7317 | 7798.5 | 8310.5 | 8392 | 8239
Kool Village | 13570 | 11745 | 11799 | 10155 | 9548 | 8534 | 9501 | 11108 | 11891 | 13149 | 13477 | 14443
Makalali | 18447.7105 | 16628.9456 | 18150.5395 | 16778.1675 | 16967.8282 | 15742.2304 | 16856.9888 | 18183.8305 | 18093.2594 | 17656.7558 | 17048.0204 | 18068.487
Mambha Cash & Carry | 24713 | 21612 | 21750 | 17547 | 14975 | 13472 | 14555 | 17167 | 18426 | 21592 | 22234 | 24984
Mathe Group Company | 72121 | 65458 | 68264 | 57584 | 52130 | 48157 | 51738 | 57201 | 59213 | 64977 | 66569 | 71854
Mdluli | 17634 | 16473 | 19238 | 17065 | 16886 | 16099 | 17101 | 17348 | 16879 | 15944 | 14731 | 15377
Medipost | 59291 | 48612 | 45479 | 32312 | 23816 | 19426 | 21982 | 28360 | 37091 | 47820 | 55073 | 60151
Meredale Heights | 5957 | 5410 | 5967 | 5723 | 6086 | 5885 | 6334 | 6633 | 6573 | 6461 | 6012 | 6145
Monument Park Checkers | 44907 | 37765 | 39036 | 33226 | 31537 | 28491 | 31513 | 36674 | 40579 | 44092 | 44165 | 47244
Nkambeni Industrial | 23544 | 21677 | 24212 | 20861 | 20012 | 18485 | 20016 | 21052 | 21403 | 20962 | 19856 | 21184
Olievenhoutbosch 1 | 52080 | 45544 | 44433 | 38648 | 35710 | 31508 | 34699 | 40906 | 45309 | 51347 | 51837 | 52952
Olievenhoutbosch 2 | 13744 | 12002 | 11708 | 10193 | 9448 | 8384 | 9230 | 10801 | 11951 | 13545 | 13626 | 13933
Opal Students | 6317 | 5312 | 5484 | 4844 | 4660 | 4243 | 4686 | 5383 | 5889 | 6297 | 6249 | 6662
Orthochem Bethlehem | 45787.2 | 39973.5 | 40622.2 | 37337.9 | 36620.7 | 33353.5791 | 36066.4551 | 40562.3619 | 41523.1887 | 44647.7625 | 44811.7068 | 47334.9198
Plastiplate | 11454.7 | 9955.3 | 10575.8 | 9316.2 | 9144.7 | 8500.6 | 9262.3 | 10470.2 | 11129.4 | 11715.5 | 11402.4 | 12145.4
PNB Unlimited | 14426.2 | 12327.9 | 12931.8 | 11024.4 | 10672.6 | 9625 | 10609 | 12263.1 | 13383.1 | 14263 | 14175.5 | 15128.2
Q-lity Meat | 5438.1 | 5030.5 | 5282.5 | 4635.1 | 4575 | 4143.4 | 4561.7 | 5138.7 | 5330 | 5632.2 | 5403.2 | 5647.1
Quintondale | 6558.3 | 5888 | 6335.4 | 5651 | 5782.9 | 5360.4 | 5892.4 | 6481.2 | 6690.9 | 6809.9 | 6587.3 | 6874.1
Riverside Lodge | 20117 | 17684 | 19164 | 16765 | 17392 | 16319 | 17777 | 19722 | 19924 | 20687 | 19526 | 20860
Sakhumnotho | 6141.4 | 5508.6 | 5936.5 | 5321.7 | 5446.5 | 5045.9 | 5553.9 | 6085.5 | 6263.9 | 6378 | 6164.1 | 6435
SaveMore Alldays - Store | 25562 | 22098 | 24392 | 23827 | 22987 | 20718 | 21811 | 25554 | 25189 | 24495 | 24514 | 25926
Savemore Liquor Alldays | 3892.3 | 3360.7 | 3712.5 | 3625.7 | 3497.5 | 3151.4 | 3316.5 | 3887.5 | 3830.3 | 3729.7 | 3733.1 | 3946.1
Saverite Durban | 13146.9 | 11450.2 | 11470.9 | 9218.9 | 7841.5 | 7108.1 | 7657.1 | 9019.7 | 9680 | 11319.5 | 11746.6 | 13355.6
Saverite PMB | 13913.7 | 11543.3 | 12043.3 | 10530.6 | 9452.2 | 8210.8 | 9090.2 | 10347.3 | 11125.2 | 12217.2 | 13140.3 | 14098.5
Secunda Plaza choppies | 25627.8 | 22616.5 | 24129.3 | 20942.1 | 20778.8 | 19071.6 | 20913.3 | 23886.3 | 25209.3 | 25379.5 | 25008.8 | 26105.1
Secunda Plaza Shops | 4844 | 4251 | 4530 | 3971 | 4026 | 3734 | 4073 | 4560 | 4749 | 4766 | 4722 | 4940
Shoprite Dube | 26360 | 22720 | 22207 | 19091 | 17077 | 14868 | 16693 | 20079 | 22828 | 26013 | 26204 | 26697
Shoprite Hillbrow | 21647 | 18412 | 19207 | 16103 | 15740 | 13974 | 15451 | 17961 | 19934 | 21559 | 21438 | 23043
Shoprite Ladybrand | 39488 | 32855 | 31263.3 | 26209 | 23138 | 19982 | 22686 | 27412 | 31462 | 36532 | 38823 | 42222
Shoprite Mini Ganyesa | 37861 | 31552 | 31851 | 27124 | 24741 | 21991 | 24194 | 28859 | 32205 | 36732 | 38185 | 40356
Shoprite Naledi | 22876 | 19487 | 19886 | 16305 | 14747 | 12857 | 14434 | 17635 | 20353 | 22357 | 22859 | 24367
Shoprite Newlands | 34135 | 26981 | 26829 | 20433 | 21068 | 16978 | 19291 | 21448 | 20157 | 25054 | 25471 | 31547
Shoprite Thokoza | 20649 | 17891 | 17668 | 15178 | 14023 | 12327 | 13742 | 16094 | 17988 | 20737 | 20655 | 21136
Spring Glade | 19574.9 | 16723.6 | 17808.6 | 15502.2 | 15075 | 13622.2 | 15167.7 | 17455.2 | 18819 | 19760.2 | 19368.5 | 20469.3
SR Morula TF 1 | 10342 | 8891 | 8671 | 7539 | 6938 | 6138 | 6763 | 7916 | 8738 | 10008 | 9999 | 10268
SR Morula TF 1 - Shoprite | 31888.4 | 27677 | 27300 | 23765 | 21915 | 19368 | 21313 | 24908 | 27534 | 31253 | 31179 | 31893
SR Morula TF 2 | 10668.8 | 9218.6 | 9045 | 7797 | 7144.8 | 6299.2 | 6941.6 | 8155.7 | 9060 | 10392 | 10393 | 10647
Thakadu Industrial
The Alec | 8222 | 6998 | 7059 | 5574 | 5282 | 4730 | 5256 | 6045 | 7051 | 8056 | 8145 | 8740
Three Peaks | 5698.8 | 5080.8 | 5209.7 | 4357.5 | 3906.6 | 3553 | 3801.5 | 4316 | 4437 | 5034.3 | 5106.1 | 5754.2
TPF Foods | 5045.9 | 4360.2 | 4711.1 | 4084.1 | 4125.1 | 3778.7 | 4137.8 | 4655.4 | 4964.6 | 5199.2 | 4977 | 5354.9
Trouw Nutrition | 15814.1 | 14182.5 | 15127.6 | 13566.2 | 13865.8 | 12963.1 | 14146.2 | 15603.1 | 15929.8 | 16382.7 | 15892.2 | 16746.5
U Save Botrivier | 8111 | 6915 | 6721 | 5701 | 5135 | 4368 | 4517 | 5248 | 5835 | 7211 | 7571 | 8107
Watt Place Rotoflo | 31142 | 26504 | 26827 | 22270 | 21135 | 18949 | 21000 | 24518 | 27252 | 30285 | 29971 | 32254
Zwartop Golf Course | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Shoprite Ekhaya | 31534 | 27088 | 25946 | 22097 | 19717 | 17225 | 19287 | 23158 | 26490 | 30317 | 30935 | 31977
Grootpan | 32305 | 29685 | 31046 | 28456 | 28669 | 26032 | 28480 | 31722 | 32846 | 34908 | 33468 | 32717
Roan Foods | 20178 | 17954 | 19150 | 18060 | 18124 | 15908 | 16827 | 19405 | 19981 | 22401 | 20125 | 20771
Engen Kaalfontein | 19301 | 16753 | 16260 | 13800 | 12669 | 11099 | 12207 | 14565.3 | 16481.3 | 18948 | 19155 | 19406
Checkers Lichtenburg | 29390 | 25795 | 25594 | 22145 | 20838 | 18631 | 20290 | 23679 | 26288 | 29851 | 30171 | 30447
Alpine Heath Resort | 32086 | 28761 | 30379 | 30915 | 33245 | 31827 | 31168 | 35166 | 31389 | 31629 | 32213 | 32115
Usave Naboomspruit | 6637 | 5857 | 5923 | 5363 | 5166 | 4726 | 5161 | 5838 | 6186 | 6701 | 6553 | 6655

## OG
Site Name | Offtake Guarantee | Expected Utilisation% | Age | As-Built kWh | Guaranteed Generation (kWh) | Unavailability kWh | Correct kWh | Actual Generation (kWh) | Shortfall (kWh) | Performance Rate | Notes
Alpine Heath Residential | YES | 90% | 1.8179 | 63342 | 56284.4232 | 17511.2012 | 38773.222 | 34917.2 | -3856.022 | 90.0549 | The system performed moderately. A few technical issues were experienced , the expected system production was corrected and system restored to normal production.
Checkrite Inanda | YES | 90% | 2.3299 | 94580 | 83740.1703 | 7823.8948 | 75916.2755 | 76046.7559 | 130.4804 | 100.1719 | The system performed as expected. A few technical issues were experienced during Feb 2026, the expected system production was corrected and system restored to normal production.
Demco | YES | 80% | 2.36 | 428379 | 337068.6042 | 7636.2489 | 329432.3553 | 166060.42 | -163371.9353 | 50.408 | The system performed as expected. As previously experienced, the site demand is low and the system was not fully utilized.
Golden Spot Resort | YES | 90% | 3.4196 | 45617 | 40080.8529 | 9467.6512 | 30613.2017 | 24341.6 | -6271.6017 | 79.5134
Golden Spot Shops | YES | 90% | 3.4223 | 40942 | 35972.526 | 2452.5762 | 33519.9498 | 32105.5 | -1414.4498 | 95.7803 | Testing
Hilston Rotoflo | YES | 85% | 3.4661 | 319608 | 265132.0923 | 0 | 265132.0923 | 254905.02 | -10227.0723 | 96.1427 | The system performed as expected. System produced 96% of expected production due to 20 days of closure during December-Jan.
Huis Herfsblaar | YES | 90% | 2.3518 | 355254 | 314489.8884 | 16705.582 | 297784.3064 | 271722.179 | -26062.1274 | 91.248 | The system performed as expected. A few technical issues were experienced during July - Aug 2025, the expected system production was corrected and system restored to normal production.
Mdluli | YES | 80% | 2.527 | 200775 | 157793.9188 | 17807.2333 | 139986.6854 | 147166.31 | 7179.6246 | 105.1288 | The system performed as expected. A few technical issues were experienced during July - Aug 2025 and Jan 2026 which limited inverter production during repairs, the expected system production was corrected and system restored to normal production.
Meredale Heights | YES | 90% | 2.9405 | 73186 | 64520.8282 | 0 | 64520.8282 | 61467.39 | -3053.4382 | 95.2675 | The system performed as expected. As previously experienced, the site demand is low and the system was not fully utilized.
Opal Students | YES | 90% | 3.1431 | 66026 | 58125.7841 | 0 | 58125.7841 | 46668.7 | -11457.0841 | 80.2892 | Testing
Plastiplate | YES | 75% | 4.4736 | 125072.5 | 90902.3489 | 1603.2966 | 89299.0523 | 72438 | -16861.0523 | 81.1184 | Testing
Riverside Lodge | YES | 85% | 3.4606 | 225937 | 187434.1498 | 0 | 187434.1498 | 176720.45 | -10713.6998 | 94.284 | Testing
The Alec | YES | 92.5% | 3.4333 | 81158 | 73282.2898 | 0 | 73282.2898 | 56043.3 | -17238.9898 | 76.4759 | Testing
Watt Place Rotoflo | YES | 90% |  | 312107 | #VALUE! | 0 | #VALUE! | 237169.27 | #VALUE! | #VALUE! | Testing
SR Morula TF 1 | YES | 90% | 1.1855 | 102211 | 91227.0252 | 5986.4593 | 85240.5659 | 77775.48 | -7465.0859 | 91.2423 | Testing
SR Morula TF 2 | YES | 90% | 1.1855 | 105762.7 | 94397.0463 | 6143.8165 | 88253.2297 | 78264.64 | -9988.5897 | 88.6819 | Testing
Olievenhoutbosch 1 | YES | 90% | 1.0897 | 524973 | 468872.953 | 115874.4719 | 352998.4812 | 300497.955 | -52500.5262 | 85.1273 | Testing
Olievenhoutbosch 2 | YES | 90% | 1.0897 | 138565 | 123757.5661 | 30580.8548 | 93176.7113 | 81974.6328 | -11202.0785 | 87.9776 | Testing
IPID - Floor 6 | YES | 90% | 1.0623 | 89076 | 79572.3978 | 34914.7861 | 44657.6117 | 33061.7 | -11595.9117 | 74.0337 | Testing
IPID - Floor 4 | YES | 90% | 1.0623 | 89076 | 79572.3978 | 34914.7861 | 44657.6117 | 47460.3 | 2802.6883 | 106.2759 | Testing
Engen Lotus Gardens | YES | 90% | 1.0157 | 31637 | 28270.8604 | 14421.7301 | 13849.1303 | 17882.44 | 4033.3097 | 129.1232 | Testing
Engen Kaalfontein | YES | 90% | 0.43806 | 190644.6 | 171052.9693 | 171487.768 | -434.7987 | 10169 | 10603.7987 | -2338.7835 | Testing
Alpine Heath Resort | YES | 90% | 0.49829 | 380893 | 341605.8861 | 281397.3692 | 60208.517 | 53212.2 | -6996.317 | 88.3799 | Testing

## measured
Site Name | Date | Measured Value (kWh)
21 Melrose | 2024-01-01 | 1815
21 Melrose | 2024-02-01 | 2295
21 Melrose | 2024-03-01 | 2474
21 Melrose | 2024-04-01 | 2136
21 Melrose | 2024-05-01 | 2212
21 Melrose | 2024-06-01 | 1863
21 Melrose | 2024-07-01 | 1943
21 Melrose | 2024-08-01 | 1710
21 Melrose | 2024-09-01 | 1579
21 Melrose | 2024-10-01 | 1593
21 Melrose | 2024-11-01 | 1794
21 Melrose | 2024-12-01 | 1794
21 Melrose | 2025-01-01 | 1992
21 Melrose | 2025-02-01 | 1458
21 Melrose | 2025-03-01 | 1382
21 Melrose | 2025-04-01 | 1183
21 Melrose | 2025-05-01 | 1860
21 Melrose | 2025-06-01 | 1756.6
21 Melrose | 2025-07-01 | 1742
21 Melrose | 2025-08-01 | 1613
21 Melrose | 2025-09-01 | 1358.7
21 Melrose | 2025-10-01 | 1601
21 Melrose | 2025-11-01 | 1444
21 Melrose | 2025-12-01 | 1375
21 Melrose | 2026-01-01 | 1549
21 Melrose | 2026-02-01 | 1362
21 Melrose | 2026-03-01 | 1237
21 Melrose | 2026-04-01 | 830
21 Melrose | 2026-05-01 | 1169.9
21 Melrose | 2026-06-01 | 1287
21 Melrose | 2026-07-01 | 1638
21 Melrose | 2026-08-01 | 1374
21 Melrose | 2026-09-01 | 1161.6
21 Melrose | 2026-10-01
21 Melrose | 2026-11-01
21 Melrose | 2026-12-01
African Global Plastics | 2024-01-01 | 23024
African Global Plastics | 2024-02-01 | 23235
African Global Plastics | 2024-03-01 | 23235
African Global Plastics | 2024-04-01 | 19307
African Global Plastics | 2024-05-01 | 18418
African Global Plastics | 2024-06-01 | 15949
African Global Plastics | 2024-07-01 | 17174
African Global Plastics | 2024-08-01 | 13588
African Global Plastics | 2024-09-01 | 20254
African Global Plastics | 2024-10-01 | 27693
African Global Plastics | 2024-11-01 | 24041
African Global Plastics | 2024-12-01 | 25076
African Global Plastics | 2025-01-01 | 22439
African Global Plastics | 2025-02-01 | 14790
African Global Plastics | 2025-03-01 | 15371
African Global Plastics | 2025-04-01 | 13930
African Global Plastics | 2025-05-01 | 15263
African Global Plastics | 2025-06-01 | 11722.16
African Global Plastics | 2025-07-01 | 3209
African Global Plastics | 2025-08-01 | 11143
African Global Plastics | 2025-09-01 | 11503
African Global Plastics | 2025-10-01 | 12856
African Global Plastics | 2025-11-01 | 11518
African Global Plastics | 2025-12-01 | 12208
African Global Plastics | 2026-01-01 | 14027
African Global Plastics | 2026-02-01 | 12261
African Global Plastics | 2026-03-01 | 10788
African Global Plastics | 2026-04-01 | 9392.09
African Global Plastics | 2026-05-01 | 11425.9
African Global Plastics | 2026-06-01 | 10184.42
African Global Plastics | 2026-07-01 | 13136.5304
African Global Plastics | 2026-08-01 | 13435.047
African Global Plastics | 2026-09-01 | 12622.0164
African Global Plastics | 2026-10-01
African Global Plastics | 2026-11-01
African Global Plastics | 2026-12-01
Alpine Heath Residential | 2024-01-01
Alpine Heath Residential | 2024-02-01
Alpine Heath Residential | 2024-03-01
Alpine Heath Residential | 2024-04-01
Alpine Heath Residential | 2024-05-01
Alpine Heath Residential | 2024-06-01
Alpine Heath Residential | 2024-07-01
Alpine Heath Residential | 2024-08-01
Alpine Heath Residential | 2024-09-01
Alpine Heath Residential | 2024-10-01
Alpine Heath Residential | 2024-11-01
Alpine Heath Residential | 2024-12-01
Alpine Heath Residential | 2025-01-01 | 2400
Alpine Heath Residential | 2025-02-01 | 3000
Alpine Heath Residential | 2025-03-01 | 3144
Alpine Heath Residential | 2025-04-01 | 2310
Alpine Heath Residential | 2025-05-01 | 3866
Alpine Heath Residential | 2025-06-01 | 3102
Alpine Heath Residential | 2025-07-01
Alpine Heath Residential | 2025-08-01 | 4721
Alpine Heath Residential | 2025-09-01 | 4200
Alpine Heath Residential | 2025-10-01 | 3499
Alpine Heath Residential | 2025-11-01 | 4045
Alpine Heath Residential | 2025-12-01 | 4277
Alpine Heath Residential | 2026-01-01 | 3071
Alpine Heath Residential | 2026-02-01 | 3013
Alpine Heath Residential | 2026-03-01 | 2340.8
Alpine Heath Residential | 2026-04-01 | 1505.4
Alpine Heath Residential | 2026-05-01 | 1467
Alpine Heath Residential | 2026-06-01 | 2778
Alpine Heath Residential | 2026-07-01 | 2644
Alpine Heath Residential | 2026-08-01 | 2758
Alpine Heath Residential | 2026-09-01 | 2338
Alpine Heath Residential | 2026-10-01
Alpine Heath Residential | 2026-11-01
Alpine Heath Residential | 2026-12-01
BP Parys | 2024-01-01
BP Parys | 2024-02-01
BP Parys | 2024-03-01
BP Parys | 2024-04-01
BP Parys | 2024-05-01
BP Parys | 2024-06-01
BP Parys | 2024-07-01
BP Parys | 2024-08-01
BP Parys | 2024-09-01
BP Parys | 2024-10-01
BP Parys | 2024-11-01
BP Parys | 2024-12-01
BP Parys | 2025-01-01 | 5900
BP Parys | 2025-02-01 | 4277
BP Parys | 2025-03-01 | 4770
BP Parys | 2025-04-01 | 3375
BP Parys | 2025-05-01 | 3507
BP Parys | 2025-06-01 | 2400
BP Parys | 2025-07-01 | 2169
BP Parys | 2025-08-01 | 968.6
BP Parys | 2025-09-01 | 2001.5
BP Parys | 2025-10-01 | 3111
BP Parys | 2025-11-01 | 1605
BP Parys | 2025-12-01
BP Parys | 2026-01-01
BP Parys | 2026-02-01 | 6068
BP Parys | 2026-03-01 | 4800
BP Parys | 2026-04-01 | 4318
BP Parys | 2026-05-01 | 3727.7
BP Parys | 2026-06-01 | 3149
Alpine Heath Resort | 2026-07-01 | 27942
BP Parys | 2026-08-01 | 3313
BP Parys | 2026-09-01 | 4204.16
BP Parys | 2026-10-01
BP Parys | 2026-11-01
BP Parys | 2026-12-01
Bendstore Plaza Shops | 2024-01-01 | 7453
Bendstore Plaza Shops | 2024-02-01 | 10174
Bendstore Plaza Shops | 2024-03-01 | 12197
Bendstore Plaza Shops | 2024-04-01 | 9850
Bendstore Plaza Shops | 2024-05-01 | 10329
Bendstore Plaza Shops | 2024-06-01 | 9684
Bendstore Plaza Shops | 2024-07-01 | 10193
Bendstore Plaza Shops | 2024-08-01 | 9840
Bendstore Plaza Shops | 2024-09-01 | 3277
Bendstore Plaza Shops | 2024-10-01 | 12496
Bendstore Plaza Shops | 2024-11-01 | 12909
Bendstore Plaza Shops | 2024-12-01 | 12587
Bendstore Plaza Shops | 2025-01-01 | 13816
Bendstore Plaza Shops | 2025-02-01 | 11397
Bendstore Plaza Shops | 2025-03-01 | 12740
Bendstore Plaza Shops | 2025-04-01 | 9167
Bendstore Plaza Shops | 2025-05-01 | 9630
Bendstore Plaza Shops | 2025-06-01 | 9081.44
Bendstore Plaza Shops | 2025-07-01 | 9450
Bendstore Plaza Shops | 2025-08-01 | 10695
Bendstore Plaza Shops | 2025-09-01 | 8585
Bendstore Plaza Shops | 2025-10-01 | 9077.9
Bendstore Plaza Shops | 2025-11-01 | 10382
Bendstore Plaza Shops | 2025-12-01 | 13631
Bendstore Plaza Shops | 2026-01-01 | 11296
Bendstore Plaza Shops | 2026-02-01 | 11241.7805
Bendstore Plaza Shops | 2026-03-01 | 10628
Bendstore Plaza Shops | 2026-04-01 | 8541.19
Bendstore Plaza Shops | 2026-05-01 | 9563.61
Bendstore Plaza Shops | 2026-06-01 | 7968.17
Bendstore Plaza Shops | 2026-07-01 | 10351.41
Bendstore Plaza Shops | 2026-08-01 | 11244.861
Bendstore Plaza Shops | 2026-09-01 | 8314.17
Bendstore Plaza Shops | 2026-10-01
Bendstore Plaza Shops | 2026-11-01
Bendstore Plaza Shops | 2026-12-01
Bendstore Spar | 2024-01-01 | 55000
Bendstore Spar | 2024-02-01 | 46799
Bendstore Spar | 2024-03-01 | 40582
Bendstore Spar | 2024-04-01 | 39615
Bendstore Spar | 2024-05-01 | 39494
Bendstore Spar | 2024-06-01 | 35378
Bendstore Spar | 2024-07-01 | 38293
Bendstore Spar | 2024-08-01 | 38554
Bendstore Spar | 2024-09-01 | 37782
Bendstore Spar | 2024-10-01 | 47662
Bendstore Spar | 2024-11-01 | 48184
Bendstore Spar | 2024-12-01 | 44138
Bendstore Spar | 2025-01-01 | 52262
Bendstore Spar | 2025-02-01 | 40904
Bendstore Spar | 2025-03-01 | 45751
Bendstore Spar | 2025-04-01 | 30758
Bendstore Spar | 2025-05-01 | 34925
Bendstore Spar | 2025-06-01 | 29716.71
Bendstore Spar | 2025-07-01 | 27958
Bendstore Spar | 2025-08-01 | 30682
Bendstore Spar | 2025-09-01 | 44171
Bendstore Spar | 2025-10-01 | 53279
Bendstore Spar | 2025-11-01 | 44434
Bendstore Spar | 2025-12-01 | 54661
Bendstore Spar | 2026-01-01 | 47457
Bendstore Spar | 2026-02-01 | 49608.8533
Bendstore Spar | 2026-03-01 | 41208
Bendstore Spar | 2026-04-01 | 36936.35
Bendstore Spar | 2026-05-01 | 38743.02
Bendstore Spar | 2026-06-01 | 31578.49
Bendstore Spar | 2026-07-01 | 39160
Bendstore Spar | 2026-08-01 | 44122.4391
Bendstore Spar | 2026-09-01 | 36563.6
Bendstore Spar | 2026-10-01
Bendstore Spar | 2026-11-01
Bendstore Spar | 2026-12-01
Beyerskloof | 2024-01-01 | 8244
Beyerskloof | 2024-02-01 | 7277
Beyerskloof | 2024-03-01 | 6614
Beyerskloof | 2024-04-01 | 4053
Beyerskloof | 2024-05-01 | 3743
Beyerskloof | 2024-06-01 | 3473
Beyerskloof | 2024-07-01 | 4260
Beyerskloof | 2024-08-01 | 5497
Beyerskloof | 2024-09-01 | 2600
Beyerskloof | 2024-10-01 | 8200
Beyerskloof | 2024-11-01 | 6700
Beyerskloof | 2024-12-01 | 8100
Beyerskloof | 2025-01-01 | 9900
Beyerskloof | 2025-02-01 | 9200
Beyerskloof | 2025-03-01 | 4480
Beyerskloof | 2025-04-01 | 4096
Beyerskloof | 2025-05-01 | 3388
Beyerskloof | 2025-06-01 | 2306.13
Beyerskloof | 2025-07-01 | 2919
Beyerskloof | 2025-08-01 | 5355
Beyerskloof | 2025-09-01 | 8600
Beyerskloof | 2025-10-01 | 10599
Beyerskloof | 2025-11-01 | 12569
Beyerskloof | 2025-12-01 | 13572
Beyerskloof | 2026-01-01 | 13416
Beyerskloof | 2026-02-01 | 10034.177
Beyerskloof | 2026-03-01 | 10400
Beyerskloof | 2026-04-01 | 7344.6
Beyerskloof | 2026-05-01 | 5508.9
Beyerskloof | 2026-06-01 | 5030.25
Beyerskloof | 2026-07-01 | 5251.38
Beyerskloof | 2026-08-01 | 6385.91
Beyerskloof | 2026-09-01 | 8881.77
Beyerskloof | 2026-10-01
Beyerskloof | 2026-11-01
Beyerskloof | 2026-12-01
Buffalo Rock | 2024-01-01
Buffalo Rock | 2024-02-01
Buffalo Rock | 2024-03-01
Buffalo Rock | 2024-04-01
Buffalo Rock | 2024-05-01
Buffalo Rock | 2024-06-01
Buffalo Rock | 2024-07-01
Buffalo Rock | 2024-08-01
Buffalo Rock | 2024-09-01
Buffalo Rock | 2024-10-01
Buffalo Rock | 2024-11-01
Buffalo Rock | 2024-12-01
Buffalo Rock | 2025-01-01
Buffalo Rock | 2025-02-01
Buffalo Rock | 2025-03-01
Buffalo Rock | 2025-04-01
Buffalo Rock | 2025-05-01
Buffalo Rock | 2025-06-01
Buffalo Rock | 2025-07-01
Buffalo Rock | 2025-08-01
Buffalo Rock | 2025-09-01
Buffalo Rock | 2025-10-01 | 1109
Buffalo Rock | 2025-11-01
Buffalo Rock | 2025-12-01
Buffalo Rock | 2026-01-01
Buffalo Rock | 2026-02-01
Buffalo Rock | 2026-03-01
Buffalo Rock | 2026-04-01
Buffalo Rock | 2026-05-01
Buffalo Rock | 2026-06-01
BP Parys | 2026-07-01 | 3615
Buffalo Rock | 2026-08-01 | 926
Buffalo Rock | 2026-09-01 | 668.4
Buffalo Rock | 2026-10-01
Buffalo Rock | 2026-11-01
Buffalo Rock | 2026-12-01
Checkers De Aar | 2024-01-01
Checkers De Aar | 2024-02-01
Checkers De Aar | 2024-03-01
Checkers De Aar | 2024-04-01
Checkers De Aar | 2024-05-01
Checkers De Aar | 2024-06-01
Checkers De Aar | 2024-07-01
Checkers De Aar | 2024-08-01
Checkers De Aar | 2024-09-01
Checkers De Aar | 2024-10-01
Checkers De Aar | 2024-11-01
Checkers De Aar | 2024-12-01
Checkers De Aar | 2025-01-01 | 31100
Checkers De Aar | 2025-02-01 | 23180
Checkers De Aar | 2025-03-01 | 20838
Checkers De Aar | 2025-04-01 | 16626
Checkers De Aar | 2025-05-01 | 15218
Checkers De Aar | 2025-06-01 | 12425.8
Checkers De Aar | 2025-07-01 | 13246
Checkers De Aar | 2025-08-01 | 16953
Checkers De Aar | 2025-09-01 | 19367
Checkers De Aar | 2025-10-01 | 25648.18
Checkers De Aar | 2025-11-01 | 26677
Checkers De Aar | 2025-12-01 | 30286
Checkers De Aar | 2026-01-01 | 30117
Checkers De Aar | 2026-02-01 | 22084
Checkers De Aar | 2026-03-01 | 22201
Checkers De Aar | 2026-04-01 | 16660.7
Checkers De Aar | 2026-05-01 | 13372.29
Checkers De Aar | 2026-06-01 | 9763.7
Buffalo Rock | 2026-07-01 | 719
Checkers De Aar | 2026-08-01 | 12651.55
Checkers De Aar | 2026-09-01 | 15296.73
Checkers De Aar | 2026-10-01
Checkers De Aar | 2026-11-01
Checkers De Aar | 2026-12-01
Checkers Silverlakes Gen | 2024-01-01
Checkers Silverlakes Gen | 2024-02-01
Checkers Silverlakes Gen | 2024-03-01
Checkers Silverlakes Gen | 2024-04-01
Checkers Silverlakes Gen | 2024-05-01
Checkers Silverlakes Gen | 2024-06-01
Checkers Silverlakes Gen | 2024-07-01
Checkers Silverlakes Gen | 2024-08-01
Checkers Silverlakes Gen | 2024-09-01
Checkers Silverlakes Gen | 2024-10-01
Checkers Silverlakes Gen | 2024-11-01
Checkers Silverlakes Gen | 2024-12-01
Checkers Silverlakes Gen | 2025-01-01
Checkers Silverlakes Gen | 2025-02-01
Checkers Silverlakes Gen | 2025-03-01 | 17913
Checkers Silverlakes Gen | 2025-04-01 | 14938
Checkers Silverlakes Gen | 2025-05-01 | 18066
Checkers Silverlakes Gen | 2025-06-01 | 12974.1
Checkers Silverlakes Gen | 2025-07-01 | 13938
Checkers Silverlakes Gen | 2025-08-01 | 18460
Checkers Silverlakes Gen | 2025-09-01 | 17970
Checkers Silverlakes Gen | 2025-10-01 | 22232
Checkers Silverlakes Gen | 2025-11-01 | 17351
Checkers Silverlakes Gen | 2025-12-01 | 21073
Checkers Silverlakes Gen | 2026-01-01 | 22123
Checkers Silverlakes Gen | 2026-02-01 | 16600
Checkers Silverlakes Gen | 2026-03-01 | 17500
Checkers Silverlakes Gen | 2026-04-01 | 15400
Checkers Silverlakes Gen | 2026-05-01 | 15615
Checkers Silverlakes Gen | 2026-06-01 | 12373.57
Checkers De Aar | 2026-07-01 | 8756.05
Checkers Silverlakes Gen | 2026-08-01 | 15825
Checkers Silverlakes Gen | 2026-09-01 | 18200
Checkers Silverlakes Gen | 2026-10-01
Checkers Silverlakes Gen | 2026-11-01
Checkers Silverlakes Gen | 2026-12-01
Checkers Silverlakes No Gen | 2024-01-01
Checkers Silverlakes No Gen | 2024-02-01
Checkers Silverlakes No Gen | 2024-03-01
Checkers Silverlakes No Gen | 2024-04-01
Checkers Silverlakes No Gen | 2024-05-01
Checkers Silverlakes No Gen | 2024-06-01
Checkers Silverlakes No Gen | 2024-07-01
Checkers Silverlakes No Gen | 2024-08-01
Checkers Silverlakes No Gen | 2024-09-01
Checkers Silverlakes No Gen | 2024-10-01
Checkers Silverlakes No Gen | 2024-11-01
Checkers Silverlakes No Gen | 2024-12-01
Checkers Silverlakes No Gen | 2025-01-01
Checkers Silverlakes No Gen | 2025-02-01
Checkers Silverlakes No Gen | 2025-03-01 | 16558
Checkers Silverlakes No Gen | 2025-04-01 | 13087
Checkers Silverlakes No Gen | 2025-05-01 | 15171
Checkers Silverlakes No Gen | 2025-06-01 | 9655.7
Checkers Silverlakes No Gen | 2025-07-01 | 10531.6
Checkers Silverlakes No Gen | 2025-08-01 | 14730
Checkers Silverlakes No Gen | 2025-09-01 | 12165
Checkers Silverlakes No Gen | 2025-10-01 | 20277
Checkers Silverlakes No Gen | 2025-11-01 | 15371
Checkers Silverlakes No Gen | 2025-12-01 | 13568
Checkers Silverlakes No Gen | 2026-01-01 | 21287
Checkers Silverlakes No Gen | 2026-02-01 | 19200
Checkers Silverlakes No Gen | 2026-03-01 | 16030
Checkers Silverlakes No Gen | 2026-04-01 | 13700
Checkers Silverlakes No Gen | 2026-05-01 | 13287
Checkers Silverlakes No Gen | 2026-06-01 | 10602.24
Checkers Lichtenburg | 2026-07-01 | 16617.1608
Checkers Silverlakes No Gen | 2026-08-01 | 18200
Checkers Silverlakes No Gen | 2026-09-01 | 16232
Checkers Silverlakes No Gen | 2026-10-01
Checkers Silverlakes No Gen | 2026-11-01
Checkers Silverlakes No Gen | 2026-12-01
Checkrite Inanda | 2024-01-01
Checkrite Inanda | 2024-02-01
Checkrite Inanda | 2024-03-01
Checkrite Inanda | 2024-04-01
Checkrite Inanda | 2024-05-01
Checkrite Inanda | 2024-06-01
Checkrite Inanda | 2024-07-01
Checkrite Inanda | 2024-08-01
Checkrite Inanda | 2024-09-01
Checkrite Inanda | 2024-10-01
Checkrite Inanda | 2024-11-01
Checkrite Inanda | 2024-12-01
Checkrite Inanda | 2025-01-01 | 8900
Checkrite Inanda | 2025-02-01 | 5390
Checkrite Inanda | 2025-03-01 | 5378
Checkrite Inanda | 2025-04-01 | 3410
Checkrite Inanda | 2025-05-01 | 3628
Checkrite Inanda | 2025-06-01 | 5836
Checkrite Inanda | 2025-07-01 | 6830
Checkrite Inanda | 2025-08-01 | 7659
Checkrite Inanda | 2025-09-01 | 5799
Checkrite Inanda | 2025-10-01 | 6484.6
Checkrite Inanda | 2025-11-01 | 7636
Checkrite Inanda | 2025-12-01 | 7000
Checkrite Inanda | 2026-01-01 | 6305
Checkrite Inanda | 2026-02-01 | 4373.4359
Checkrite Inanda | 2026-03-01 | 4958
Checkrite Inanda | 2026-04-01 | 6980.52
Checkrite Inanda | 2026-05-01 | 6633.98
Alpine Heath Resort | 2026-06-01 | 25295
Checkers Silverlakes Gen | 2026-07-01 | 16600
Checkrite Inanda | 2026-08-01 | 6595.107
Checkrite Inanda | 2026-09-01 | 5791.73
Checkrite Inanda | 2026-10-01
Checkrite Inanda | 2026-11-01
Checkrite Inanda | 2026-12-01
Club Houghton | 2024-01-01 | 3578
Club Houghton | 2024-02-01 | 3594
Club Houghton | 2024-03-01 | 3674
Club Houghton | 2024-04-01 | 3533
Club Houghton | 2024-05-01 | 3191
Club Houghton | 2024-06-01 | 2884
Club Houghton | 2024-07-01 | 3894
Club Houghton | 2024-08-01 | 4058
Club Houghton | 2024-09-01 | 3726
Club Houghton | 2024-10-01 | 4063
Club Houghton | 2024-11-01 | 3998
Club Houghton | 2024-12-01 | 3593
Club Houghton | 2025-01-01 | 3726
Club Houghton | 2025-02-01 | 3060
Club Houghton | 2025-03-01 | 3350
Club Houghton | 2025-04-01 | 2383
Club Houghton | 2025-05-01 | 3026
Club Houghton | 2025-06-01 | 2637.9
Club Houghton | 2025-07-01 | 2506
Club Houghton | 2025-08-01 | 2144
Club Houghton | 2025-09-01 | 2520
Club Houghton | 2025-10-01 | 2989
Club Houghton | 2025-11-01 | 2384
Club Houghton | 2025-12-01 | 2166
Club Houghton | 2026-01-01 | 2756
Club Houghton | 2026-02-01 | 1526
Club Houghton | 2026-03-01 | 1909
Club Houghton | 2026-04-01 | 2190.9
Club Houghton | 2026-05-01 | 2313.3
Club Houghton | 2026-06-01 | 1184
Checkers Silverlakes No Gen | 2026-07-01 | 14345
Club Houghton | 2026-08-01 | 4021
Club Houghton | 2026-09-01 | 3663
Club Houghton | 2026-10-01
Club Houghton | 2026-11-01
Club Houghton | 2026-12-01
Coldstar International | 2024-01-01 | 5665
Coldstar International | 2024-02-01 | 3554
Coldstar International | 2024-03-01 | 1
Coldstar International | 2024-04-01 | 1
Coldstar International | 2024-05-01 | 1
Coldstar International | 2024-06-01 | 3309
Coldstar International | 2024-07-01 | 2293
Coldstar International | 2024-08-01 | 1967
Coldstar International | 2024-09-01 | 3009
Coldstar International | 2024-10-01 | 4500
Coldstar International | 2024-11-01 | 3918
Coldstar International | 2024-12-01 | 2583
Coldstar International | 2025-01-01 | 3426
Coldstar International | 2025-02-01 | 3380.46
Coldstar International | 2025-03-01 | 3717
Coldstar International | 2025-04-01 | 2027
Coldstar International | 2025-05-01 | 3199
Coldstar International | 2025-06-01 | 2899.41
Coldstar International | 2025-07-01 | 3705
Coldstar International | 2025-08-01 | 4242
Coldstar International | 2025-09-01 | 3928
Coldstar International | 2025-10-01 | 4810
Coldstar International | 2025-11-01 | 5556
Coldstar International | 2025-12-01 | 5696
Coldstar International | 2026-01-01 | 5960
Coldstar International | 2026-02-01 | 5548
Coldstar International | 2026-03-01 | 5036
Coldstar International | 2026-04-01 | 4183.27
Coldstar International | 2026-05-01 | 4320
Coldstar International | 2026-06-01 | 3510
Checkrite Inanda | 2026-07-01 | 5573.8
Coldstar International | 2026-08-01 | 4690
Coldstar International | 2026-09-01 | 3950.63
Coldstar International | 2026-10-01
Coldstar International | 2026-11-01
Coldstar International | 2026-12-01
Cultura Fresh | 2024-01-01
Cultura Fresh | 2024-02-01
Cultura Fresh | 2024-03-01
Cultura Fresh | 2024-04-01
Cultura Fresh | 2024-05-01
Cultura Fresh | 2024-06-01
Cultura Fresh | 2024-07-01
Cultura Fresh | 2024-08-01
Cultura Fresh | 2024-09-01
Cultura Fresh | 2024-10-01
Cultura Fresh | 2024-11-01
Cultura Fresh | 2024-12-01
Cultura Fresh | 2025-01-01
Cultura Fresh | 2025-02-01
Cultura Fresh | 2025-03-01
Cultura Fresh | 2025-04-01
Cultura Fresh | 2025-05-01
Cultura Fresh | 2025-06-01
Cultura Fresh | 2025-07-01
Cultura Fresh | 2025-08-01
Cultura Fresh | 2025-09-01 | 8715
Cultura Fresh | 2025-10-01 | 11487.6
Cultura Fresh | 2025-11-01 | 11643
Cultura Fresh | 2025-12-01 | 11559
Cultura Fresh | 2026-01-01 | 12880
Cultura Fresh | 2026-02-01 | 9660
Cultura Fresh | 2026-03-01 | 9967
Cultura Fresh | 2026-04-01 | 4183
Cultura Fresh | 2026-05-01
Cultura Fresh | 2026-06-01
Club Houghton | 2026-07-01 | 3646
Cultura Fresh | 2026-08-01
Cultura Fresh | 2026-09-01
Cultura Fresh | 2026-10-01
Cultura Fresh | 2026-11-01
Cultura Fresh | 2026-12-01
Demco | 2024-01-01
Demco | 2024-02-01
Demco | 2024-03-01
Demco | 2024-04-01
Demco | 2024-05-01
Demco | 2024-06-01
Demco | 2024-07-01
Demco | 2024-08-01
Demco | 2024-09-01
Demco | 2024-10-01
Demco | 2024-11-01
Demco | 2024-12-01
Demco | 2025-01-01 | 17200
Demco | 2025-02-01 | 15760
Demco | 2025-03-01 | 15700
Demco | 2025-04-01 | 10223
Demco | 2025-05-01 | 14225
Demco | 2025-06-01 | 14376.5
Demco | 2025-07-01 | 15177.99
Demco | 2025-08-01 | 16924
Demco | 2025-09-01 | 16705
Demco | 2025-10-01 | 21308.4
Demco | 2025-11-01 | 12744
Demco | 2025-12-01 | 7631
Demco | 2026-01-01 | 7744.97
Demco | 2026-02-01 | 13221
Demco | 2026-03-01 | 14695
Demco | 2026-04-01 | 14798.11
Demco | 2026-05-01 | 13154.32
Checkrite Inanda | 2026-06-01 | 5387.22
Coldstar International | 2026-07-01 | 3547
Demco | 2026-08-01 | 14955
Demco | 2026-09-01 | 18244.51
Demco | 2026-10-01
Demco | 2026-11-01
Demco | 2026-12-01
Engen Lotus Gardens | 2024-01-01
Engen Lotus Gardens | 2024-02-01
Engen Lotus Gardens | 2024-03-01
Engen Lotus Gardens | 2024-04-01
Engen Lotus Gardens | 2024-05-01
Engen Lotus Gardens | 2024-06-01
Engen Lotus Gardens | 2024-07-01
Engen Lotus Gardens | 2024-08-01
Engen Lotus Gardens | 2024-09-01
Engen Lotus Gardens | 2024-10-01
Engen Lotus Gardens | 2024-11-01
Engen Lotus Gardens | 2024-12-01
Engen Lotus Gardens | 2025-01-01
Engen Lotus Gardens | 2025-02-01
Engen Lotus Gardens | 2025-03-01
Engen Lotus Gardens | 2025-04-01
Engen Lotus Gardens | 2025-05-01
Engen Lotus Gardens | 2025-06-01
Engen Lotus Gardens | 2025-07-01
Engen Lotus Gardens | 2025-08-01
Engen Lotus Gardens | 2025-09-01
Engen Lotus Gardens | 2025-10-01
Engen Lotus Gardens | 2025-11-01
Engen Lotus Gardens | 2025-12-01
Engen Lotus Gardens | 2026-01-01 | 3245
Engen Lotus Gardens | 2026-02-01 | 3122
Engen Lotus Gardens | 2026-03-01 | 2817
Engen Lotus Gardens | 2026-04-01 | 2735.53
Engen Lotus Gardens | 2026-05-01 | 3239.91
Demco | 2026-06-01 | 11956.63
Cultura Fresh | 2026-07-01 | 0
Engen Lotus Gardens | 2026-08-01 | 3368.28
Engen Lotus Gardens | 2026-09-01 | 2640.395
Engen Lotus Gardens | 2026-10-01
Engen Lotus Gardens | 2026-11-01
Engen Lotus Gardens | 2026-12-01
Giba Gorge Main | 2024-01-01 | 9736
Giba Gorge Main | 2024-02-01 | 8912
Giba Gorge Main | 2024-03-01 | 9597
Giba Gorge Main | 2024-04-01 | 7950
Giba Gorge Main | 2024-05-01 | 7482
Giba Gorge Main | 2024-06-01 | 6656
Giba Gorge Main | 2024-07-01 | 11170
Giba Gorge Main | 2024-08-01 | 11290
Giba Gorge Main | 2024-09-01 | 8578
Giba Gorge Main | 2024-10-01 | 12704
Giba Gorge Main | 2024-11-01 | 5700
Giba Gorge Main | 2024-12-01
Giba Gorge Main | 2025-01-01
Giba Gorge Main | 2025-02-01
Giba Gorge Main | 2025-03-01 | 6684
Giba Gorge Main | 2025-04-01 | 3992
Giba Gorge Main | 2025-05-01 | 6009
Giba Gorge Main | 2025-06-01 | 5530.9
Giba Gorge Main | 2025-07-01 | 6694
Giba Gorge Main | 2025-08-01 | 7750
Giba Gorge Main | 2025-09-01 | 7031
Giba Gorge Main | 2025-10-01 | 9805
Giba Gorge Main | 2025-11-01 | 9365
Giba Gorge Main | 2025-12-01 | 5379
Giba Gorge Main | 2026-01-01 | 4979.16
Giba Gorge Main | 2026-02-01 | 2172.67
Giba Gorge Main | 2026-03-01 | 350
Giba Gorge Main | 2026-04-01 | 194.99
Giba Gorge Main | 2026-05-01
Giba Gorge Main | 2026-06-01 | 3521
Demco | 2026-07-01 | 12633
Giba Gorge Main | 2026-08-01 | 4981
Giba Gorge Main | 2026-09-01 | 5324.68
Giba Gorge Main | 2026-10-01
Giba Gorge Main | 2026-11-01
Giba Gorge Main | 2026-12-01
Giba Gorge Storage | 2024-01-01 | 4830
Giba Gorge Storage | 2024-02-01 | 7231
Giba Gorge Storage | 2024-03-01 | 5436
Giba Gorge Storage | 2024-04-01 | 5158
Giba Gorge Storage | 2024-05-01 | 3827
Giba Gorge Storage | 2024-06-01 | 3220
Giba Gorge Storage | 2024-07-01 | 5497
Giba Gorge Storage | 2024-08-01 | 4475
Giba Gorge Storage | 2024-09-01 | 1847
Giba Gorge Storage | 2024-10-01 | 1575
Giba Gorge Storage | 2024-11-01 | 5700
Giba Gorge Storage | 2024-12-01 | 1938
Giba Gorge Storage | 2025-01-01 | 5227
Giba Gorge Storage | 2025-02-01 | 5137
Giba Gorge Storage | 2025-03-01 | 5031
Giba Gorge Storage | 2025-04-01 | 3147
Giba Gorge Storage | 2025-05-01 | 4797
Giba Gorge Storage | 2025-06-01 | 3255.49
Giba Gorge Storage | 2025-07-01 | 5212
Giba Gorge Storage | 2025-08-01 | 1743.88
Giba Gorge Storage | 2025-09-01 | 4503
Giba Gorge Storage | 2025-10-01 | 6159
Giba Gorge Storage | 2025-11-01 | 6232
Giba Gorge Storage | 2025-12-01 | 5380
Giba Gorge Storage | 2026-01-01 | 7601.5
Giba Gorge Storage | 2026-02-01 | 6347.07
Giba Gorge Storage | 2026-03-01 | 7063
Giba Gorge Storage | 2026-04-01 | 4736.87
Giba Gorge Storage | 2026-05-01 | 4375.54
Giba Gorge Storage | 2026-06-01 | 3483
Engen Kaalfontein | 2026-07-01 | 6140
Giba Gorge Storage | 2026-08-01 | 5110
Giba Gorge Storage | 2026-09-01 | 5755.15
Giba Gorge Storage | 2026-10-01
Giba Gorge Storage | 2026-11-01
Giba Gorge Storage | 2026-12-01
Golden Spot Resort | 2024-01-01 | 961
Golden Spot Resort | 2024-02-01 | 798
Golden Spot Resort | 2024-03-01 | 398
Golden Spot Resort | 2024-04-01 | 1334
Golden Spot Resort | 2024-05-01 | 1953
Golden Spot Resort | 2024-06-01 | 1657
Golden Spot Resort | 2024-07-01 | 1845
Golden Spot Resort | 2024-08-01 | 2034
Golden Spot Resort | 2024-09-01 | 1982
Golden Spot Resort | 2024-10-01 | 2181
Golden Spot Resort | 2024-11-01 | 1783
Golden Spot Resort | 2024-12-01 | 2366
Golden Spot Resort | 2025-01-01 | 2514
Golden Spot Resort | 2025-02-01 | 2930
Golden Spot Resort | 2025-03-01 | 1758
Golden Spot Resort | 2025-04-01 | 1646
Golden Spot Resort | 2025-05-01 | 2386
Golden Spot Resort | 2025-06-01 | 1228
Golden Spot Resort | 2025-07-01 | 1684
Golden Spot Resort | 2025-08-01 | 1766.1
Golden Spot Resort | 2025-09-01 | 1960
Golden Spot Resort | 2025-10-01 | 2119
Golden Spot Resort | 2025-11-01 | 1774
Golden Spot Resort | 2025-12-01 | 2120
Golden Spot Resort | 2026-01-01 | 647
Golden Spot Resort | 2026-02-01 | 1429
Golden Spot Resort | 2026-03-01 | 1816
Golden Spot Resort | 2026-04-01 | 3513.5
Golden Spot Resort | 2026-05-01 | 3029
Engen Kaalfontein | 2026-06-01 | 10169
Golden Spot Resort | 2026-06-01 | 2484
Engen Lotus Gardens | 2026-07-01 | 3388.4248
Golden Spot Resort | 2026-08-01 | 1628
Golden Spot Resort | 2026-09-01 | 747.8
Golden Spot Resort | 2026-10-01
Golden Spot Resort | 2026-11-01
Golden Spot Resort | 2026-12-01
Golden Spot Shops | 2024-01-01 | 1880
Golden Spot Shops | 2024-02-01 | 1559
Golden Spot Shops | 2024-03-01 | 1596
Golden Spot Shops | 2024-04-01 | 2170
Golden Spot Shops | 2024-05-01 | 2876
Golden Spot Shops | 2024-06-01 | 2499
Golden Spot Shops | 2024-07-01 | 2895
Golden Spot Shops | 2024-08-01 | 3177
Golden Spot Shops | 2024-09-01 | 3048
Golden Spot Shops | 2024-10-01 | 3449
Golden Spot Shops | 2024-11-01 | 3441
Golden Spot Shops | 2024-12-01 | 3537
Golden Spot Shops | 2025-01-01 | 3700
Golden Spot Shops | 2025-02-01 | 2900
Golden Spot Shops | 2025-03-01 | 3471
Golden Spot Shops | 2025-04-01 | 2668
Golden Spot Shops | 2025-05-01 | 3127
Golden Spot Shops | 2025-06-01 | 2748.4
Golden Spot Shops | 2025-07-01 | 2501
Golden Spot Shops | 2025-08-01 | 299.8
Golden Spot Shops | 2025-09-01 | 2705
Golden Spot Shops | 2025-10-01 | 2939
Golden Spot Shops | 2025-11-01 | 2609
Golden Spot Shops | 2025-12-01 | 3364
Golden Spot Shops | 2026-01-01 | 3086
Golden Spot Shops | 2026-02-01 | 3628
Golden Spot Shops | 2026-03-01 | 2909
Golden Spot Shops | 2026-04-01 | 2558.1
Golden Spot Shops | 2026-05-01 | 3029.6
Engen Lotus Gardens | 2026-06-01 | 2723
Giba Gorge Main | 2026-07-01 | 5136
Golden Spot Shops | 2026-08-01
Golden Spot Shops | 2026-09-01 | 0
Golden Spot Shops | 2026-10-01
Golden Spot Shops | 2026-11-01
Golden Spot Shops | 2026-12-01
Grootpan | 2024-01-01
Grootpan | 2024-02-01
Grootpan | 2024-03-01
Grootpan | 2024-04-01
Grootpan | 2024-05-01
Grootpan | 2024-06-01
Grootpan | 2024-07-01
Grootpan | 2024-08-01
Grootpan | 2024-09-01
Grootpan | 2024-10-01
Grootpan | 2024-11-01
Grootpan | 2024-12-01
Grootpan | 2025-01-01
Grootpan | 2025-02-01
Grootpan | 2025-03-01
Grootpan | 2025-04-01
Grootpan | 2025-05-01
Grootpan | 2025-06-01
Grootpan | 2025-07-01
Grootpan | 2025-08-01
Grootpan | 2025-09-01
Grootpan | 2025-10-01
Grootpan | 2025-11-01
Grootpan | 2025-12-01
Grootpan | 2026-01-01
Grootpan | 2026-02-01
Grootpan | 2026-03-01 | 2780
Grootpan | 2026-04-01 | 14950
Grootpan | 2026-05-01 | 6540
Grootpan | 2026-06-01 | 7560
Giba Gorge Storage | 2026-07-01 | 4112
Grootpan | 2026-08-01 | 18070
Grootpan | 2026-09-01 | 9230
Grootpan | 2026-10-01
Grootpan | 2026-11-01
Grootpan | 2026-12-01
HB Dunn | 2024-01-01
HB Dunn | 2024-02-01
HB Dunn | 2024-03-01
HB Dunn | 2024-04-01
HB Dunn | 2024-05-01
HB Dunn | 2024-06-01 | 1659
HB Dunn | 2024-07-01 | 2542
HB Dunn | 2024-08-01 | 2833
HB Dunn | 2024-09-01 | 2688
HB Dunn | 2024-10-01 | 3664
HB Dunn | 2024-11-01 | 3499
HB Dunn | 2024-12-01 | 2842
HB Dunn | 2025-01-01 | 3075
HB Dunn | 2025-02-01 | 3328
HB Dunn | 2025-03-01 | 2317
HB Dunn | 2025-04-01 | 3007
HB Dunn | 2025-05-01 | 3516
HB Dunn | 2025-06-01 | 2912.8
HB Dunn | 2025-07-01 | 2789
HB Dunn | 2025-08-01 | 3342
HB Dunn | 2025-09-01 | 3079
HB Dunn | 2025-10-01 | 3708
HB Dunn | 2025-11-01 | 2852
HB Dunn | 2025-12-01 | 2386
HB Dunn | 2026-01-01 | 1855
HB Dunn | 2026-02-01 | 3786
HB Dunn | 2026-03-01 | 2926
HB Dunn | 2026-04-01 | 1520
HB Dunn | 2026-05-01 | 2675.6
HB Dunn | 2026-06-01 | 2896
Golden Spot Resort | 2026-07-01 | 857
HB Dunn | 2026-08-01 | 2805
HB Dunn | 2026-09-01 | 2916.4
HB Dunn | 2026-10-01
HB Dunn | 2026-11-01
HB Dunn | 2026-12-01
Helderberg Collage | 2024-01-01 | 32658
Helderberg Collage | 2024-02-01 | 26200
Helderberg Collage | 2024-03-01 | 23764
Helderberg Collage | 2024-04-01 | 17748
Helderberg Collage | 2024-05-01 | 12623
Helderberg Collage | 2024-06-01 | 9466
Helderberg Collage | 2024-07-01 | 8265
Helderberg Collage | 2024-08-01 | 14669
Helderberg Collage | 2024-09-01 | 20334
Helderberg Collage | 2024-10-01 | 26318
Helderberg Collage | 2024-11-01 | 29589
Helderberg Collage | 2024-12-01 | 31807
Helderberg Collage | 2025-01-01 | 32545
Helderberg Collage | 2025-02-01 | 20706
Helderberg Collage | 2025-03-01 | 16650
Helderberg Collage | 2025-04-01 | 13216
Helderberg Collage | 2025-05-01 | 8710
Helderberg Collage | 2025-06-01 | 7500.92
Helderberg Collage | 2025-07-01 | 9649
Helderberg Collage | 2025-08-01 | 13424
Helderberg Collage | 2025-09-01 | 19447
Helderberg Collage | 2025-10-01 | 33678
Helderberg Collage | 2025-11-01 | 40164
Helderberg Collage | 2025-12-01 | 42482
Helderberg Collage | 2026-01-01 | 40719
Helderberg Collage | 2026-02-01 | 29862
Helderberg Collage | 2026-03-01 | 30793
Helderberg Collage | 2026-04-01 | 19657.41
Helderberg Collage | 2026-05-01 | 14538.69
Helderberg Collage | 2026-06-01 | 14538.69
Golden Spot Shops | 2026-07-01 | 1400
Helderberg Collage | 2026-08-01 | 20567
Helderberg Collage | 2026-09-01 | 24320.29
Helderberg Collage | 2026-10-01
Helderberg Collage | 2026-11-01
Helderberg Collage | 2026-12-01
Hilston Rotoflo | 2024-01-01 | 17880
Hilston Rotoflo | 2024-02-01 | 18790
Hilston Rotoflo | 2024-03-01 | 22610
Hilston Rotoflo | 2024-04-01 | 20030
Hilston Rotoflo | 2024-05-01 | 17820
Hilston Rotoflo | 2024-06-01 | 11000
Hilston Rotoflo | 2024-07-01 | 17460
Hilston Rotoflo | 2024-08-01 | 24290
Hilston Rotoflo | 2024-09-01 | 22510
Hilston Rotoflo | 2024-10-01 | 31780
Hilston Rotoflo | 2024-11-01 | 30100
Hilston Rotoflo | 2024-12-01 | 17966
Hilston Rotoflo | 2025-01-01 | 20808
Hilston Rotoflo | 2025-02-01 | 21538
Hilston Rotoflo | 2025-03-01 | 22662
Hilston Rotoflo | 2025-04-01 | 17413
Hilston Rotoflo | 2025-05-01 | 20430
Hilston Rotoflo | 2025-06-01 | 18398.74
Hilston Rotoflo | 2025-07-01 | 19115
Hilston Rotoflo | 2025-08-01 | 21942
Hilston Rotoflo | 2025-09-01 | 21707
Hilston Rotoflo | 2025-10-01 | 28392
Hilston Rotoflo | 2025-11-01 | 24635
Hilston Rotoflo | 2025-12-01 | 13946
Hilston Rotoflo | 2026-01-01 | 25775
Hilston Rotoflo | 2026-02-01 | 24391
Hilston Rotoflo | 2026-03-01 | 22838
Hilston Rotoflo | 2026-04-01 | 19038.02
Hilston Rotoflo | 2026-05-01 | 19892
Grootpan | 2026-07-01 | 8390
Hilston Rotoflo | 2026-08-01 | 23217
Hilston Rotoflo | 2026-09-01 | 22918
Hilston Rotoflo | 2026-10-01
Hilston Rotoflo | 2026-11-01
Hilston Rotoflo | 2026-12-01
Huis Herfsblaar | 2024-01-01
Huis Herfsblaar | 2024-02-01
Huis Herfsblaar | 2024-03-01
Huis Herfsblaar | 2024-04-01
Huis Herfsblaar | 2024-05-01
Huis Herfsblaar | 2024-06-01 | 5360
Huis Herfsblaar | 2024-07-01 | 22610
Huis Herfsblaar | 2024-08-01 | 23490
Huis Herfsblaar | 2024-09-01 | 20740
Huis Herfsblaar | 2024-10-01 | 32140
Huis Herfsblaar | 2024-11-01 | 32300
Huis Herfsblaar | 2024-12-01 | 29734
Huis Herfsblaar | 2025-01-01 | 30000
Huis Herfsblaar | 2025-02-01 | 20560
Huis Herfsblaar | 2025-03-01 | 19975
Huis Herfsblaar | 2025-04-01 | 19104
Huis Herfsblaar | 2025-05-01 | 23300
Huis Herfsblaar | 2025-06-01 | 17947.87
Huis Herfsblaar | 2025-07-01 | 13847
Huis Herfsblaar | 2025-08-01 | 22606
Huis Herfsblaar | 2025-09-01 | 23653
Huis Herfsblaar | 2025-10-01 | 29483
Huis Herfsblaar | 2025-11-01 | 22193
Huis Herfsblaar | 2025-12-01 | 27897
Huis Herfsblaar | 2026-01-01 | 26300
Huis Herfsblaar | 2026-02-01 | 27127.919
Huis Herfsblaar | 2026-03-01 | 23100
Huis Herfsblaar | 2026-04-01 | 19981.06
Huis Herfsblaar | 2026-05-01 | 20533.1
Golden Spot Shops | 2026-06-01 | 2477
HB Dunn | 2026-07-01 | 2598
Huis Herfsblaar | 2026-08-01 | 23941.67
Huis Herfsblaar | 2026-09-01 | 23016.89
Huis Herfsblaar | 2026-10-01
Huis Herfsblaar | 2026-11-01
Huis Herfsblaar | 2026-12-01
IPID - Floor 4 | 2024-01-01
IPID - Floor 4 | 2024-02-01
IPID - Floor 4 | 2024-03-01
IPID - Floor 4 | 2024-04-01
IPID - Floor 4 | 2024-05-01
IPID - Floor 4 | 2024-06-01
IPID - Floor 4 | 2024-07-01
IPID - Floor 4 | 2024-08-01
IPID - Floor 4 | 2024-09-01
IPID - Floor 4 | 2024-10-01
IPID - Floor 4 | 2024-11-01
IPID - Floor 4 | 2024-12-01
IPID - Floor 4 | 2025-01-01
IPID - Floor 4 | 2025-02-01
IPID - Floor 4 | 2025-03-01
IPID - Floor 4 | 2025-04-01
IPID - Floor 4 | 2025-05-01
IPID - Floor 4 | 2025-06-01
IPID - Floor 4 | 2025-07-01
IPID - Floor 4 | 2025-08-01
IPID - Floor 4 | 2025-09-01
IPID - Floor 4 | 2025-10-01
IPID - Floor 4 | 2025-11-01
IPID - Floor 4 | 2025-12-01 | 5820
IPID - Floor 4 | 2026-01-01 | 7914
IPID - Floor 4 | 2026-02-01 | 8094
IPID - Floor 4 | 2026-03-01 | 6511
IPID - Floor 4 | 2026-04-01 | 6094.6
IPID - Floor 4 | 2026-05-01 | 7117.7
Hilston Rotoflo | 2026-06-01 | 13234
Helderberg Collage | 2026-07-01 | 14156
IPID - Floor 4 | 2026-08-01 | 7937
IPID - Floor 4 | 2026-09-01 | 7314.8
IPID - Floor 4 | 2026-10-01
IPID - Floor 4 | 2026-11-01
IPID - Floor 4 | 2026-12-01
IPID - Floor 6 | 2024-01-01
IPID - Floor 6 | 2024-02-01
IPID - Floor 6 | 2024-03-01
IPID - Floor 6 | 2024-04-01
IPID - Floor 6 | 2024-05-01
IPID - Floor 6 | 2024-06-01
IPID - Floor 6 | 2024-07-01
IPID - Floor 6 | 2024-08-01
IPID - Floor 6 | 2024-09-01
IPID - Floor 6 | 2024-10-01
IPID - Floor 6 | 2024-11-01
IPID - Floor 6 | 2024-12-01
IPID - Floor 6 | 2025-01-01
IPID - Floor 6 | 2025-02-01
IPID - Floor 6 | 2025-03-01
IPID - Floor 6 | 2025-04-01
IPID - Floor 6 | 2025-05-01
IPID - Floor 6 | 2025-06-01
IPID - Floor 6 | 2025-07-01
IPID - Floor 6 | 2025-08-01
IPID - Floor 6 | 2025-09-01
IPID - Floor 6 | 2025-10-01
IPID - Floor 6 | 2025-11-01
IPID - Floor 6 | 2025-12-01 | 5820
IPID - Floor 6 | 2026-01-01 | 5904
IPID - Floor 6 | 2026-02-01 | 5406
IPID - Floor 6 | 2026-03-01 | 4115
IPID - Floor 6 | 2026-04-01 | 4377
IPID - Floor 6 | 2026-05-01 | 4300
Huis Herfsblaar | 2026-06-01 | 15001.1
Hilston Rotoflo | 2026-07-01 | 17975
IPID - Floor 6 | 2026-08-01 | 5281
IPID - Floor 6 | 2026-09-01 | 4730
IPID - Floor 6 | 2026-10-01
IPID - Floor 6 | 2026-11-01
IPID - Floor 6 | 2026-12-01
Kool Village | 2024-01-01 | 13629
Kool Village | 2024-02-01 | 12014
Kool Village | 2024-03-01 | 12428
Kool Village | 2024-04-01 | 9084
Kool Village | 2024-05-01 | 8049
Kool Village | 2024-06-01 | 6600
Kool Village | 2024-07-01 | 7832
Kool Village | 2024-08-01 | 8766
Kool Village | 2024-09-01 | 9208
Kool Village | 2024-10-01 | 12879
Kool Village | 2024-11-01 | 13410
Kool Village | 2024-12-01 | 13869
Kool Village | 2025-01-01 | 13136
Kool Village | 2025-02-01 | 10624
Kool Village | 2025-03-01 | 10420
Kool Village | 2025-04-01 | 7391
Kool Village | 2025-05-01 | 7947
Kool Village | 2025-06-01 | 6390.63
Kool Village | 2025-07-01 | 7146
Kool Village | 2025-08-01 | 7396
Kool Village | 2025-09-01 | 8160
Kool Village | 2025-10-01 | 10866
Kool Village | 2025-11-01 | 10612
Kool Village | 2025-12-01 | 11236
Kool Village | 2026-01-01 | 13357
Kool Village | 2026-02-01 | 9365
Kool Village | 2026-03-01 | 7814
Kool Village | 2026-04-01 | 5599.56
Kool Village | 2026-05-01 | 5867.76
Kool Village | 2026-06-01 | 4645.31
Huis Herfsblaar | 2026-07-01 | 20850.76
Kool Village | 2026-08-01 | 8388.6689
Kool Village | 2026-09-01 | 7912.61
Kool Village | 2026-10-01
Kool Village | 2026-11-01
Kool Village | 2026-12-01
Makalali | 2024-01-01
Makalali | 2024-02-01
Makalali | 2024-03-01
Makalali | 2024-04-01
Makalali | 2024-05-01
Makalali | 2024-06-01
Makalali | 2024-07-01
Makalali | 2024-08-01
Makalali | 2024-09-01
Makalali | 2024-10-01
Makalali | 2024-11-01
Makalali | 2024-12-01
Makalali | 2025-01-01
Makalali | 2025-02-01
Makalali | 2025-03-01
Makalali | 2025-04-01
Makalali | 2025-05-01
Makalali | 2025-06-01
Makalali | 2025-07-01
Makalali | 2025-08-01
Makalali | 2025-09-01
Makalali | 2025-10-01
Makalali | 2025-11-01
Makalali | 2025-12-01
Makalali | 2026-01-01 | 13394
Makalali | 2026-02-01 | 16065
Makalali | 2026-03-01 | 733
Makalali | 2026-04-01 | 4797.7
Makalali | 2026-05-01 | 5970.07
Makalali | 2026-06-01 | 5060.4
IPID - Floor 4 | 2026-07-01 | 7311
Makalali | 2026-08-01 | 7086.5031
Makalali | 2026-09-01 | 4821.7015
Makalali | 2026-10-01
Makalali | 2026-11-01
Makalali | 2026-12-01
Mambha Cash & Carry | 2024-01-01 | 18892
Mambha Cash & Carry | 2024-02-01 | 18598
Mambha Cash & Carry | 2024-03-01 | 18598
Mambha Cash & Carry | 2024-04-01 | 15678
Mambha Cash & Carry | 2024-05-01 | 14588
Mambha Cash & Carry | 2024-06-01 | 12745
Mambha Cash & Carry | 2024-07-01 | 14803
Mambha Cash & Carry | 2024-08-01 | 15941
Mambha Cash & Carry | 2024-09-01 | 13907
Mambha Cash & Carry | 2024-10-01 | 19899
Mambha Cash & Carry | 2024-11-01 | 18123
Mambha Cash & Carry | 2024-12-01 | 18905
Mambha Cash & Carry | 2025-01-01 | 19907
Mambha Cash & Carry | 2025-02-01 | 15243
Mambha Cash & Carry | 2025-03-01 | 17983
Mambha Cash & Carry | 2025-04-01 | 13643
Mambha Cash & Carry | 2025-05-01 | 15993
Mambha Cash & Carry | 2025-06-01 | 13300.84
Mambha Cash & Carry | 2025-07-01 | 12259
Mambha Cash & Carry | 2025-08-01 | 14893
Mambha Cash & Carry | 2025-09-01 | 13710
Mambha Cash & Carry | 2025-10-01 | 17312
Mambha Cash & Carry | 2025-11-01 | 19748
Mambha Cash & Carry | 2025-12-01 | 19810
Mambha Cash & Carry | 2026-01-01 | 21506.5322
Mambha Cash & Carry | 2026-02-01 | 21266.5806
Mambha Cash & Carry | 2026-03-01 | 18344
Mambha Cash & Carry | 2026-04-01 | 14760.15
Mambha Cash & Carry | 2026-05-01 | 14261.66
Mambha Cash & Carry | 2026-06-01 | 12292.03
IPID - Floor 6 | 2026-07-01 | 3841
Mambha Cash & Carry | 2026-08-01 | 15549.0352
Mambha Cash & Carry | 2026-09-01 | 14407.6783
Mambha Cash & Carry | 2026-10-01
Mambha Cash & Carry | 2026-11-01
Mambha Cash & Carry | 2026-12-01
Mathe Group Company | 2024-01-01 | 52780
Mathe Group Company | 2024-02-01 | 40425
Mathe Group Company | 2024-03-01 | 52832
Mathe Group Company | 2024-04-01 | 46312
Mathe Group Company | 2024-05-01 | 45881
Mathe Group Company | 2024-06-01 | 36174
Mathe Group Company | 2024-07-01 | 49449
Mathe Group Company | 2024-08-01 | 50022
Mathe Group Company | 2024-09-01 | 41179
Mathe Group Company | 2024-10-01 | 38998
Mathe Group Company | 2024-11-01 | 54400
Mathe Group Company | 2024-12-01 | 48109
Mathe Group Company | 2025-01-01 | 50600
Mathe Group Company | 2025-02-01 | 39450
Mathe Group Company | 2025-03-01 | 50665
Mathe Group Company | 2025-04-01 | 33121
Mathe Group Company | 2025-05-01 | 49152
Mathe Group Company | 2025-06-01 | 39999.41
Mathe Group Company | 2025-07-01 | 42250
Mathe Group Company | 2025-08-01 | 42926
Mathe Group Company | 2025-09-01 | 40517.3
Mathe Group Company | 2025-10-01 | 46787.68
Mathe Group Company | 2025-11-01 | 53245
Mathe Group Company | 2025-12-01 | 48360
Mathe Group Company | 2026-01-01 | 49681.6714
Mathe Group Company | 2026-02-01 | 58060.8339
Mathe Group Company | 2026-03-01 | 50832
Mathe Group Company | 2026-04-01 | 41412.22
Mathe Group Company | 2026-05-01 | 46300.95
Mathe Group Company | 2026-06-01 | 37511.86
Kool Village | 2026-07-01 | 6582.2
Mathe Group Company | 2026-08-01 | 49938.125
Mathe Group Company | 2026-09-01 | 43037.19
Mathe Group Company | 2026-10-01
Mathe Group Company | 2026-11-01
Mathe Group Company | 2026-12-01
Mdluli | 2024-01-01
Mdluli | 2024-02-01
Mdluli | 2024-03-01
Mdluli | 2024-04-01 | 6916
Mdluli | 2024-05-01 | 14281
Mdluli | 2024-06-01 | 12149
Mdluli | 2024-07-01 | 15601
Mdluli | 2024-08-01 | 7706
Mdluli | 2024-09-01 | 1
Mdluli | 2024-10-01 | 7310
Mdluli | 2024-11-01 | 13770
Mdluli | 2024-12-01
Mdluli | 2025-01-01 | 4700
Mdluli | 2025-02-01 | 12300
Mdluli | 2025-03-01 | 13554
Mdluli | 2025-04-01 | 9839
Mdluli | 2025-05-01
Mdluli | 2025-06-01 | 12605.8
Mdluli | 2025-07-01 | 8064
Mdluli | 2025-08-01 | 13494
Mdluli | 2025-09-01 | 11744.7
Mdluli | 2025-10-01 | 13202
Mdluli | 2025-11-01 | 10765
Mdluli | 2025-12-01 | 13231
Mdluli | 2026-01-01 | 11720.01
Mdluli | 2026-02-01 | 15533
Mdluli | 2026-03-01 | 12559
Mdluli | 2026-04-01 | 11577.01
Mdluli | 2026-05-01 | 13966.89
IPID - Floor 4 | 2026-06-01 | 5909
Makalali | 2026-07-01 | 6010.4032
Mdluli | 2026-08-01 | 14728.02
Mdluli | 2026-09-01 | 10471.23
Mdluli | 2026-10-01
Mdluli | 2026-11-01
Mdluli | 2026-12-01
Medipost | 2024-01-01
Medipost | 2024-02-01
Medipost | 2024-03-01
Medipost | 2024-04-01
Medipost | 2024-05-01
Medipost | 2024-06-01
Medipost | 2024-07-01
Medipost | 2024-08-01
Medipost | 2024-09-01
Medipost | 2024-10-01
Medipost | 2024-11-01
Medipost | 2024-12-01
Medipost | 2025-01-01
Medipost | 2025-02-01
Medipost | 2025-03-01
Medipost | 2025-04-01
Medipost | 2025-05-01
Medipost | 2025-06-01
Medipost | 2025-07-01
Medipost | 2025-08-01
Medipost | 2025-09-01
Medipost | 2025-10-01
Medipost | 2025-11-01
Medipost | 2025-12-01 | 44400
Medipost | 2026-01-01 | 44972.3
Medipost | 2026-02-01 | 44384
Medipost | 2026-03-01 | 42181
Medipost | 2026-04-01 | 29438.84
Medipost | 2026-05-01 | 20478.6
Medipost | 2026-06-01 | 18349.15
Mambha Cash & Carry | 2026-07-01 | 12604.391
Medipost | 2026-08-01 | 26558.07
Medipost | 2026-09-01 | 31565.57
Medipost | 2026-10-01
Medipost | 2026-11-01
Medipost | 2026-12-01
Meredale Heights | 2024-01-01 | 3824
Meredale Heights | 2024-02-01 | 3746
Meredale Heights | 2024-03-01 | 3799
Meredale Heights | 2024-04-01 | 3854
Meredale Heights | 2024-05-01 | 4391
Meredale Heights | 2024-06-01 | 4167
Meredale Heights | 2024-07-01 | 4515
Meredale Heights | 2024-08-01 | 4113
Meredale Heights | 2024-09-01 | 3620
Meredale Heights | 2024-10-01 | 4760
Meredale Heights | 2024-11-01 | 3916
Meredale Heights | 2024-12-01 | 4124
Meredale Heights | 2025-01-01 | 3080
Meredale Heights | 2025-02-01 | 2400
Meredale Heights | 2025-03-01 | 2832
Meredale Heights | 2025-04-01 | 2690
Meredale Heights | 2025-05-01 | 3597
Meredale Heights | 2025-06-01 | 4831.17
Meredale Heights | 2025-07-01 | 5152
Meredale Heights | 2025-08-01 | 5913
Meredale Heights | 2025-09-01 | 5163
Meredale Heights | 2025-10-01 | 5859
Meredale Heights | 2025-11-01 | 4665
Meredale Heights | 2025-12-01 | 5472
Meredale Heights | 2026-01-01 | 5579.67
Meredale Heights | 2026-02-01 | 4787
Meredale Heights | 2026-03-01 | 4406
Meredale Heights | 2026-04-01 | 4506.8
Meredale Heights | 2026-05-01 | 5143.42
IPID - Floor 6 | 2026-06-01 | 3139.7
Mathe Group Company | 2026-07-01 | 40997.1224
Meredale Heights | 2026-08-01 | 6058
Meredale Heights | 2026-09-01 | 5214.57
Meredale Heights | 2026-10-01
Meredale Heights | 2026-11-01
Meredale Heights | 2026-12-01
Monument Park Checkers | 2024-01-01
Monument Park Checkers | 2024-02-01
Monument Park Checkers | 2024-03-01 | 41550.8
Monument Park Checkers | 2024-04-01 | 25447.6
Monument Park Checkers | 2024-05-01 | 28056
Monument Park Checkers | 2024-06-01 | 27241
Monument Park Checkers | 2024-07-01 | 31078
Monument Park Checkers | 2024-08-01 | 33515
Monument Park Checkers | 2024-09-01 | 34245
Monument Park Checkers | 2024-10-01 | 46108
Monument Park Checkers | 2024-11-01 | 42922
Monument Park Checkers | 2024-12-01 | 44138
Monument Park Checkers | 2025-01-01 | 41100
Monument Park Checkers | 2025-02-01 | 30900
Monument Park Checkers | 2025-03-01 | 31593
Monument Park Checkers | 2025-04-01 | 25646
Monument Park Checkers | 2025-05-01 | 33184
Monument Park Checkers | 2025-06-01 | 29359.5
Monument Park Checkers | 2025-07-01 | 23487
Monument Park Checkers | 2025-08-01 | 34316
Monument Park Checkers | 2025-09-01 | 33632.7
Monument Park Checkers | 2025-10-01 | 41353
Monument Park Checkers | 2025-11-01 | 44434
Monument Park Checkers | 2025-12-01 | 40551
Monument Park Checkers | 2026-01-01 | 42821
Monument Park Checkers | 2026-02-01 | 39129
Monument Park Checkers | 2026-03-01 | 31935
Monument Park Checkers | 2026-04-01 | 26513.02
Monument Park Checkers | 2026-05-01 | 29984.36
Monument Park Checkers | 2026-06-01 | 23145.12
Mdluli | 2026-07-01 | 13303
Monument Park Checkers | 2026-08-01 | 35675.901
Monument Park Checkers | 2026-09-01 | 33460.18
Monument Park Checkers | 2026-10-01
Monument Park Checkers | 2026-11-01
Monument Park Checkers | 2026-12-01
Nkambeni Industrial | 2024-01-01
Nkambeni Industrial | 2024-02-01
Nkambeni Industrial | 2024-03-01
Nkambeni Industrial | 2024-04-01
Nkambeni Industrial | 2024-05-01
Nkambeni Industrial | 2024-06-01
Nkambeni Industrial | 2024-07-01
Nkambeni Industrial | 2024-08-01
Nkambeni Industrial | 2024-09-01
Nkambeni Industrial | 2024-10-01
Nkambeni Industrial | 2024-11-01
Nkambeni Industrial | 2024-12-01
Nkambeni Industrial | 2025-01-01 | 21130
Nkambeni Industrial | 2025-02-01 | 17140
Nkambeni Industrial | 2025-03-01
Nkambeni Industrial | 2025-04-01
Nkambeni Industrial | 2025-05-01
Nkambeni Industrial | 2025-06-01
Nkambeni Industrial | 2025-07-01
Nkambeni Industrial | 2025-08-01
Nkambeni Industrial | 2025-09-01
Nkambeni Industrial | 2025-10-01
Nkambeni Industrial | 2025-11-01
Nkambeni Industrial | 2025-12-01
Nkambeni Industrial | 2026-01-01 | 9830
Nkambeni Industrial | 2026-02-01 | 20200
Nkambeni Industrial | 2026-03-01 | 16198
Nkambeni Industrial | 2026-04-01
Nkambeni Industrial | 2026-05-01
Nkambeni Industrial | 2026-06-01
Medipost | 2026-07-01 | 20358.73
Nkambeni Industrial | 2026-08-01
Nkambeni Industrial | 2026-09-01
Nkambeni Industrial | 2026-10-01
Nkambeni Industrial | 2026-11-01
Nkambeni Industrial | 2026-12-01
Olievenhoutbosch 1 | 2024-01-01
Olievenhoutbosch 1 | 2024-02-01
Olievenhoutbosch 1 | 2024-03-01
Olievenhoutbosch 1 | 2024-04-01
Olievenhoutbosch 1 | 2024-05-01
Olievenhoutbosch 1 | 2024-06-01
Olievenhoutbosch 1 | 2024-07-01
Olievenhoutbosch 1 | 2024-08-01
Olievenhoutbosch 1 | 2024-09-01
Olievenhoutbosch 1 | 2024-10-01
Olievenhoutbosch 1 | 2024-11-01
Olievenhoutbosch 1 | 2024-12-01
Olievenhoutbosch 1 | 2025-01-01
Olievenhoutbosch 1 | 2025-02-01
Olievenhoutbosch 1 | 2025-03-01
Olievenhoutbosch 1 | 2025-04-01
Olievenhoutbosch 1 | 2025-05-01
Olievenhoutbosch 1 | 2025-06-01
Olievenhoutbosch 1 | 2025-07-01
Olievenhoutbosch 1 | 2025-08-01
Olievenhoutbosch 1 | 2025-09-01
Olievenhoutbosch 1 | 2025-10-01 | 42200
Olievenhoutbosch 1 | 2025-11-01 | 37652
Olievenhoutbosch 1 | 2025-12-01 | 32569
Olievenhoutbosch 1 | 2026-01-01 | 43979.9977
Olievenhoutbosch 1 | 2026-02-01 | 35538.4873
Olievenhoutbosch 1 | 2026-03-01 | 34079
Olievenhoutbosch 1 | 2026-04-01 | 26385.27
Olievenhoutbosch 1 | 2026-05-01 | 29535.2
Mdluli | 2026-06-01 | 11309.7
Meredale Heights | 2026-07-01 | 5690
Olievenhoutbosch 1 | 2026-08-01 | 35179.4355
Olievenhoutbosch 1 | 2026-09-01 | 35252.9187
Olievenhoutbosch 1 | 2026-10-01
Olievenhoutbosch 1 | 2026-11-01
Olievenhoutbosch 1 | 2026-12-01
Olievenhoutbosch 2 | 2024-01-01
Olievenhoutbosch 2 | 2024-02-01
Olievenhoutbosch 2 | 2024-03-01
Olievenhoutbosch 2 | 2024-04-01
Olievenhoutbosch 2 | 2024-05-01
Olievenhoutbosch 2 | 2024-06-01
Olievenhoutbosch 2 | 2024-07-01
Olievenhoutbosch 2 | 2024-08-01
Olievenhoutbosch 2 | 2024-09-01
Olievenhoutbosch 2 | 2024-10-01
Olievenhoutbosch 2 | 2024-11-01
Olievenhoutbosch 2 | 2024-12-01
Olievenhoutbosch 2 | 2025-01-01
Olievenhoutbosch 2 | 2025-02-01
Olievenhoutbosch 2 | 2025-03-01
Olievenhoutbosch 2 | 2025-04-01
Olievenhoutbosch 2 | 2025-05-01
Olievenhoutbosch 2 | 2025-06-01
Olievenhoutbosch 2 | 2025-07-01
Olievenhoutbosch 2 | 2025-08-01
Olievenhoutbosch 2 | 2025-09-01
Olievenhoutbosch 2 | 2025-10-01 | 11800
Olievenhoutbosch 2 | 2025-11-01 | 9938
Olievenhoutbosch 2 | 2025-12-01 | 9094
Olievenhoutbosch 2 | 2026-01-01 | 11835.674
Olievenhoutbosch 2 | 2026-02-01 | 9479.8288
Olievenhoutbosch 2 | 2026-03-01 | 9043
Olievenhoutbosch 2 | 2026-04-01 | 7039.32
Olievenhoutbosch 2 | 2026-05-01 | 8144.81
Meredale Heights | 2026-06-01 | 4820.5
Monument Park Checkers | 2026-07-01 | 27326.29
Olievenhoutbosch 2 | 2026-08-01 | 9590.4249
Olievenhoutbosch 2 | 2026-09-01 | 9418.8442
Olievenhoutbosch 2 | 2026-10-01
Olievenhoutbosch 2 | 2026-11-01
Olievenhoutbosch 2 | 2026-12-01
Opal Students | 2024-01-01 | 337
Opal Students | 2024-02-01 | 4222
Opal Students | 2024-03-01 | 5410
Opal Students | 2024-04-01 | 4799
Opal Students | 2024-05-01 | 4368
Opal Students | 2024-06-01 | 3307
Opal Students | 2024-07-01 | 3819
Opal Students | 2024-08-01 | 5147
Opal Students | 2024-09-01 | 4101
Opal Students | 2024-10-01 | 6591
Opal Students | 2024-11-01 | 4960
Opal Students | 2024-12-01 | 652
Opal Students | 2025-01-01 | 720
Opal Students | 2025-02-01 | 3776
Opal Students | 2025-03-01 | 4415
Opal Students | 2025-04-01 | 3551
Opal Students | 2025-05-01 | 4580
Opal Students | 2025-06-01 | 3965.8
Opal Students | 2025-07-01 | 4015
Opal Students | 2025-08-01 | 4593
Opal Students | 2025-09-01 | 4428
Opal Students | 2025-10-01 | 6002
Opal Students | 2025-11-01 | 4286
Opal Students | 2025-12-01 | 985
Opal Students | 2026-01-01 | 1496.8
Opal Students | 2026-02-01 | 4735
Opal Students | 2026-03-01 | 4747
Opal Students | 2026-04-01 | 4036.9
Opal Students | 2026-05-01 | 4180
Olievenhoutbosch 1 | 2026-06-01 | 18559
Nkambeni Industrial | 2026-07-01 | 0
Opal Students | 2026-08-01 | 4901
Opal Students | 2026-09-01 | 4904
Opal Students | 2026-10-01
Opal Students | 2026-11-01
Opal Students | 2026-12-01
Orthochem Bethlehem | 2024-01-01 | 27336
Orthochem Bethlehem | 2024-02-01 | 34673
Orthochem Bethlehem | 2024-03-01 | 35335
Orthochem Bethlehem | 2024-04-01 | 23354
Orthochem Bethlehem | 2024-05-01 | 24682
Orthochem Bethlehem | 2024-06-01 | 21004
Orthochem Bethlehem | 2024-07-01 | 24855
Orthochem Bethlehem | 2024-08-01 | 27804
Orthochem Bethlehem | 2024-09-01 | 24854
Orthochem Bethlehem | 2024-10-01 | 41343
Orthochem Bethlehem | 2024-11-01 | 40614
Orthochem Bethlehem | 2024-12-01 | 20454
Orthochem Bethlehem | 2025-01-01 | 35500
Orthochem Bethlehem | 2025-02-01 | 33170
Orthochem Bethlehem | 2025-03-01 | 29562
Orthochem Bethlehem | 2025-04-01 | 23660
Orthochem Bethlehem | 2025-05-01 | 27021
Orthochem Bethlehem | 2025-06-01 | 23016.87
Orthochem Bethlehem | 2025-07-01 | 23980
Orthochem Bethlehem | 2025-08-01 | 26825
Orthochem Bethlehem | 2025-09-01 | 29989
Orthochem Bethlehem | 2025-10-01 | 39431.18
Orthochem Bethlehem | 2025-11-01 | 36933
Orthochem Bethlehem | 2025-12-01 | 24542
Orthochem Bethlehem | 2026-01-01 | 38558.8383
Orthochem Bethlehem | 2026-02-01 | 35289.5949
Orthochem Bethlehem | 2026-03-01 | 33082
Orthochem Bethlehem | 2026-04-01 | 26958.67
Orthochem Bethlehem | 2026-05-01 | 28264.56
Orthochem Bethlehem | 2026-06-01 | 20267.33
Olievenhoutbosch 1 | 2026-07-01 | 27717.5927
Orthochem Bethlehem | 2026-08-01 | 24964.912
Orthochem Bethlehem | 2026-09-01 | 22767.1484
Orthochem Bethlehem | 2026-10-01
Orthochem Bethlehem | 2026-11-01
Orthochem Bethlehem | 2026-12-01
PNB Unlimited | 2024-01-01 | 12283
PNB Unlimited | 2024-02-01 | 11752
PNB Unlimited | 2024-03-01 | 11293
PNB Unlimited | 2024-04-01 | 10034
PNB Unlimited | 2024-05-01 | 7886
PNB Unlimited | 2024-06-01 | 9067
PNB Unlimited | 2024-07-01 | 8952
PNB Unlimited | 2024-08-01 | 8952
PNB Unlimited | 2024-09-01 | 8110
PNB Unlimited | 2024-10-01 | 12770
PNB Unlimited | 2024-11-01 | 10951
PNB Unlimited | 2024-12-01 | 11135
PNB Unlimited | 2025-01-01 | 10294
PNB Unlimited | 2025-02-01 | 7952
PNB Unlimited | 2025-03-01 | 9856
PNB Unlimited | 2025-04-01 | 7739
PNB Unlimited | 2025-05-01 | 9189
PNB Unlimited | 2025-06-01 | 7656.32
PNB Unlimited | 2025-07-01 | 8158
PNB Unlimited | 2025-08-01 | 5429
PNB Unlimited | 2025-09-01 | 7249
PNB Unlimited | 2025-10-01 | 8107
PNB Unlimited | 2025-11-01 | 2305
PNB Unlimited | 2025-12-01 | 7641
PNB Unlimited | 2026-01-01 | 9717
PNB Unlimited | 2026-02-01 | 8045
PNB Unlimited | 2026-03-01 | 7035
PNB Unlimited | 2026-04-01 | 3742.54
PNB Unlimited | 2026-05-01 | 6041.14
PNB Unlimited | 2026-06-01 | 3334
Olievenhoutbosch 2 | 2026-07-01 | 7966.5733
PNB Unlimited | 2026-08-01 | 6624
PNB Unlimited | 2026-09-01 | 6723.42
PNB Unlimited | 2026-10-01
PNB Unlimited | 2026-11-01
PNB Unlimited | 2026-12-01
Plastiplate | 2024-01-01 | 4452
Plastiplate | 2024-02-01 | 6906
Plastiplate | 2024-03-01 | 6752
Plastiplate | 2024-04-01 | 6350
Plastiplate | 2024-05-01 | 7236
Plastiplate | 2024-06-01 | 6002
Plastiplate | 2024-07-01 | 7142
Plastiplate | 2024-08-01 | 6654
Plastiplate | 2024-09-01 | 6375
Plastiplate | 2024-10-01 | 6305
Plastiplate | 2024-11-01 | 7074
Plastiplate | 2024-12-01 | 3371
Plastiplate | 2025-01-01 | 5083
Plastiplate | 2025-02-01 | 4977
Plastiplate | 2025-03-01 | 5306
Plastiplate | 2025-04-01 | 4700
Plastiplate | 2025-05-01 | 6568
Plastiplate | 2025-06-01 | 6255.59
Plastiplate | 2025-07-01 | 5980
Plastiplate | 2025-08-01 | 6685
Plastiplate | 2025-09-01 | 7118
Plastiplate | 2025-10-01 | 7677
Plastiplate | 2025-11-01 | 5691
Plastiplate | 2025-12-01 | 3680
Plastiplate | 2026-01-01 | 5605
Plastiplate | 2026-02-01 | 7388
Plastiplate | 2026-03-01 | 6319.4
Plastiplate | 2026-04-01 | 4370.48
Plastiplate | 2026-05-01 | 5968.12
Olievenhoutbosch 2 | 2026-06-01 | 5600
Opal Students | 2026-07-01 | 3812
Plastiplate | 2026-08-01 | 6801
Plastiplate | 2026-09-01 | 6058.46
Plastiplate | 2026-10-01
Plastiplate | 2026-11-01
Plastiplate | 2026-12-01
Q-lity Meat | 2024-01-01 | 4700
Q-lity Meat | 2024-02-01 | 4300
Q-lity Meat | 2024-03-01 | 5200
Q-lity Meat | 2024-04-01 | 4500
Q-lity Meat | 2024-05-01 | 4300
Q-lity Meat | 2024-06-01 | 3800
Q-lity Meat | 2024-07-01 | 4100
Q-lity Meat | 2024-08-01 | 4000
Q-lity Meat | 2024-09-01 | 3700
Q-lity Meat | 2024-10-01 | 5479
Q-lity Meat | 2024-11-01 | 5500
Q-lity Meat | 2024-12-01 | 2742
Q-lity Meat | 2025-01-01 | 5100
Q-lity Meat | 2025-02-01 | 3970
Q-lity Meat | 2025-03-01 | 4540
Q-lity Meat | 2025-04-01 | 3526
Q-lity Meat | 2025-05-01 | 4309
Q-lity Meat | 2025-06-01 | 3564
Q-lity Meat | 2025-07-01 | 3444
Q-lity Meat | 2025-08-01 | 4434
Q-lity Meat | 2025-09-01 | 4300
Q-lity Meat | 2025-10-01 | 4956
Q-lity Meat | 2025-11-01 | 4173
Q-lity Meat | 2025-12-01 | 5010
Q-lity Meat | 2026-01-01 | 4573
Q-lity Meat | 2026-02-01 | 4586.77
Q-lity Meat | 2026-03-01 | 4089
Q-lity Meat | 2026-04-01 | 844.2
Q-lity Meat | 2026-05-01 | 0
Q-lity Meat | 2026-06-01
Orthochem Bethlehem | 2026-07-01 | 25915.637
Q-lity Meat | 2026-08-01
Q-lity Meat | 2026-09-01 | 0
Q-lity Meat | 2026-10-01
Q-lity Meat | 2026-11-01
Q-lity Meat | 2026-12-01
Quintondale | 2024-01-01 | 6159
Quintondale | 2024-02-01 | 4495
Quintondale | 2024-03-01 | 5040
Quintondale | 2024-04-01 | 4485
Quintondale | 2024-05-01 | 4861
Quintondale | 2024-06-01 | 3929
Quintondale | 2024-07-01 | 4619
Quintondale | 2024-08-01 | 5354
Quintondale | 2024-09-01 | 4908
Quintondale | 2024-10-01 | 6335
Quintondale | 2024-11-01 | 5824
Quintondale | 2024-12-01 | 6091
Quintondale | 2025-01-01 | 5309
Quintondale | 2025-02-01 | 3761
Quintondale | 2025-03-01 | 4074
Quintondale | 2025-04-01 | 3902
Quintondale | 2025-05-01 | 5047
Quintondale | 2025-06-01 | 4585.36
Quintondale | 2025-07-01 | 4750
Quintondale | 2025-08-01 | 4940
Quintondale | 2025-09-01 | 4923
Quintondale | 2025-10-01 | 5673
Quintondale | 2025-11-01 | 4641
Quintondale | 2025-12-01 | 5262
Quintondale | 2026-01-01 | 5546
Quintondale | 2026-02-01 | 5201.23
Quintondale | 2026-03-01 | 4579
Quintondale | 2026-04-01 | 4134.11
Quintondale | 2026-05-01 | 4665.67
Quintondale | 2026-06-01 | 3785
Plastiplate | 2026-07-01 | 6917
Quintondale | 2026-08-01 | 5246
Quintondale | 2026-09-01 | 4995.41
Quintondale | 2026-10-01
Quintondale | 2026-11-01
Quintondale | 2026-12-01
Riverside Lodge | 2024-01-01 | 6600
Riverside Lodge | 2024-02-01 | 13300
Riverside Lodge | 2024-03-01 | 15420
Riverside Lodge | 2024-04-01 | 12860
Riverside Lodge | 2024-05-01 | 14610
Riverside Lodge | 2024-06-01 | 12010
Riverside Lodge | 2024-07-01 | 13050
Riverside Lodge | 2024-08-01 | 17380
Riverside Lodge | 2024-09-01 | 15040
Riverside Lodge | 2024-10-01 | 16040
Riverside Lodge | 2024-11-01 | 12800
Riverside Lodge | 2024-12-01 | 11928
Riverside Lodge | 2025-01-01 | 11300
Riverside Lodge | 2025-02-01 | 8382
Riverside Lodge | 2025-03-01 | 11945
Riverside Lodge | 2025-04-01 | 13271
Riverside Lodge | 2025-05-01 | 17380
Riverside Lodge | 2025-06-01 | 15760.44
Riverside Lodge | 2025-07-01 | 15336
Riverside Lodge | 2025-08-01 | 18373
Riverside Lodge | 2025-09-01 | 14826
Riverside Lodge | 2025-10-01 | 14653
Riverside Lodge | 2025-11-01 | 11613
Riverside Lodge | 2025-12-01 | 12623
Riverside Lodge | 2026-01-01 | 13947
Riverside Lodge | 2026-02-01 | 15878
Riverside Lodge | 2026-03-01 | 15307
Riverside Lodge | 2026-04-01 | 13475.98
Riverside Lodge | 2026-05-01 | 16989.47
Opal Students | 2026-06-01 | 3164
PNB Unlimited | 2026-07-01 | 6388
Riverside Lodge | 2026-08-01 | 18348
Riverside Lodge | 2026-09-01 | 16094
Riverside Lodge | 2026-10-01
Riverside Lodge | 2026-11-01
Riverside Lodge | 2026-12-01
SR Morula TF 1 | 2024-01-01
SR Morula TF 1 | 2024-02-01
SR Morula TF 1 | 2024-03-01
SR Morula TF 1 | 2024-04-01
SR Morula TF 1 | 2024-05-01
SR Morula TF 1 | 2024-06-01
SR Morula TF 1 | 2024-07-01
SR Morula TF 1 | 2024-08-01
SR Morula TF 1 | 2024-09-01
SR Morula TF 1 | 2024-10-01
SR Morula TF 1 | 2024-11-01
SR Morula TF 1 | 2024-12-01
SR Morula TF 1 | 2025-01-01
SR Morula TF 1 | 2025-02-01
SR Morula TF 1 | 2025-03-01
SR Morula TF 1 | 2025-04-01
SR Morula TF 1 | 2025-05-01
SR Morula TF 1 | 2025-06-01
SR Morula TF 1 | 2025-07-01
SR Morula TF 1 | 2025-08-01 | 2845
SR Morula TF 1 | 2025-09-01 | 7367
SR Morula TF 1 | 2025-10-01 | 8824
SR Morula TF 1 | 2025-11-01 | 7686
SR Morula TF 1 | 2025-12-01 | 9330
SR Morula TF 1 | 2026-01-01 | 9387
SR Morula TF 1 | 2026-02-01 | 8600
SR Morula TF 1 | 2026-03-01 | 6749
SR Morula TF 1 | 2026-04-01 | 6091.51
SR Morula TF 1 | 2026-05-01 | 6169.97
Plastiplate | 2026-06-01 | 5956
Q-lity Meat | 2026-07-01 | 0
SR Morula TF 1 | 2026-08-01 | 6659
SR Morula TF 1 | 2026-09-01 | 6939.4893
SR Morula TF 1 | 2026-10-01
SR Morula TF 1 | 2026-11-01
SR Morula TF 1 | 2026-12-01
SR Morula TF 1 - Shoprite | 2024-01-01
SR Morula TF 1 - Shoprite | 2024-02-01
SR Morula TF 1 - Shoprite | 2024-03-01
SR Morula TF 1 - Shoprite | 2024-04-01
SR Morula TF 1 - Shoprite | 2024-05-01
SR Morula TF 1 - Shoprite | 2024-06-01
SR Morula TF 1 - Shoprite | 2024-07-01
SR Morula TF 1 - Shoprite | 2024-08-01
SR Morula TF 1 - Shoprite | 2024-09-01
SR Morula TF 1 - Shoprite | 2024-10-01
SR Morula TF 1 - Shoprite | 2024-11-01
SR Morula TF 1 - Shoprite | 2024-12-01
SR Morula TF 1 - Shoprite | 2025-01-01
SR Morula TF 1 - Shoprite | 2025-02-01
SR Morula TF 1 - Shoprite | 2025-03-01
SR Morula TF 1 - Shoprite | 2025-04-01
SR Morula TF 1 - Shoprite | 2025-05-01
SR Morula TF 1 - Shoprite | 2025-06-01
SR Morula TF 1 - Shoprite | 2025-07-01
SR Morula TF 1 - Shoprite | 2025-08-01 | 8229
SR Morula TF 1 - Shoprite | 2025-09-01 | 21334
SR Morula TF 1 - Shoprite | 2025-10-01 | 26578
SR Morula TF 1 - Shoprite | 2025-11-01 | 22629
SR Morula TF 1 - Shoprite | 2025-12-01 | 27791
SR Morula TF 1 - Shoprite | 2026-01-01 | 27879
SR Morula TF 1 - Shoprite | 2026-02-01 | 25500
SR Morula TF 1 - Shoprite | 2026-03-01 | 20753
SR Morula TF 1 - Shoprite | 2026-04-01 | 18061.39
SR Morula TF 1 - Shoprite | 2026-05-01 | 18908.48
SR Morula TF 1 - Shoprite | 2026-06-01 | 14035.5
Quintondale | 2026-07-01 | 4628
SR Morula TF 1 - Shoprite | 2026-08-01 | 20112.53
SR Morula TF 1 - Shoprite | 2026-09-01 | 20045.69
SR Morula TF 1 - Shoprite | 2026-10-01
SR Morula TF 1 - Shoprite | 2026-11-01
SR Morula TF 1 - Shoprite | 2026-12-01
SR Morula TF 2 | 2024-01-01
SR Morula TF 2 | 2024-02-01
SR Morula TF 2 | 2024-03-01
SR Morula TF 2 | 2024-04-01
SR Morula TF 2 | 2024-05-01
SR Morula TF 2 | 2024-06-01
SR Morula TF 2 | 2024-07-01
SR Morula TF 2 | 2024-08-01
SR Morula TF 2 | 2024-09-01
SR Morula TF 2 | 2024-10-01
SR Morula TF 2 | 2024-11-01
SR Morula TF 2 | 2024-12-01
SR Morula TF 2 | 2025-01-01
SR Morula TF 2 | 2025-02-01
SR Morula TF 2 | 2025-03-01
SR Morula TF 2 | 2025-04-01
SR Morula TF 2 | 2025-05-01
SR Morula TF 2 | 2025-06-01
SR Morula TF 2 | 2025-07-01
SR Morula TF 2 | 2025-08-01 | 2512
SR Morula TF 2 | 2025-09-01 | 7570
SR Morula TF 2 | 2025-10-01 | 8856
SR Morula TF 2 | 2025-11-01 | 7508
SR Morula TF 2 | 2025-12-01 | 9313
SR Morula TF 2 | 2026-01-01 | 9484
SR Morula TF 2 | 2026-02-01 | 8425.8
SR Morula TF 2 | 2026-03-01 | 7083
SR Morula TF 2 | 2026-04-01 | 6207.8
SR Morula TF 2 | 2026-05-01 | 6478.04
Riverside Lodge | 2026-06-01 | 13699
Riverside Lodge | 2026-07-01 | 16691
SR Morula TF 2 | 2026-08-01 | 2900
SR Morula TF 2 | 2026-09-01 | 6579.8013
SR Morula TF 2 | 2026-10-01
SR Morula TF 2 | 2026-11-01
SR Morula TF 2 | 2026-12-01
Sakhumnotho | 2024-01-01 | 1720
Sakhumnotho | 2024-02-01 | 1864
Sakhumnotho | 2024-03-01 | 2167
Sakhumnotho | 2024-04-01 | 1409
Sakhumnotho | 2024-05-01 | 1672
Sakhumnotho | 2024-06-01 | 1125
Sakhumnotho | 2024-07-01 | 2628
Sakhumnotho | 2024-08-01 | 794
Sakhumnotho | 2024-09-01 | 1822
Sakhumnotho | 2024-10-01 | 2044
Sakhumnotho | 2024-11-01 | 1984
Sakhumnotho | 2024-12-01 | 1687
Sakhumnotho | 2025-01-01 | 2354
Sakhumnotho | 2025-02-01 | 1728
Sakhumnotho | 2025-03-01 | 1704
Sakhumnotho | 2025-04-01 | 1518
Sakhumnotho | 2025-05-01 | 2450
Sakhumnotho | 2025-06-01 | 2470.27
Sakhumnotho | 2025-07-01 | 2714
Sakhumnotho | 2025-08-01 | 2694
Sakhumnotho | 2025-09-01 | 1488
Sakhumnotho | 2025-10-01 | 380
Sakhumnotho | 2025-11-01
Sakhumnotho | 2025-12-01
Sakhumnotho | 2026-01-01
Sakhumnotho | 2026-02-01
Sakhumnotho | 2026-03-01
Sakhumnotho | 2026-04-01
Sakhumnotho | 2026-05-01
Sakhumnotho | 2026-06-01
Roan Foods | 2026-07-01 | 10570
Sakhumnotho | 2026-08-01
Sakhumnotho | 2026-09-01
Sakhumnotho | 2026-10-01
Sakhumnotho | 2026-11-01
Sakhumnotho | 2026-12-01
SaveMore Alldays - Store | 2024-01-01 | 17948
SaveMore Alldays - Store | 2024-02-01 | 16954
SaveMore Alldays - Store | 2024-03-01 | 16498
SaveMore Alldays - Store | 2024-04-01 | 13514
SaveMore Alldays - Store | 2024-05-01 | 13524
SaveMore Alldays - Store | 2024-06-01 | 11348
SaveMore Alldays - Store | 2024-07-01 | 12215
SaveMore Alldays - Store | 2024-08-01 | 12637
SaveMore Alldays - Store | 2024-09-01 | 12990
SaveMore Alldays - Store | 2024-10-01 | 10518
SaveMore Alldays - Store | 2024-11-01 | 5878
SaveMore Alldays - Store | 2024-12-01 | 17496
SaveMore Alldays - Store | 2025-01-01 | 16026
SaveMore Alldays - Store | 2025-02-01 | 13689
SaveMore Alldays - Store | 2025-03-01 | 11995
SaveMore Alldays - Store | 2025-04-01 | 6680
SaveMore Alldays - Store | 2025-05-01 | 11933
SaveMore Alldays - Store | 2025-06-01 | 9797.26
SaveMore Alldays - Store | 2025-07-01 | 9134.4
SaveMore Alldays - Store | 2025-08-01 | 15551
SaveMore Alldays - Store | 2025-09-01 | 14894
SaveMore Alldays - Store | 2025-10-01 | 17167
SaveMore Alldays - Store | 2025-11-01 | 14437
SaveMore Alldays - Store | 2025-12-01 | 14721
SaveMore Alldays - Store | 2026-01-01 | 16129
SaveMore Alldays - Store | 2026-02-01 | 15901
SaveMore Alldays - Store | 2026-03-01 | 13942
SaveMore Alldays - Store | 2026-04-01 | 12240.56
SaveMore Alldays - Store | 2026-05-01 | 12352.61
SaveMore Alldays - Store | 2026-06-01 | 11089
Sakhumnotho | 2026-07-01 | 0
SaveMore Alldays - Store | 2026-08-01 | 13852
SaveMore Alldays - Store | 2026-09-01 | 13027.93
SaveMore Alldays - Store | 2026-10-01
SaveMore Alldays - Store | 2026-11-01
SaveMore Alldays - Store | 2026-12-01
Savemore Liquor Alldays | 2024-01-01 | 1424
Savemore Liquor Alldays | 2024-02-01 | 1471
Savemore Liquor Alldays | 2024-03-01 | 1705
Savemore Liquor Alldays | 2024-04-01 | 1306
Savemore Liquor Alldays | 2024-05-01 | 856
Savemore Liquor Alldays | 2024-06-01 | 1086
Savemore Liquor Alldays | 2024-07-01 | 1232
Savemore Liquor Alldays | 2024-08-01 | 1007
Savemore Liquor Alldays | 2024-09-01 | 1218
Savemore Liquor Alldays | 2024-10-01 | 1389
Savemore Liquor Alldays | 2024-11-01 | 1731
Savemore Liquor Alldays | 2024-12-01 | 1418
Savemore Liquor Alldays | 2025-01-01 | 1493
Savemore Liquor Alldays | 2025-02-01 | 1368.9
Savemore Liquor Alldays | 2025-03-01 | 960
Savemore Liquor Alldays | 2025-04-01 | 694
Savemore Liquor Alldays | 2025-05-01 | 580
Savemore Liquor Alldays | 2025-06-01 | 449.2
Savemore Liquor Alldays | 2025-07-01 | 575
Savemore Liquor Alldays | 2025-08-01 | 1437
Savemore Liquor Alldays | 2025-09-01 | 1257
Savemore Liquor Alldays | 2025-10-01 | 1616
Savemore Liquor Alldays | 2025-11-01 | 1463
Savemore Liquor Alldays | 2025-12-01 | 1836
Savemore Liquor Alldays | 2026-01-01 | 1637
Savemore Liquor Alldays | 2026-02-01 | 1801
Savemore Liquor Alldays | 2026-03-01 | 1516
Savemore Liquor Alldays | 2026-04-01 | 1353.29
Savemore Liquor Alldays | 2026-05-01 | 1302.09
Savemore Liquor Alldays | 2026-06-01 | 1100
SaveMore Alldays - Store | 2026-07-01 | 12059
Savemore Liquor Alldays | 2026-08-01 | 1071
Savemore Liquor Alldays | 2026-09-01 | 1290.91
Savemore Liquor Alldays | 2026-10-01
Savemore Liquor Alldays | 2026-11-01
Savemore Liquor Alldays | 2026-12-01
Saverite Durban | 2024-01-01 | 8341
Saverite Durban | 2024-02-01 | 8056
Saverite Durban | 2024-03-01 | 7588
Saverite Durban | 2024-04-01 | 6746
Saverite Durban | 2024-05-01 | 6595
Saverite Durban | 2024-06-01 | 5221
Saverite Durban | 2024-07-01 | 6498
Saverite Durban | 2024-08-01 | 6727
Saverite Durban | 2024-09-01 | 5408
Saverite Durban | 2024-10-01 | 8018
Saverite Durban | 2024-11-01 | 7818
Saverite Durban | 2024-12-01 | 9041
Saverite Durban | 2025-01-01 | 9601
Saverite Durban | 2025-02-01 | 7317
Saverite Durban | 2025-03-01 | 8211
Saverite Durban | 2025-04-01 | 6924
Saverite Durban | 2025-05-01 | 7428
Saverite Durban | 2025-06-01 | 7026.25
Saverite Durban | 2025-07-01 | 7318
Saverite Durban | 2025-08-01 | 7873
Saverite Durban | 2025-09-01 | 6985
Saverite Durban | 2025-10-01 | 9680.31
Saverite Durban | 2025-11-01 | 11102
Saverite Durban | 2025-12-01 | 11384
Saverite Durban | 2026-01-01 | 12215
Saverite Durban | 2026-02-01 | 11691
Saverite Durban | 2026-03-01 | 10159
Saverite Durban | 2026-04-01 | 8032.01
Saverite Durban | 2026-05-01 | 7738.42
Saverite Durban | 2026-06-01 | 6442
Savemore Liquor Alldays | 2026-07-01 | 1098
Saverite Durban | 2026-08-01 | 8202
Saverite Durban | 2026-09-01 | 7731.86
Saverite Durban | 2026-10-01
Saverite Durban | 2026-11-01
Saverite Durban | 2026-12-01
Saverite PMB | 2024-01-01 | 11804
Saverite PMB | 2024-02-01 | 9158
Saverite PMB | 2024-03-01 | 9784
Saverite PMB | 2024-04-01 | 7858
Saverite PMB | 2024-05-01 | 7246
Saverite PMB | 2024-06-01 | 6127
Saverite PMB | 2024-07-01 | 8521
Saverite PMB | 2024-08-01 | 9050
Saverite PMB | 2024-09-01 | 8302
Saverite PMB | 2024-10-01 | 11290
Saverite PMB | 2024-11-01 | 10513
Saverite PMB | 2024-12-01 | 11507
Saverite PMB | 2025-01-01 | 11679
Saverite PMB | 2025-02-01 | 7567
Saverite PMB | 2025-03-01 | 9564
Saverite PMB | 2025-04-01 | 6957
Saverite PMB | 2025-05-01 | 7705
Saverite PMB | 2025-06-01 | 6515.6
Saverite PMB | 2025-07-01 | 7651
Saverite PMB | 2025-08-01 | 8548
Saverite PMB | 2025-09-01 | 7542
Saverite PMB | 2025-10-01 | 10186
Saverite PMB | 2025-11-01 | 10802
Saverite PMB | 2025-12-01 | 11033
Saverite PMB | 2026-01-01 | 7790
Saverite PMB | 2026-02-01 | 5171.0647
Saverite PMB | 2026-03-01 | 8153.5
Saverite PMB | 2026-04-01 | 7873.17
Saverite PMB | 2026-05-01 | 7767.8
Saverite PMB | 2026-06-01 | 7190.68
Saverite Durban | 2026-07-01 | 6823
Saverite PMB | 2026-08-01 | 9679.5108
Saverite PMB | 2026-09-01 | 8602.5566
Saverite PMB | 2026-10-01
Saverite PMB | 2026-11-01
Saverite PMB | 2026-12-01
Secunda Plaza Shops | 2024-01-01 | 4297
Secunda Plaza Shops | 2024-02-01 | 4176
Secunda Plaza Shops | 2024-03-01 | 4682
Secunda Plaza Shops | 2024-04-01 | 3965
Secunda Plaza Shops | 2024-05-01 | 3760
Secunda Plaza Shops | 2024-06-01 | 3240
Secunda Plaza Shops | 2024-07-01 | 3836
Secunda Plaza Shops | 2024-08-01 | 3915
Secunda Plaza Shops | 2024-09-01 | 3746
Secunda Plaza Shops | 2024-10-01 | 3449
Secunda Plaza Shops | 2024-11-01 | 4630
Secunda Plaza Shops | 2024-12-01 | 5059
Secunda Plaza Shops | 2025-01-01 | 4475
Secunda Plaza Shops | 2025-02-01 | 3651
Secunda Plaza Shops | 2025-03-01 | 3912
Secunda Plaza Shops | 2025-04-01 | 3361
Secunda Plaza Shops | 2025-05-01 | 3626
Secunda Plaza Shops | 2025-06-01 | 3199.19
Secunda Plaza Shops | 2025-07-01 | 3303
Secunda Plaza Shops | 2025-08-01 | 3882
Secunda Plaza Shops | 2025-09-01 | 4064
Secunda Plaza Shops | 2025-10-01 | 4609
Secunda Plaza Shops | 2025-11-01 | 3681
Secunda Plaza Shops | 2025-12-01 | 1203
Secunda Plaza Shops | 2026-01-01 | 3014
Secunda Plaza Shops | 2026-02-01 | 4641.05
Secunda Plaza Shops | 2026-03-01 | 3756
Secunda Plaza Shops | 2026-04-01 | 3294.1
Secunda Plaza Shops | 2026-05-01 | 3420.82
Secunda Plaza Shops | 2026-06-01 | 2882
Saverite PMB | 2026-07-01 | 6825.8941
Secunda Plaza Shops | 2026-08-01 | 3905
Secunda Plaza Shops | 2026-09-01 | 3972.39
Secunda Plaza Shops | 2026-10-01
Secunda Plaza Shops | 2026-11-01
Secunda Plaza Shops | 2026-12-01
Secunda Plaza choppies | 2024-01-01 | 14153
Secunda Plaza choppies | 2024-02-01 | 12255
Secunda Plaza choppies | 2024-03-01 | 14981
Secunda Plaza choppies | 2024-04-01 | 12548
Secunda Plaza choppies | 2024-05-01 | 12499
Secunda Plaza choppies | 2024-06-01 | 10764
Secunda Plaza choppies | 2024-07-01 | 12646
Secunda Plaza choppies | 2024-08-01 | 13284
Secunda Plaza choppies | 2024-09-01 | 12781
Secunda Plaza choppies | 2024-10-01 | 16310
Secunda Plaza choppies | 2024-11-01 | 16857
Secunda Plaza choppies | 2024-12-01 | 17902
Secunda Plaza choppies | 2025-01-01 | 16357
Secunda Plaza choppies | 2025-02-01 | 13076
Secunda Plaza choppies | 2025-03-01 | 13410
Secunda Plaza choppies | 2025-04-01 | 11361
Secunda Plaza choppies | 2025-05-01 | 12073
Secunda Plaza choppies | 2025-06-01 | 10687.39
Secunda Plaza choppies | 2025-07-01 | 10449
Secunda Plaza choppies | 2025-08-01 | 10325
Secunda Plaza choppies | 2025-09-01 | 9595
Secunda Plaza choppies | 2025-10-01 | 11068
Secunda Plaza choppies | 2025-11-01 | 10671
Secunda Plaza choppies | 2025-12-01 | 1812
Secunda Plaza choppies | 2026-01-01 | 306
Secunda Plaza choppies | 2026-02-01 | 522.4446
Secunda Plaza choppies | 2026-03-01 | 372
Secunda Plaza choppies | 2026-04-01 | 44.97
Secunda Plaza choppies | 2026-05-01 | 0
Secunda Plaza choppies | 2026-06-01
Secunda Plaza choppies | 2026-07-01 | 0
Secunda Plaza choppies | 2026-08-01
Secunda Plaza choppies | 2026-09-01 | 0
Secunda Plaza choppies | 2026-10-01
Secunda Plaza choppies | 2026-11-01
Secunda Plaza choppies | 2026-12-01
Shoprite Dube | 2024-01-01
Shoprite Dube | 2024-02-01
Shoprite Dube | 2024-03-01
Shoprite Dube | 2024-04-01
Shoprite Dube | 2024-05-01
Shoprite Dube | 2024-06-01
Shoprite Dube | 2024-07-01
Shoprite Dube | 2024-08-01
Shoprite Dube | 2024-09-01
Shoprite Dube | 2024-10-01
Shoprite Dube | 2024-11-01
Shoprite Dube | 2024-12-01
Shoprite Dube | 2025-01-01 | 10100
Shoprite Dube | 2025-02-01 | 12001
Shoprite Dube | 2025-03-01 | 13213
Shoprite Dube | 2025-04-01 | 9636
Shoprite Dube | 2025-05-01 | 10261
Shoprite Dube | 2025-06-01 | 11348.4
Shoprite Dube | 2025-07-01 | 14705
Shoprite Dube | 2025-08-01 | 16958
Shoprite Dube | 2025-09-01 | 17766
Shoprite Dube | 2025-10-01 | 22849
Shoprite Dube | 2025-11-01 | 20014
Shoprite Dube | 2025-12-01 | 21334.1162
Shoprite Dube | 2026-01-01 | 23434
Shoprite Dube | 2026-02-01 | 21742.1962
Shoprite Dube | 2026-03-01 | 18523
Shoprite Dube | 2026-04-01 | 15379.43
Shoprite Dube | 2026-05-01 | 15576.52
Shoprite Dube | 2026-06-01 | 12252.53
Secunda Plaza Shops | 2026-07-01 | 2926.66
Shoprite Dube | 2026-08-01 | 17067.58
Shoprite Dube | 2026-09-01 | 18587.26
Shoprite Dube | 2026-10-01
Shoprite Dube | 2026-11-01
Shoprite Dube | 2026-12-01
Shoprite Ekhaya | 2024-01-01
Shoprite Ekhaya | 2024-02-01
Shoprite Ekhaya | 2024-03-01
Shoprite Ekhaya | 2024-04-01
Shoprite Ekhaya | 2024-05-01
Shoprite Ekhaya | 2024-06-01
Shoprite Ekhaya | 2024-07-01
Shoprite Ekhaya | 2024-08-01
Shoprite Ekhaya | 2024-09-01
Shoprite Ekhaya | 2024-10-01
Shoprite Ekhaya | 2024-11-01
Shoprite Ekhaya | 2024-12-01
Shoprite Ekhaya | 2025-01-01
Shoprite Ekhaya | 2025-02-01
Shoprite Ekhaya | 2025-03-01
Shoprite Ekhaya | 2025-04-01
Shoprite Ekhaya | 2025-05-01
Shoprite Ekhaya | 2025-06-01
Shoprite Ekhaya | 2025-07-01
Shoprite Ekhaya | 2025-08-01
Shoprite Ekhaya | 2025-09-01
Shoprite Ekhaya | 2025-10-01
Shoprite Ekhaya | 2025-11-01
Shoprite Ekhaya | 2025-12-01
Shoprite Ekhaya | 2026-01-01
Shoprite Ekhaya | 2026-02-01
Shoprite Ekhaya | 2026-03-01 | 10022
Shoprite Ekhaya | 2026-04-01 | 11511.86
Shoprite Ekhaya | 2026-05-01 | 14709.43
Shoprite Ekhaya | 2026-06-01 | 12264.7
Shoprite Dube | 2026-07-01 | 13658
Shoprite Ekhaya | 2026-08-01 | 16951.843
Shoprite Ekhaya | 2026-09-01 | 20723.3362
Shoprite Ekhaya | 2026-10-01
Shoprite Ekhaya | 2026-11-01
Shoprite Ekhaya | 2026-12-01
Shoprite Hillbrow | 2024-01-01
Shoprite Hillbrow | 2024-02-01
Shoprite Hillbrow | 2024-03-01
Shoprite Hillbrow | 2024-04-01
Shoprite Hillbrow | 2024-05-01
Shoprite Hillbrow | 2024-06-01
Shoprite Hillbrow | 2024-07-01
Shoprite Hillbrow | 2024-08-01
Shoprite Hillbrow | 2024-09-01
Shoprite Hillbrow | 2024-10-01
Shoprite Hillbrow | 2024-11-01
Shoprite Hillbrow | 2024-12-01
Shoprite Hillbrow | 2025-01-01 | 18900
Shoprite Hillbrow | 2025-02-01 | 13110
Shoprite Hillbrow | 2025-03-01 | 11124
Shoprite Hillbrow | 2025-04-01 | 9398
Shoprite Hillbrow | 2025-05-01 | 10507
Shoprite Hillbrow | 2025-06-01 | 8615
Shoprite Hillbrow | 2025-07-01 | 9297
Shoprite Hillbrow | 2025-08-01 | 11805
Shoprite Hillbrow | 2025-09-01 | 12829
Shoprite Hillbrow | 2025-10-01 | 18800
Shoprite Hillbrow | 2025-11-01 | 15186
Shoprite Hillbrow | 2025-12-01 | 17488.2707
Shoprite Hillbrow | 2026-01-01 | 18755
Shoprite Hillbrow | 2026-02-01 | 15395.7162
Shoprite Hillbrow | 2026-03-01 | 11700
Shoprite Hillbrow | 2026-04-01 | 8798.96
Shoprite Hillbrow | 2026-05-01 | 8378.25
Shoprite Hillbrow | 2026-06-01 | 6213.16
Shoprite Ekhaya | 2026-07-01 | 11339.6067
Shoprite Hillbrow | 2026-08-01 | 9821.36
Shoprite Hillbrow | 2026-09-01 | 11626.59
Shoprite Hillbrow | 2026-10-01
Shoprite Hillbrow | 2026-11-01
Shoprite Hillbrow | 2026-12-01
Shoprite Ladybrand | 2024-01-01
Shoprite Ladybrand | 2024-02-01
Shoprite Ladybrand | 2024-03-01
Shoprite Ladybrand | 2024-04-01
Shoprite Ladybrand | 2024-05-01
Shoprite Ladybrand | 2024-06-01
Shoprite Ladybrand | 2024-07-01
Shoprite Ladybrand | 2024-08-01
Shoprite Ladybrand | 2024-09-01
Shoprite Ladybrand | 2024-10-01
Shoprite Ladybrand | 2024-11-01
Shoprite Ladybrand | 2024-12-01
Shoprite Ladybrand | 2025-01-01 | 33100
Shoprite Ladybrand | 2025-02-01 | 24950
Shoprite Ladybrand | 2025-03-01 | 24126
Shoprite Ladybrand | 2025-04-01 | 18837
Shoprite Ladybrand | 2025-05-01 | 22373
Shoprite Ladybrand | 2025-06-01 | 18416.6
Shoprite Ladybrand | 2025-07-01 | 19123
Shoprite Ladybrand | 2025-08-01 | 22404
Shoprite Ladybrand | 2025-09-01 | 21900
Shoprite Ladybrand | 2025-10-01 | 29612
Shoprite Ladybrand | 2025-11-01 | 26751
Shoprite Ladybrand | 2025-12-01 | 30623.1004
Shoprite Ladybrand | 2026-01-01 | 34009
Shoprite Ladybrand | 2026-02-01 | 24602.8829
Shoprite Ladybrand | 2026-03-01 | 23540
Shoprite Ladybrand | 2026-04-01 | 18199.29
Shoprite Ladybrand | 2026-05-01 | 17860.55
Shoprite Ladybrand | 2026-06-01 | 14774.05
Shoprite Hillbrow | 2026-07-01 | 6980.78
Shoprite Ladybrand | 2026-08-01 | 21703.83
Shoprite Ladybrand | 2026-09-01 | 20441.04
Shoprite Ladybrand | 2026-10-01
Shoprite Ladybrand | 2026-11-01
Shoprite Ladybrand | 2026-12-01
Shoprite Mini Ganyesa | 2024-01-01
Shoprite Mini Ganyesa | 2024-02-01
Shoprite Mini Ganyesa | 2024-03-01
Shoprite Mini Ganyesa | 2024-04-01
Shoprite Mini Ganyesa | 2024-05-01
Shoprite Mini Ganyesa | 2024-06-01
Shoprite Mini Ganyesa | 2024-07-01
Shoprite Mini Ganyesa | 2024-08-01 | 3670
Shoprite Mini Ganyesa | 2024-09-01 | 24226
Shoprite Mini Ganyesa | 2024-10-01 | 29060
Shoprite Mini Ganyesa | 2024-11-01 | 28700
Shoprite Mini Ganyesa | 2024-12-01 | 32654
Shoprite Mini Ganyesa | 2025-01-01 | 31900
Shoprite Mini Ganyesa | 2025-02-01 | 24980
Shoprite Mini Ganyesa | 2025-03-01 | 24068
Shoprite Mini Ganyesa | 2025-04-01 | 17329
Shoprite Mini Ganyesa | 2025-05-01 | 19241
Shoprite Mini Ganyesa | 2025-06-01 | 18515.91
Shoprite Mini Ganyesa | 2025-07-01 | 18781
Shoprite Mini Ganyesa | 2025-08-01 | 21235
Shoprite Mini Ganyesa | 2025-09-01 | 23085
Shoprite Mini Ganyesa | 2025-10-01 | 25611
Shoprite Mini Ganyesa | 2025-11-01 | 25276
Shoprite Mini Ganyesa | 2025-12-01 | 28457.1296
Shoprite Mini Ganyesa | 2026-01-01 | 29092
Shoprite Mini Ganyesa | 2026-02-01 | 23486.9398
Shoprite Mini Ganyesa | 2026-03-01 | 22459
Shoprite Mini Ganyesa | 2026-04-01 | 18207.86
Shoprite Mini Ganyesa | 2026-05-01 | 17848.83
Shoprite Mini Ganyesa | 2026-06-01 | 14983.63
Shoprite Ladybrand | 2026-07-01 | 17814.88
Shoprite Mini Ganyesa | 2026-08-01 | 20218.59
Shoprite Mini Ganyesa | 2026-09-01 | 17902.21
Shoprite Mini Ganyesa | 2026-10-01
Shoprite Mini Ganyesa | 2026-11-01
Shoprite Mini Ganyesa | 2026-12-01
Shoprite Naledi | 2024-01-01
Shoprite Naledi | 2024-02-01
Shoprite Naledi | 2024-03-01
Shoprite Naledi | 2024-04-01
Shoprite Naledi | 2024-05-01
Shoprite Naledi | 2024-06-01
Shoprite Naledi | 2024-07-01
Shoprite Naledi | 2024-08-01
Shoprite Naledi | 2024-09-01 | 10570
Shoprite Naledi | 2024-10-01 | 18040
Shoprite Naledi | 2024-11-01 | 18800
Shoprite Naledi | 2024-12-01 | 20883
Shoprite Naledi | 2025-01-01 | 20300
Shoprite Naledi | 2025-02-01 | 13100
Shoprite Naledi | 2025-03-01 | 12342
Shoprite Naledi | 2025-04-01 | 10819
Shoprite Naledi | 2025-05-01 | 15169
Shoprite Naledi | 2025-06-01 | 13081.41
Shoprite Naledi | 2025-07-01 | 14154
Shoprite Naledi | 2025-08-01 | 16190
Shoprite Naledi | 2025-09-01 | 16520
Shoprite Naledi | 2025-10-01 | 20440
Shoprite Naledi | 2025-11-01 | 17928
Shoprite Naledi | 2025-12-01 | 20527.8823
Shoprite Naledi | 2026-01-01 | 22071
Shoprite Naledi | 2026-02-01 | 18965
Shoprite Naledi | 2026-03-01 | 15865
Shoprite Naledi | 2026-04-01 | 13806.89
Shoprite Naledi | 2026-05-01 | 13506.85
Shoprite Naledi | 2026-06-01 | 10711.09
Shoprite Mini Ganyesa | 2026-07-01 | 18234
Shoprite Naledi | 2026-08-01 | 14997.19
Shoprite Naledi | 2026-09-01 | 15845.86
Shoprite Naledi | 2026-10-01
Shoprite Naledi | 2026-11-01
Shoprite Naledi | 2026-12-01
Shoprite Newlands | 2024-01-01
Shoprite Newlands | 2024-02-01
Shoprite Newlands | 2024-03-01
Shoprite Newlands | 2024-04-01
Shoprite Newlands | 2024-05-01
Shoprite Newlands | 2024-06-01
Shoprite Newlands | 2024-07-01
Shoprite Newlands | 2024-08-01
Shoprite Newlands | 2024-09-01
Shoprite Newlands | 2024-10-01
Shoprite Newlands | 2024-11-01
Shoprite Newlands | 2024-12-01
Shoprite Newlands | 2025-01-01
Shoprite Newlands | 2025-02-01
Shoprite Newlands | 2025-03-01
Shoprite Newlands | 2025-04-01
Shoprite Newlands | 2025-05-01
Shoprite Newlands | 2025-06-01
Shoprite Newlands | 2025-07-01
Shoprite Newlands | 2025-08-01
Shoprite Newlands | 2025-09-01
Shoprite Newlands | 2025-10-01
Shoprite Newlands | 2025-11-01
Shoprite Newlands | 2025-12-01 | 18509
Shoprite Newlands | 2026-01-01 | 32917
Shoprite Newlands | 2026-02-01 | 31107
Shoprite Newlands | 2026-03-01 | 26454
Shoprite Newlands | 2026-04-01 | 20930.87
Shoprite Newlands | 2026-05-01 | 20539.96
Shoprite Newlands | 2026-06-01 | 17006.73
Shoprite Naledi | 2026-07-01 | 9106.96
Shoprite Newlands | 2026-08-01 | 22467.354
Shoprite Newlands | 2026-09-01 | 21057.6623
Shoprite Newlands | 2026-10-01
Shoprite Newlands | 2026-11-01
Shoprite Newlands | 2026-12-01
Shoprite Thokoza | 2024-01-01
Shoprite Thokoza | 2024-02-01
Shoprite Thokoza | 2024-03-01
Shoprite Thokoza | 2024-04-01
Shoprite Thokoza | 2024-05-01
Shoprite Thokoza | 2024-06-01
Shoprite Thokoza | 2024-07-01
Shoprite Thokoza | 2024-08-01
Shoprite Thokoza | 2024-09-01
Shoprite Thokoza | 2024-10-01
Shoprite Thokoza | 2024-11-01
Shoprite Thokoza | 2024-12-01
Shoprite Thokoza | 2025-01-01
Shoprite Thokoza | 2025-02-01
Shoprite Thokoza | 2025-03-01
Shoprite Thokoza | 2025-04-01 | 4166
Shoprite Thokoza | 2025-05-01 | 5400
Shoprite Thokoza | 2025-06-01 | 8687.3
Shoprite Thokoza | 2025-07-01 | 7090
Shoprite Thokoza | 2025-08-01 | 10240
Shoprite Thokoza | 2025-09-01 | 11379
Shoprite Thokoza | 2025-10-01 | 16828.7
Shoprite Thokoza | 2025-11-01 | 15461
Shoprite Thokoza | 2025-12-01 | 17561
Shoprite Thokoza | 2026-01-01 | 20127
Shoprite Thokoza | 2026-02-01 | 16780
Shoprite Thokoza | 2026-03-01 | 14651
Shoprite Thokoza | 2026-04-01 | 12498.2
Shoprite Thokoza | 2026-05-01 | 11697.82
Shoprite Thokoza | 2026-06-01 | 9082.64
Shoprite Newlands | 2026-07-01 | 17999.1711
Shoprite Thokoza | 2026-08-01 | 11233.53
Shoprite Thokoza | 2026-09-01 | 11994.93
Shoprite Thokoza | 2026-10-01
Shoprite Thokoza | 2026-11-01
Shoprite Thokoza | 2026-12-01
Spring Glade | 2024-01-01 | 9171
Spring Glade | 2024-02-01 | 8406
Spring Glade | 2024-03-01 | 9529
Spring Glade | 2024-04-01 | 8796
Spring Glade | 2024-05-01 | 10039
Spring Glade | 2024-06-01 | 10175
Spring Glade | 2024-07-01 | 10629
Spring Glade | 2024-08-01 | 10264
Spring Glade | 2024-09-01 | 9192
Spring Glade | 2024-10-01 | 10175
Spring Glade | 2024-11-01 | 9431
Spring Glade | 2024-12-01 | 9104
Spring Glade | 2025-01-01 | 5093
Spring Glade | 2025-02-01 | 7532
Spring Glade | 2025-03-01 | 7375
Spring Glade | 2025-04-01 | 7602
Spring Glade | 2025-05-01 | 10378
Spring Glade | 2025-06-01 | 10510.45
Spring Glade | 2025-07-01 | 9750
Spring Glade | 2025-08-01 | 10081
Spring Glade | 2025-09-01 | 11225
Spring Glade | 2025-10-01 | 9885
Spring Glade | 2025-11-01 | 8679
Spring Glade | 2025-12-01 | 9967
Spring Glade | 2026-01-01 | 9751
Spring Glade | 2026-02-01 | 8451
Spring Glade | 2026-03-01 | 8559
Spring Glade | 2026-04-01 | 7937.13
Spring Glade | 2026-05-01 | 10005.8
Spring Glade | 2026-06-01 | 9053
Shoprite Thokoza | 2026-07-01 | 7916.06
Spring Glade | 2026-08-01 | 9565
Spring Glade | 2026-09-01 | 7250.71
Spring Glade | 2026-10-01
Spring Glade | 2026-11-01
Spring Glade | 2026-12-01
TPF Foods | 2024-01-01 | 3404
TPF Foods | 2024-02-01 | 3408
TPF Foods | 2024-03-01 | 3131
TPF Foods | 2024-04-01 | 2829
TPF Foods | 2024-05-01 | 3129
TPF Foods | 2024-06-01 | 2591
TPF Foods | 2024-07-01 | 3122
TPF Foods | 2024-08-01 | 2990
TPF Foods | 2024-09-01 | 2990
TPF Foods | 2024-10-01 | 4061
TPF Foods | 2024-11-01 | 3991
TPF Foods | 2024-12-01 | 3569
TPF Foods | 2025-01-01 | 3838
TPF Foods | 2025-02-01 | 2653
TPF Foods | 2025-03-01 | 2925
TPF Foods | 2025-04-01 | 2246
TPF Foods | 2025-05-01 | 3149
TPF Foods | 2025-06-01 | 2654.45
TPF Foods | 2025-07-01 | 2863
TPF Foods | 2025-08-01 | 3192
TPF Foods | 2025-09-01 | 3092
TPF Foods | 2025-10-01 | 3600
TPF Foods | 2025-11-01 | 2755
TPF Foods | 2025-12-01 | 3248
TPF Foods | 2026-01-01 | 3546
TPF Foods | 2026-02-01 | 3398
TPF Foods | 2026-03-01 | 2638
TPF Foods | 2026-04-01 | 2034.35
TPF Foods | 2026-05-01 | 2231.41
TPF Foods | 2026-06-01 | 1788
Spring Glade | 2026-07-01 | 9713.47
TPF Foods | 2026-08-01 | 3050
TPF Foods | 2026-09-01 | 2619.92
TPF Foods | 2026-10-01
TPF Foods | 2026-11-01
TPF Foods | 2026-12-01
Thakadu Industrial | 2024-01-01
Thakadu Industrial | 2024-02-01
Thakadu Industrial | 2024-03-01
Thakadu Industrial | 2024-04-01
Thakadu Industrial | 2024-05-01
Thakadu Industrial | 2024-06-01
Thakadu Industrial | 2024-07-01
Thakadu Industrial | 2024-08-01
Thakadu Industrial | 2024-09-01
Thakadu Industrial | 2024-10-01
Thakadu Industrial | 2024-11-01
Thakadu Industrial | 2024-12-01
Thakadu Industrial | 2025-01-01
Thakadu Industrial | 2025-02-01
Thakadu Industrial | 2025-03-01
Thakadu Industrial | 2025-04-01
Thakadu Industrial | 2025-05-01
Thakadu Industrial | 2025-06-01
Thakadu Industrial | 2025-07-01
Thakadu Industrial | 2025-08-01
Thakadu Industrial | 2025-09-01
Thakadu Industrial | 2025-10-01
Thakadu Industrial | 2025-11-01
Thakadu Industrial | 2025-12-01
Thakadu Industrial | 2026-01-01
Thakadu Industrial | 2026-02-01
Thakadu Industrial | 2026-03-01
Thakadu Industrial | 2026-04-01
Thakadu Industrial | 2026-05-01
Thakadu Industrial | 2026-06-01
SR Morula TF 1 | 2026-07-01 | 2899
Thakadu Industrial | 2026-08-01
Thakadu Industrial | 2026-09-01
Thakadu Industrial | 2026-10-01
Thakadu Industrial | 2026-11-01
Thakadu Industrial | 2026-12-01
The Alec | 2024-01-01 | 6142
The Alec | 2024-02-01 | 5738
The Alec | 2024-03-01 | 5912
The Alec | 2024-04-01 | 4354
The Alec | 2024-05-01 | 3536
The Alec | 2024-06-01 | 2689
The Alec | 2024-07-01 | 3106
The Alec | 2024-08-01 | 4461
The Alec | 2024-09-01 | 5033
The Alec | 2024-10-01 | 6965
The Alec | 2024-11-01 | 6934
The Alec | 2024-12-01 | 7000
The Alec | 2025-01-01 | 5900
The Alec | 2025-02-01 | 4280
The Alec | 2025-03-01 | 4292
The Alec | 2025-04-01 | 3097
The Alec | 2025-05-01 | 3200
The Alec | 2025-06-01 | 2560.4
The Alec | 2025-07-01 | 2823
The Alec | 2025-08-01 | 4200
The Alec | 2025-09-01 | 4566
The Alec | 2025-10-01 | 6195.1
The Alec | 2025-11-01 | 5304
The Alec | 2025-12-01 | 6296
The Alec | 2026-01-01 | 6828
The Alec | 2026-02-01 | 6062
The Alec | 2026-03-01 | 4541
The Alec | 2026-04-01 | 3743.09
The Alec | 2026-05-01 | 3041.11
SR Morula TF 1 | 2026-06-01 | 4726
SR Morula TF 1 - Shoprite | 2026-07-01 | 10206
The Alec | 2026-08-01 | 3881
The Alec | 2026-09-01 | 4853.26
The Alec | 2026-10-01
The Alec | 2026-11-01
The Alec | 2026-12-01
Three Peaks | 2024-01-01 | 3510
Three Peaks | 2024-02-01 | 3517
Three Peaks | 2024-03-01 | 3409
Three Peaks | 2024-04-01 | 2977
Three Peaks | 2024-05-01 | 2754
Three Peaks | 2024-06-01 | 2322
Three Peaks | 2024-07-01 | 3200
Three Peaks | 2024-08-01 | 1967.434
Three Peaks | 2024-09-01 | 2608
Three Peaks | 2024-10-01 | 3179
Three Peaks | 2024-11-01 | 2499
Three Peaks | 2024-12-01 | 2419
Three Peaks | 2025-01-01 | 2940
Three Peaks | 2025-02-01 | 2482
Three Peaks | 2025-03-01 | 2660
Three Peaks | 2025-04-01 | 3014
Three Peaks | 2025-05-01 | 3259
Three Peaks | 2025-06-01 | 2701.4
Three Peaks | 2025-07-01 | 2990
Three Peaks | 2025-08-01 | 3504
Three Peaks | 2025-09-01 | 3456
Three Peaks | 2025-10-01 | 4131
Three Peaks | 2025-11-01 | 3798
Three Peaks | 2025-12-01 | 4633
Three Peaks | 2026-01-01 | 5177
Three Peaks | 2026-02-01 | 3087
Three Peaks | 2026-03-01 | 4035
Three Peaks | 2026-04-01 | 3282.98
Three Peaks | 2026-05-01 | 3208.4
Three Peaks | 2026-06-01 | 3015
SR Morula TF 2 | 2026-07-01 | 4951
Three Peaks | 2026-08-01 | 3769
Three Peaks | 2026-09-01 | 3170.27
Three Peaks | 2026-10-01
Three Peaks | 2026-11-01
Three Peaks | 2026-12-01
Trouw Nutrition | 2024-01-01
Trouw Nutrition | 2024-02-01 | 11561
Trouw Nutrition | 2024-03-01 | 11738
Trouw Nutrition | 2024-04-01 | 307
Trouw Nutrition | 2024-05-01 | 1
Trouw Nutrition | 2024-06-01 | 1
Trouw Nutrition | 2024-07-01 | 6245
Trouw Nutrition | 2024-08-01 | 10791
Trouw Nutrition | 2024-09-01 | 10127
Trouw Nutrition | 2024-10-01 | 12940
Trouw Nutrition | 2024-11-01 | 12711
Trouw Nutrition | 2024-12-01 | 12090
Trouw Nutrition | 2025-01-01 | 10838
Trouw Nutrition | 2025-02-01 | 8901
Trouw Nutrition | 2025-03-01 | 9398
Trouw Nutrition | 2025-04-01 | 8195
Trouw Nutrition | 2025-05-01 | 6021
Trouw Nutrition | 2025-06-01 | 4341.56
Trouw Nutrition | 2025-07-01 | 6989
Trouw Nutrition | 2025-08-01 | 11205
Trouw Nutrition | 2025-09-01 | 10024
Trouw Nutrition | 2025-10-01 | 13192
Trouw Nutrition | 2025-11-01 | 10364
Trouw Nutrition | 2025-12-01 | 10702
Trouw Nutrition | 2026-01-01 | 12710
Trouw Nutrition | 2026-02-01 | 12261
Trouw Nutrition | 2026-03-01 | 11049
Trouw Nutrition | 2026-04-01 | 9364.19
Trouw Nutrition | 2026-05-01 | 10132.34
Trouw Nutrition | 2026-06-01 | 8126
Thakadu Industrial | 2026-07-01 | 0
Trouw Nutrition | 2026-08-01 | 11112
Trouw Nutrition | 2026-09-01 | 10023.98
Trouw Nutrition | 2026-10-01
Trouw Nutrition | 2026-11-01
Trouw Nutrition | 2026-12-01
U Save Botrivier | 2024-01-01
U Save Botrivier | 2024-02-01
U Save Botrivier | 2024-03-01
U Save Botrivier | 2024-04-01
U Save Botrivier | 2024-05-01
U Save Botrivier | 2024-06-01
U Save Botrivier | 2024-07-01
U Save Botrivier | 2024-08-01
U Save Botrivier | 2024-09-01
U Save Botrivier | 2024-10-01
U Save Botrivier | 2024-11-01
U Save Botrivier | 2024-12-01
U Save Botrivier | 2025-01-01
U Save Botrivier | 2025-02-01
U Save Botrivier | 2025-03-01
U Save Botrivier | 2025-04-01
U Save Botrivier | 2025-05-01
U Save Botrivier | 2025-06-01
U Save Botrivier | 2025-07-01
U Save Botrivier | 2025-08-01 | 3866
U Save Botrivier | 2025-09-01 | 4249
U Save Botrivier | 2025-10-01 | 5286
U Save Botrivier | 2025-11-01 | 5001
U Save Botrivier | 2025-12-01 | 6707
U Save Botrivier | 2026-01-01 | 7171.5
U Save Botrivier | 2026-02-01 | 4844
U Save Botrivier | 2026-03-01 | 5410
U Save Botrivier | 2026-04-01 | 2815.5
U Save Botrivier | 2026-05-01 | 2205.5
U Save Botrivier | 2026-06-01 | 1921.8
The Alec | 2026-07-01 | 2690
U Save Botrivier | 2026-08-01 | 4145
U Save Botrivier | 2026-09-01 | 3820.9749
U Save Botrivier | 2026-10-01
U Save Botrivier | 2026-11-01
U Save Botrivier | 2026-12-01
Watt Place Rotoflo | 2024-01-01 | 17892
Watt Place Rotoflo | 2024-02-01 | 15929
Watt Place Rotoflo | 2024-03-01 | 18524
Watt Place Rotoflo | 2024-04-01 | 13076
Watt Place Rotoflo | 2024-05-01 | 17640
Watt Place Rotoflo | 2024-06-01 | 14642
Watt Place Rotoflo | 2024-07-01 | 15002
Watt Place Rotoflo | 2024-08-01 | 20792
Watt Place Rotoflo | 2024-09-01 | 20898
Watt Place Rotoflo | 2024-10-01 | 30325
Watt Place Rotoflo | 2024-11-01 | 27930
Watt Place Rotoflo | 2024-12-01 | 17653
Watt Place Rotoflo | 2025-01-01 | 23957
Watt Place Rotoflo | 2025-02-01 | 19898
Watt Place Rotoflo | 2025-03-01 | 18434
Watt Place Rotoflo | 2025-04-01 | 16717
Watt Place Rotoflo | 2025-05-01 | 19518
Watt Place Rotoflo | 2025-06-01 | 16703.9
Watt Place Rotoflo | 2025-07-01 | 17442.42
Watt Place Rotoflo | 2025-08-01 | 21419
Watt Place Rotoflo | 2025-09-01 | 19487
Watt Place Rotoflo | 2025-10-01 | 25859.04
Watt Place Rotoflo | 2025-11-01 | 23228
Watt Place Rotoflo | 2025-12-01 | 13257
Watt Place Rotoflo | 2026-01-01 | 24628
Watt Place Rotoflo | 2026-02-01 | 24848.5
Watt Place Rotoflo | 2026-03-01 | 20359
Watt Place Rotoflo | 2026-04-01 | 17480.97
Watt Place Rotoflo | 2026-05-01 | 17505.34
SR Morula TF 2 | 2026-06-01 | 4827
Three Peaks | 2026-07-01 | 3037
Watt Place Rotoflo | 2026-08-01 | 18697
Watt Place Rotoflo | 2026-09-01 | 19614.48
Watt Place Rotoflo | 2026-10-01
Watt Place Rotoflo | 2026-11-01
Watt Place Rotoflo | 2026-12-01
Zwartop Golf Course | 2024-01-01
Zwartop Golf Course | 2024-02-01
Zwartop Golf Course | 2024-03-01
Zwartop Golf Course | 2024-04-01
Zwartop Golf Course | 2024-05-01
Zwartop Golf Course | 2024-06-01
Zwartop Golf Course | 2024-07-01
Zwartop Golf Course | 2024-08-01
Zwartop Golf Course | 2024-09-01
Zwartop Golf Course | 2024-10-01
Zwartop Golf Course | 2024-11-01
Zwartop Golf Course | 2024-12-01
Zwartop Golf Course | 2025-01-01
Zwartop Golf Course | 2025-02-01
Zwartop Golf Course | 2025-03-01
Zwartop Golf Course | 2025-04-01
Zwartop Golf Course | 2025-05-01
Zwartop Golf Course | 2025-06-01
Zwartop Golf Course | 2025-07-01
Zwartop Golf Course | 2025-08-01
Zwartop Golf Course | 2025-09-01
Zwartop Golf Course | 2025-10-01
Zwartop Golf Course | 2025-11-01
Zwartop Golf Course | 2025-12-01
Zwartop Golf Course | 2026-01-01
Zwartop Golf Course | 2026-02-01
Zwartop Golf Course | 2026-03-01
Zwartop Golf Course | 2026-04-01
Zwartop Golf Course | 2026-05-01
Zwartop Golf Course | 2026-06-01 | 0
Tlou Integrated Tech | 2026-07-01 | 10958.8256
Zwartop Golf Course | 2026-08-01
Zwartop Golf Course | 2026-09-01
Zwartop Golf Course | 2026-10-01
Zwartop Golf Course | 2026-11-01
Zwartop Golf Course | 2026-12-01
Roan Foods | 2026-04-01 | 10820
Roan Foods | 2026-05-01 | 11820
Checkers Lichtenburg | 2026-05-01 | 17630
Alpine Heath Resort | 2026-05-01 | 27917.2
Engen Kaalfontein | 2024-01-01
Engen Kaalfontein | 2024-02-01
Engen Kaalfontein | 2024-03-01
Engen Kaalfontein | 2024-04-01
Engen Kaalfontein | 2024-05-01
Engen Kaalfontein | 2024-06-01
Engen Kaalfontein | 2024-07-01
Engen Kaalfontein | 2024-08-01
Engen Kaalfontein | 2024-09-01
Engen Kaalfontein | 2024-10-01
Engen Kaalfontein | 2024-11-01
Engen Kaalfontein | 2024-12-01
Engen Kaalfontein | 2025-01-01
Engen Kaalfontein | 2025-02-01
Engen Kaalfontein | 2025-03-01
Engen Kaalfontein | 2025-04-01
Engen Kaalfontein | 2025-05-01
Engen Kaalfontein | 2025-06-01
Engen Kaalfontein | 2025-07-01
Engen Kaalfontein | 2025-08-01
Engen Kaalfontein | 2025-09-01
Engen Kaalfontein | 2025-10-01
Engen Kaalfontein | 2025-11-01
Engen Kaalfontein | 2025-12-01
Engen Kaalfontein | 2026-01-01
Engen Kaalfontein | 2026-02-01
Engen Kaalfontein | 2026-03-01
Engen Kaalfontein | 2026-04-01
Engen Kaalfontein | 2026-05-01
The Alec | 2026-06-01 | 2444
TPF Foods | 2026-07-01 | 2200.69
Engen Kaalfontein | 2026-08-01 | 14833.728
Engen Kaalfontein | 2026-09-01 | 12896.9249
Engen Kaalfontein | 2026-10-01
Engen Kaalfontein | 2026-11-01
Engen Kaalfontein | 2026-12-01
Alpine Heath Resort | 2024-01-01
Alpine Heath Resort | 2024-02-01
Alpine Heath Resort | 2024-03-01
Alpine Heath Resort | 2024-04-01
Alpine Heath Resort | 2024-05-01
Alpine Heath Resort | 2024-06-01
Alpine Heath Resort | 2024-07-01
Alpine Heath Resort | 2024-08-01
Alpine Heath Resort | 2024-09-01
Alpine Heath Resort | 2024-10-01
Alpine Heath Resort | 2024-11-01
Alpine Heath Resort | 2024-12-01
Alpine Heath Resort | 2025-01-01
Alpine Heath Resort | 2025-02-01
Alpine Heath Resort | 2025-03-01
Alpine Heath Resort | 2025-04-01
Alpine Heath Resort | 2025-05-01
Alpine Heath Resort | 2025-06-01
Alpine Heath Resort | 2025-07-01
Alpine Heath Resort | 2025-08-01
Alpine Heath Resort | 2025-09-01
Alpine Heath Resort | 2025-10-01
Alpine Heath Resort | 2025-11-01
Alpine Heath Resort | 2025-12-01
Alpine Heath Resort | 2026-01-01
Alpine Heath Resort | 2026-02-01
Alpine Heath Resort | 2026-03-01
Alpine Heath Resort | 2026-04-01
Watt Place Rotoflo | 2026-06-01 | 11655
Trouw Nutrition | 2026-07-01 | 9893.59
Alpine Heath Resort | 2026-08-01 | 29161
Alpine Heath Resort | 2026-09-01 | 21788
Alpine Heath Resort | 2026-10-01
Alpine Heath Resort | 2026-11-01
Alpine Heath Resort | 2026-12-01
U Save Botrivier | 2026-07-01 | 2292.691
Usave Naboomspruit | 2026-07-01 | 4094.8841
Watt Place Rotoflo | 2026-07-01 | 14705
Zwartop Golf Course | 2026-07-01 | 0
Checkers Lichtenburg | 2026-08-01 | 19960.113
Roan Foods | 2026-08-01 | 9230
Tlou Integrated Tech | 2026-08-01 | 13767.458
Usave Naboomspruit | 2026-08-01 | 4246.929
Shoprite SRH Bizana | 2026-08-01 | 15700
Shoprite Mayfair | 2026-08-01 | 8306.7484
Roan Foods | 2026-06-01 | 10720
Checkers Lichtenburg | 2026-06-01 | 14172
Checkers Lichtenburg | 2026-09-01 | 18541.7396
Roan Foods | 2026-09-01 | 11370
Tlou Integrated Tech | 2026-09-01 | 12209.5066
Usave Naboomspruit | 2026-09-01 | 4005.8959
Shoprite SRH Bizana | 2026-09-01 | 13165.4802
Shoprite Mayfair | 2026-09-01 | 14788.0946
Note on A1: Mathakgale Mohale: Sep-26 values (C34:C2701 Sep rows, and new rows 2717:2722): Source: 261001 kWh Registration_September.xlsx, Meter Overview sheet, Total kWh column, uploaded 2026-10-05.
Note on C321: Mathakgale Mohale: Aug-2026 measured. Offline 01/08 - 04/08. Source: 260901 kWh Registration_August.xlsx, Meter Overview
Note on C1437: Mathakgale Mohale: Inverter readings. Source: 260901 kWh Registration_August.xlsx, Meter Overview
Note on C1761: Mathakgale Mohale: System offline until 17/08 (municipal fault). Source: 260901 kWh Registration_August.xlsx, Meter Overview
Note on C2013: Mathakgale Mohale: System off due to grid unavailability. Source: 260901 kWh Registration_August.xlsx, Meter Overview
Note on C2553: Mathakgale Mohale: Inverter readings. Source: 260901 kWh Registration_August.xlsx, Meter Overview
Note on C2714: Mathakgale Mohale: Commissioned 17/08. Source: 260901 kWh Registration_August.xlsx, Meter Overview

## Expected Production
Site Name | Expected Utilisation% | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec
21 Melrose | 0.9 | 2370.6 | 2680.2 | 2183.4 | 1873.8 | 1822.5 | 1629 | 1814.4 | 2116.8 | 2275.2 | 2407.5 | 2356.2 | 2482.2 | 2027
African Global Plastics | 0.85 | 22515.905 | 19786.13 | 20148.4 | 16764.89 | 15972.095 | 14367.21 | 15907.665 | 18527.365 | 20404.335 | 22320.66 | 22520.665 | 23777.985
Alpine Heath Residential | 0.9 | 4801.5 | 4303.8 | 4545.9 | 4619.7 | 4990.5 | 4761.9 | 4680.9 | 5249.7 | 4694.4 | 4732.2 | 4822.2 | 4805.1
Bendstore Plaza Shops | 0.85 | 16262.2 | 13986.75 | 15463.2 | 14886.05 | 14411.75 | 13050.05 | 13735.15 | 15350.15 | 15431.75 | 14821.45 | 14695.65 | 16154.25
Bendstore Spar | 0.9 | 51314.7347 | 44103.2907 | 48739.27 | 46849.8989 | 45273.2333 | 40943.9718 | 43112.803 | 48266.5027 | 48602.8914 | 46748.9108 | 46388.4816 | 50640.3114
Beyerskloof | 0.9 | 13787.1 | 11359.8 | 10881 | 7828.2 | 5953.5 | 5166 | 5564.7 | 6960.6 | 8946 | 11314.8 | 12713.4 | 13878.9
BP Parys | 0.9 | 8151.3 | 7235.1 | 7075.8 | 5754.6 | 5424.3 | 4787.1 | 5360.4 | 6363 | 7218.9 | 7839 | 8191.8 | 8227.8
Buffalo Rock | 0.9 | 2202.3 | 1983.6 | 2127.6 | 1767.6 | 1631.7 | 1480.5 | 1612.8 | 1764 | 1868.4 | 1900.8 | 1835.1 | 1986.3
Checkers De Aar | 0.9 | 26689.5 | 20674.8 | 20095.2 | 16286.4 | 13518.9 | 11864.7 | 13589.1 | 17109 | 19506.6 | 24081.3 | 25889.4 | 27992.7
Checkers Silverlakes Gen | 0.9 | 21105 | 18220.5 | 18368.1 | 15103.8 | 14130 | 12619.8 | 14002.2 | 16641.9 | 18626.4 | 20503.8 | 20601 | 22024.8
Checkers Silverlakes No Gen | 0.9 | 21105 | 18220.5 | 18368.1 | 15103.8 | 14130 | 12619.8 | 14002.2 | 16641.9 | 18626.4 | 20503.8 | 20601 | 22024.8
Checkrite Inanda | 0.9 | 8664.3 | 8100 | 7805.7 | 6534 | 5592.6 | 5059.8 | 5372.1 | 6485.4 | 6914.7 | 8033.4 | 8012.7 | 8547.3
Club Houghton | 0.9 | 5767.2 | 4828.5 | 4913.1 | 4149.9 | 3937.5 | 3463.2 | 3874.5 | 4560.3 | 5033.7 | 5613.3 | 5712.3 | 6027.3
Coldstar International | 0.85 | 4897.02 | 4496.245 | 4548.605 | 3805.195 | 3522.57 | 3187.925 | 3416.15 | 3857.045 | 3805.705 | 4238.695 | 4335.34 | 5058.01
Cultura Fresh | 0.9 | 11798.1 | 10269.9 | 10571.4 | 8335.8 | 6723.9 | 5859.9 | 6453 | 7491.6 | 8864.1 | 10361.7 | 10972.8 | 11630.7
Demco | 0.8 | 33516 | 28776.8 | 29186.4 | 24678.4 | 23380.8 | 20986.4 | 23255.2 | 27306.4 | 30312 | 33024 | 33214.4 | 35066.4
Engen Lotus Gardens | 0.9 | 2461.5 | 2300.4 | 2281.5 | 2197.8 | 2226.6 | 2480.4 | 2349.9 | 2520 | 2436.3 | 2425.5 | 2356.2 | 2437.2
Giba Gorge Main | 0.8 | 13584 | 12445.28 | 12742.08 | 10941.84 | 9881.28 | 9234.88 | 9756.08 | 10822.4 | 10915.68 | 12133.12 | 12325.9898 | 13473.8978
Giba Gorge Storage | 0.75 | 11384.625 | 10143.6 | 10396.425 | 8842.275 | 7963.725 | 7364.325 | 7865.175 | 8758.725 | 8956.35 | 9957.75 | 10009.6634 | 11121.5007
Golden Spot Resort | 0.9 | 4042.8 | 3650.4 | 3957.3 | 3279.6 | 3050.1 | 2790 | 3044.7 | 3298.5 | 3492.9 | 3509.1 | 3348 | 3591.9
Golden Spot Shops | 0.9 | 3618 | 3254.4 | 3608.1 | 2962.8 | 2723.4 | 2461.5 | 2701.8 | 2973.6 | 3147.3 | 3179.7 | 3013.2 | 3204
HB Dunn | 0.9 | 4235.4 | 3699 | 3788.1 | 3184.2 | 3052.8 | 2752.2 | 3029.4 | 3546.9 | 3911.4 | 4103.1 | 4120.2 | 4377.6
Helderberg Collage | 0.9 | 39600.81 | 33064.92 | 32219.55 | 23614.38 | 17952.57 | 14925.6 | 16774.83 | 20886.75 | 26689.95 | 33024.69 | 37111.77 | 40125.69
Hilston Rotoflo | 0.85 | 27758.45 | 24250.5 | 22859.9 | 20353.25 | 18229.1 | 16127.9 | 17954.55 | 20938.05 | 23291.7 | 25925.85 | 27223.8 | 26753.75
Huis Herfsblaar | 0.9 | 30214.8 | 26381.7 | 27566.1 | 23747.4 | 22569.3 | 20228.4 | 22354.2 | 26968.5 | 28840.5 | 30258 | 29380.5 | 31219.2
IPID - Floor 4 | 0.9 | 7573.5 | 6513.75 | 6841.35 | 6183 | 5924.7 | 5295.6 | 5785.2 | 6585.3 | 7018.65 | 7479.45 | 7552.8 | 7415.1
IPID - Floor 6 | 0.9 | 7573.5 | 6513.75 | 6841.35 | 6183 | 5924.7 | 5295.6 | 5785.2 | 6585.3 | 7018.65 | 7479.45 | 7552.8 | 7415.1
Kool Village | 0.9 | 12213 | 10570.5 | 10619.1 | 9139.5 | 8593.2 | 7680.6 | 8550.9 | 9997.2 | 10701.9 | 11834.1 | 12129.3 | 12998.7
Makalali | 0.9 | 16602.9395 | 14966.051 | 16335.4855 | 15100.3508 | 15271.0454 | 14168.0073 | 15171.29 | 16365.4474 | 16283.9335 | 15891.0803 | 15343.2183 | 16261.6383
Mambha Cash & Carry | 0.9 | 22241.7 | 19450.8 | 19575 | 15792.3 | 13477.5 | 12124.8 | 13099.5 | 15450.3 | 16583.4 | 19432.8 | 20010.6 | 22485.6
Mathe Group Company | 0.85 | 61302.85 | 55639.3 | 58024.4 | 48946.4 | 44310.5 | 40933.45 | 43977.3 | 48620.85 | 50331.05 | 55230.45 | 56583.65 | 61075.9
Mdluli | 0.8 | 14107.2 | 13178.4 | 15390.4 | 13652 | 13508.8 | 12879.2 | 13680.8 | 13878.4 | 13503.2 | 12755.2 | 11784.8 | 12301.6
Medipost | 0.9 | 53361.9 | 43750.8 | 40931.1 | 29080.8 | 21434.4 | 17483.4 | 19783.8 | 25524 | 33381.9 | 43038 | 49565.7 | 54135.9
Meredale Heights | 0.9 | 5361.3 | 4869 | 5370.3 | 5150.7 | 5477.4 | 5296.5 | 5700.6 | 5969.7 | 5915.7 | 5814.9 | 5410.8 | 5530.5
Monument Park Checkers | 0.9 | 40416.3 | 33988.5 | 35132.4 | 29903.4 | 28383.3 | 25641.9 | 28361.7 | 33006.6 | 36521.1 | 39682.8 | 39748.5 | 42519.6
Nkambeni Industrial | 1 | 23544 | 21677 | 24212 | 20861 | 20012 | 18485 | 20016 | 21052 | 21403 | 20962 | 19856 | 21184
Olievenhoutbosch 1 | 0.9 | 46872 | 40989.6 | 39989.7 | 34783.2 | 32139 | 28357.2 | 31229.1 | 36815.4 | 40778.1 | 46212.3 | 46653.3 | 47656.8
Olievenhoutbosch 2 | 0.9 | 12369.6 | 10801.8 | 10537.2 | 9173.7 | 8503.2 | 7545.6 | 8307 | 9720.9 | 10755.9 | 12190.5 | 12263.4 | 12539.7
Opal Students | 0.9 | 5685.3 | 4780.8 | 4935.6 | 4359.6 | 4194 | 3818.7 | 4217.4 | 4844.7 | 5300.1 | 5667.3 | 5624.1 | 5995.8
Orthochem Bethlehem | 0.9 | 41208.48 | 35976.15 | 36559.98 | 33604.11 | 32958.63 | 30018.2212 | 32459.8096 | 36506.1257 | 37370.8698 | 40182.9863 | 40330.5361 | 42601.4278
Plastiplate | 0.75 | 8591.025 | 7466.475 | 7931.85 | 6987.15 | 6858.525 | 6375.45 | 6946.725 | 7852.65 | 8347.05 | 8786.625 | 8551.8 | 9109.05
PNB Unlimited | 0.8 | 11540.96 | 9862.32 | 10345.44 | 8819.52 | 8538.08 | 7700 | 8487.2 | 9810.48 | 10706.48 | 11410.4 | 11340.4 | 12102.56
Q-lity Meat | 0.9 | 4894.29 | 4527.45 | 4754.25 | 4171.59 | 4117.5 | 3729.06 | 4105.53 | 4624.83 | 4797 | 5068.98 | 4862.88 | 5082.39
Quintondale | 0.9 | 5902.47 | 5299.2 | 5701.86 | 5085.9 | 5204.61 | 4824.36 | 5303.16 | 5833.08 | 6021.81 | 6128.91 | 5928.57 | 6186.69
Riverside Lodge | 0.85 | 17099.45 | 15031.4 | 16289.4 | 14250.25 | 14783.2 | 13871.15 | 15110.45 | 16763.7 | 16935.4 | 17583.95 | 16597.1 | 17731
Sakhumnotho | 0.84532 | 5191.479 | 4656.5573 | 5018.2719 | 4498.5661 | 4604.0626 | 4265.4254 | 4694.8505 | 5144.2253 | 5295.0313 | 5391.4829 | 5210.6678 | 5439.6664
SaveMore Alldays - Store | 0.9 | 23005.8 | 19888.2 | 21952.8 | 21444.3 | 20688.3 | 18646.2 | 19629.9 | 22998.6 | 22670.1 | 22045.5 | 22062.6 | 23333.4
Savemore Liquor Alldays | 0.85 | 3308.455 | 2856.595 | 3155.625 | 3081.845 | 2972.875 | 2678.69 | 2819.025 | 3304.375 | 3255.755 | 3170.245 | 3173.135 | 3354.185
Saverite Durban | 0.95 | 12489.555 | 10877.69 | 10897.355 | 8757.955 | 7449.425 | 6752.695 | 7274.245 | 8568.715 | 9196 | 10753.525 | 11159.27 | 12687.82
Saverite PMB | 0.95 | 13218.015 | 10966.135 | 11441.135 | 10004.07 | 8979.59 | 7800.26 | 8635.69 | 9829.935 | 10568.94 | 11606.34 | 12483.285 | 13393.575
Secunda Plaza choppies | 0.9 | 23065.02 | 20354.85 | 21716.37 | 18847.89 | 18700.92 | 17164.44 | 18821.97 | 21497.67 | 22688.37 | 22841.55 | 22507.92 | 23494.59
Secunda Plaza Shops | 0.9 | 4359.6 | 3825.9 | 4077 | 3573.9 | 3623.4 | 3360.6 | 3665.7 | 4104 | 4274.1 | 4289.4 | 4249.8 | 4446
Shoprite Dube | 0.9 | 23724 | 20448 | 19986.3 | 17181.9 | 15369.3 | 13381.2 | 15023.7 | 18071.1 | 20545.2 | 23411.7 | 23583.6 | 24027.3
Shoprite Hillbrow | 0.95 | 20564.65 | 17491.4 | 18246.65 | 15297.85 | 14953 | 13275.3 | 14678.45 | 17062.95 | 18937.3 | 20481.05 | 20366.1 | 21890.85
Shoprite Ladybrand | 0.95 | 37513.6 | 31212.25 | 29700.135 | 24898.55 | 21981.1 | 18982.9 | 21551.7 | 26041.4 | 29888.9 | 34705.4 | 36881.85 | 40110.9
Shoprite Mini Ganyesa | 0.9 | 34074.9 | 28396.8 | 28665.9 | 24411.6 | 22266.9 | 19791.9 | 21774.6 | 25973.1 | 28984.5 | 33058.8 | 34366.5 | 36320.4
Shoprite Naledi | 0.9 | 20588.4 | 17538.3 | 17897.4 | 14674.5 | 13272.3 | 11571.3 | 12990.6 | 15871.5 | 18317.7 | 20121.3 | 20573.1 | 21930.3
Shoprite Newlands | 0.9 | 30721.5 | 24282.9 | 24146.1 | 18389.7 | 18961.2 | 15280.2 | 17361.9 | 19303.2 | 18141.3 | 22548.6 | 22923.9 | 28392.3
Shoprite Thokoza | 0.9 | 18584.1 | 16101.9 | 15901.2 | 13660.2 | 12620.7 | 11094.3 | 12367.8 | 14484.6 | 16189.2 | 18663.3 | 18589.5 | 19022.4
Spring Glade | 0.85 | 16638.665 | 14215.06 | 15137.31 | 13176.87 | 12813.75 | 11578.87 | 12892.545 | 14836.92 | 15996.15 | 16796.17 | 16463.225 | 17398.905
SR Morula TF 1 | 0.9 | 9307.8 | 8001.9 | 7803.9 | 6785.1 | 6244.2 | 5524.2 | 6086.7 | 7124.4 | 7864.2 | 9007.2 | 8999.1 | 9241.2
SR Morula TF 1 - Shoprite | 0.9 | 28699.56 | 24909.3 | 24570 | 21388.5 | 19723.5 | 17431.2 | 19181.7 | 22417.2 | 24780.6 | 28127.7 | 28061.1 | 28703.7
SR Morula TF 2 | 0.9 | 9601.92 | 8296.74 | 8140.5 | 7017.3 | 6430.32 | 5669.28 | 6247.44 | 7340.13 | 8154 | 9352.8 | 9353.7 | 9582.3
Thakadu Industrial |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
The Alec | 0.925 | 7605.35 | 6473.15 | 6529.575 | 5155.95 | 4885.85 | 4375.25 | 4861.8 | 5591.625 | 6522.175 | 7451.8 | 7534.125 | 8084.5
Three Peaks | 0.75 | 4274.1 | 3810.6 | 3907.275 | 3268.125 | 2929.95 | 2664.75 | 2851.125 | 3237 | 3327.75 | 3775.725 | 3829.575 | 4315.65
TPF Foods | 0.75 | 3784.425 | 3270.15 | 3533.325 | 3063.075 | 3093.825 | 2834.025 | 3103.35 | 3491.55 | 3723.45 | 3899.4 | 3732.75 | 4016.175
Trouw Nutrition | 0.85 | 13441.985 | 12055.125 | 12858.46 | 11531.27 | 11785.93 | 11018.635 | 12024.27 | 13262.635 | 13540.33 | 13925.295 | 13508.37 | 14234.525
U Save Botrivier | 0.9 | 7299.9 | 6223.5 | 6048.9 | 5130.9 | 4621.5 | 3931.2 | 4065.3 | 4723.2 | 5251.5 | 6489.9 | 6813.9 | 7296.3
Watt Place Rotoflo | 0.9 | 28027.8 | 23853.6 | 24144.3 | 20043 | 19021.5 | 17054.1 | 18900 | 22066.2 | 24526.8 | 27256.5 | 26973.9 | 29028.6
Zwartop Golf Course | 0.9 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
Shoprite Ekhaya | 0.9 | 28380.6 | 24379.2 | 23351.4 | 19887.3 | 17745.3 | 15502.5 | 17358.3 | 20842.2 | 23841 | 27285.3 | 27841.5 | 28779.3
Grootpan | 0.9 | 29074.5 | 26716.5 | 27941.4 | 25610.4 | 25802.1 | 23428.8 | 25632 | 28549.8 | 29561.4 | 31417.2 | 30121.2 | 29445.3
Roan Foods | 1 | 20178 | 17954 | 19150 | 18060 | 18124 | 15908 | 16827 | 19405 | 19981 | 22401 | 20125 | 20771
Engen Kaalfontein | 0.9 | 17370.9 | 15077.7 | 14634 | 12420 | 11402.1 | 9989.1 | 10986.3 | 13108.77 | 14833.17 | 17053.2 | 17239.5 | 17465.4
Checkers Lichtenburg | 0.9 | 26451 | 23215.5 | 23034.6 | 19930.5 | 18754.2 | 16767.9 | 18261 | 21311.1 | 23659.2 | 26865.9 | 27153.9 | 27402.3
Alpine Heath Resort | 0.9 | 28877.4 | 25884.9 | 27341.1 | 27823.5 | 29920.5 | 28644.3 | 28051.2 | 31649.4 | 28250.1 | 28466.1 | 28991.7 | 28903.5
Usave Naboomspruit | 0.9 | 5973.3 | 5271.3 | 5330.7 | 4826.7 | 4649.4 | 4253.4 | 4644.9 | 5254.2 | 5567.4 | 6030.9 | 5897.7 | 5989.5
664.3667

## expected_production
Site Name | Date | Base Expected (kWh) | Commissioned Date | Age (yrs) | Degradation Factor | Expected Production (kWh) | Annual degradation rate | 0.7%
21 Melrose | 2024-01-01 | 2370.6 | 2023-02-06 | 0.90075 | 0.99369 | 2355.6475
21 Melrose | 2024-02-01 | 2680.2 | 2023-02-06 | 0.98563 | 0.9931 | 2661.7073
21 Melrose | 2024-03-01 | 2183.4 | 2023-02-06 | 1.065 | 0.99255 | 2167.1261
21 Melrose | 2024-04-01 | 1873.8 | 2023-02-06 | 1.1499 | 0.99195 | 1858.7252
21 Melrose | 2024-05-01 | 1822.5 | 2023-02-06 | 1.232 | 0.99138 | 1806.7951
21 Melrose | 2024-06-01 | 1629 | 2023-02-06 | 1.3169 | 0.99079 | 1614
21 Melrose | 2024-07-01 | 1814.4 | 2023-02-06 | 1.399 | 0.99022 | 1796.6559
21 Melrose | 2024-08-01 | 2116.8 | 2023-02-06 | 1.4839 | 0.98963 | 2094.8492
21 Melrose | 2024-09-01 | 2275.2 | 2023-02-06 | 1.5688 | 0.98904 | 2250.2646
21 Melrose | 2024-10-01 | 2407.5 | 2023-02-06 | 1.6509 | 0.98847 | 2379.7412
21 Melrose | 2024-11-01 | 2356.2 | 2023-02-06 | 1.7358 | 0.98788 | 2327.6446
21 Melrose | 2024-12-01 | 2482.2 | 2023-02-06 | 1.8179 | 0.98731 | 2450.7032
21 Melrose | 2025-01-01 | 2370.6 | 2023-02-06 | 1.9028 | 0.98672 | 2339.1242
21 Melrose | 2025-02-01 | 2680.2 | 2023-02-06 | 1.9877 | 0.98613 | 2643.0373
21 Melrose | 2025-03-01 | 2183.4 | 2023-02-06 | 2.0643 | 0.9856 | 2151.9666
21 Melrose | 2025-04-01 | 1873.8 | 2023-02-06 | 2.1492 | 0.98502 | 1845.723
21 Melrose | 2025-05-01 | 1822.5 | 2023-02-06 | 2.2313 | 0.98445 | 1794.1562
21 Melrose | 2025-06-01 | 1629 | 2023-02-06 | 2.3162 | 0.98386 | 1602.7097
21 Melrose | 2025-07-01 | 1814.4 | 2023-02-06 | 2.3984 | 0.98329 | 1784.0879
21 Melrose | 2025-08-01 | 2116.8 | 2023-02-06 | 2.4832 | 0.98271 | 2080.1953
21 Melrose | 2025-09-01 | 2275.2 | 2023-02-06 | 2.5681 | 0.98212 | 2234.5235
21 Melrose | 2025-10-01 | 2407.5 | 2023-02-06 | 2.6502 | 0.98156 | 2363.0944
21 Melrose | 2025-11-01 | 2356.2 | 2023-02-06 | 2.7351 | 0.98097 | 2311.3622
21 Melrose | 2025-12-01 | 2482.2 | 2023-02-06 | 2.8172 | 0.9804 | 2433.5599
21 Melrose | 2026-01-01 | 2370.6 | 2023-02-06 | 2.9021 | 0.97982 | 2322.7615
21 Melrose | 2026-02-01 | 2680.2 | 2023-02-06 | 2.987 | 0.97924 | 2624.5486
21 Melrose | 2026-03-01 | 2183.4 | 2023-02-06 | 3.0637 | 0.97871 | 2136.9131
21 Melrose | 2026-04-01 | 1873.8 | 2023-02-06 | 3.1485 | 0.97813 | 1832.8117
21 Melrose | 2026-05-01 | 1822.5 | 2023-02-06 | 3.2307 | 0.97756 | 1781.6057
21 Melrose | 2026-06-01 | 1629 | 2023-02-06 | 3.3155 | 0.97698 | 1591.4984
21 Melrose | 2026-07-01 | 1814.4 | 2023-02-06 | 3.3977 | 0.97642 | 1771.6078
21 Melrose | 2026-08-01 | 2116.8 | 2023-02-06 | 3.4825 | 0.97583 | 2065.6438
21 Melrose | 2026-09-01 | 2275.2 | 2023-02-06 | 3.5674 | 0.97525 | 2218.8925
21 Melrose | 2026-10-01 | 2407.5 | 2023-02-06 | 3.6496 | 0.97469 | 2346.564
21 Melrose | 2026-11-01 | 2356.2 | 2023-02-06 | 3.7344 | 0.97411 | 2295.1937
21 Melrose | 2026-12-01 | 2482.2 | 2023-02-06 | 3.8166 | 0.97355 | 2416.5366
African Global Plastics | 2024-01-01 | 22515.905 | 2023-09-27 | 0.26283 | 0.99816 | 22474.3721
African Global Plastics | 2024-02-01 | 19786.13 | 2023-09-27 | 0.34771 | 0.99756 | 19737.8612
African Global Plastics | 2024-03-01 | 20148.4 | 2023-09-27 | 0.4271 | 0.997 | 20088.0404
African Global Plastics | 2024-04-01 | 16764.89 | 2023-09-27 | 0.51198 | 0.99641 | 16704.7042
African Global Plastics | 2024-05-01 | 15972.095 | 2023-09-27 | 0.59411 | 0.99584 | 15905.5757
African Global Plastics | 2024-06-01 | 14367.21 | 2023-09-27 | 0.67899 | 0.99524 | 14298.847
African Global Plastics | 2024-07-01 | 15907.665 | 2023-09-27 | 0.76112 | 0.99467 | 15822.8402
African Global Plastics | 2024-08-01 | 18527.365 | 2023-09-27 | 0.846 | 0.99407 | 18417.5872
African Global Plastics | 2024-09-01 | 20404.335 | 2023-09-27 | 0.93087 | 0.99348 | 20271.3464
African Global Plastics | 2024-10-01 | 22320.66 | 2023-09-27 | 1.013 | 0.99291 | 22162.3907
African Global Plastics | 2024-11-01 | 22520.665 | 2023-09-27 | 1.0979 | 0.99232 | 22347.6498
African Global Plastics | 2024-12-01 | 23777.985 | 2023-09-27 | 1.18 | 0.99175 | 23581.7005
African Global Plastics | 2025-01-01 | 22515.905 | 2023-09-27 | 1.2649 | 0.99115 | 22316.7296
African Global Plastics | 2025-02-01 | 19786.13 | 2023-09-27 | 1.3498 | 0.99056 | 19599.4135
African Global Plastics | 2025-03-01 | 20148.4 | 2023-09-27 | 1.4264 | 0.99003 | 19947.5201
African Global Plastics | 2025-04-01 | 16764.89 | 2023-09-27 | 1.5113 | 0.98944 | 16587.851
African Global Plastics | 2025-05-01 | 15972.095 | 2023-09-27 | 1.5934 | 0.98887 | 15794.3126
African Global Plastics | 2025-06-01 | 14367.21 | 2023-09-27 | 1.6783 | 0.98828 | 14198.8233
African Global Plastics | 2025-07-01 | 15907.665 | 2023-09-27 | 1.7604 | 0.98771 | 15712.1558
African Global Plastics | 2025-08-01 | 18527.365 | 2023-09-27 | 1.8453 | 0.98712 | 18288.752
African Global Plastics | 2025-09-01 | 20404.335 | 2023-09-27 | 1.9302 | 0.98653 | 20129.5437
African Global Plastics | 2025-10-01 | 22320.66 | 2023-09-27 | 2.0123 | 0.98596 | 22007.3598
African Global Plastics | 2025-11-01 | 22520.665 | 2023-09-27 | 2.0972 | 0.98538 | 22191.3229
African Global Plastics | 2025-12-01 | 23777.985 | 2023-09-27 | 2.1793 | 0.98481 | 23416.7412
African Global Plastics | 2026-01-01 | 22515.905 | 2023-09-27 | 2.2642 | 0.98422 | 22160.6191
African Global Plastics | 2026-02-01 | 19786.13 | 2023-09-27 | 2.3491 | 0.98363 | 19462.3111
African Global Plastics | 2026-03-01 | 20148.4 | 2023-09-27 | 2.4257 | 0.9831 | 19807.9827
African Global Plastics | 2026-04-01 | 16764.89 | 2023-09-27 | 2.5106 | 0.98252 | 16471.8153
African Global Plastics | 2026-05-01 | 15972.095 | 2023-09-27 | 2.5927 | 0.98195 | 15683.8278
African Global Plastics | 2026-06-01 | 14367.21 | 2023-09-27 | 2.6776 | 0.98137 | 14099.4994
African Global Plastics | 2026-07-01 | 15907.665 | 2023-09-27 | 2.7598 | 0.9808 | 15602.2457
African Global Plastics | 2026-08-01 | 18527.365 | 2023-09-27 | 2.8446 | 0.98022 | 18160.8181
African Global Plastics | 2026-09-01 | 20404.335 | 2023-09-27 | 2.9295 | 0.97963 | 19988.733
African Global Plastics | 2026-10-01 | 22320.66 | 2023-09-27 | 3.0116 | 0.97907 | 21853.4133
African Global Plastics | 2026-11-01 | 22520.665 | 2023-09-27 | 3.0965 | 0.97848 | 22036.0896
African Global Plastics | 2026-12-01 | 23777.985 | 2023-09-27 | 3.1786 | 0.97792 | 23252.9358
Alpine Heath Residential | 2024-01-01 | 4801.5 | 2025-01-01 | 0 | 1 | 4801.5
Alpine Heath Residential | 2024-02-01 | 4303.8 | 2025-01-01 | 0 | 1 | 4303.8
Alpine Heath Residential | 2024-03-01 | 4545.9 | 2025-01-01 | 0 | 1 | 4545.9
Alpine Heath Residential | 2024-04-01 | 4619.7 | 2025-01-01 | 0 | 1 | 4619.7
Alpine Heath Residential | 2024-05-01 | 4990.5 | 2025-01-01 | 0 | 1 | 4990.5
Alpine Heath Residential | 2024-06-01 | 4761.9 | 2025-01-01 | 0 | 1 | 4761.9
Alpine Heath Residential | 2024-07-01 | 4680.9 | 2025-01-01 | 0 | 1 | 4680.9
Alpine Heath Residential | 2024-08-01 | 5249.7 | 2025-01-01 | 0 | 1 | 5249.7
Alpine Heath Residential | 2024-09-01 | 4694.4 | 2025-01-01 | 0 | 1 | 4694.4
Alpine Heath Residential | 2024-10-01 | 4732.2 | 2025-01-01 | 0 | 1 | 4732.2
Alpine Heath Residential | 2024-11-01 | 4822.2 | 2025-01-01 | 0 | 1 | 4822.2
Alpine Heath Residential | 2024-12-01 | 4805.1 | 2025-01-01 | 0 | 1 | 4805.1
Alpine Heath Residential | 2025-01-01 | 4801.5 | 2025-01-01 | 0 | 1 | 4801.5
Alpine Heath Residential | 2025-02-01 | 4303.8 | 2025-01-01 | 0.084873 | 0.9994 | 4301.2348
Alpine Heath Residential | 2025-03-01 | 4545.9 | 2025-01-01 | 0.16153 | 0.99887 | 4540.7447
Alpine Heath Residential | 2025-04-01 | 4619.7 | 2025-01-01 | 0.24641 | 0.99827 | 4611.7106
Alpine Heath Residential | 2025-05-01 | 4990.5 | 2025-01-01 | 0.32854 | 0.99769 | 4978.9958
Alpine Heath Residential | 2025-06-01 | 4761.9 | 2025-01-01 | 0.41342 | 0.9971 | 4748.0911
Alpine Heath Residential | 2025-07-01 | 4680.9 | 2025-01-01 | 0.49555 | 0.99652 | 4664.6339
Alpine Heath Residential | 2025-08-01 | 5249.7 | 2025-01-01 | 0.58042 | 0.99593 | 5228.3392
Alpine Heath Residential | 2025-09-01 | 4694.4 | 2025-01-01 | 0.6653 | 0.99534 | 4672.5121
Alpine Heath Residential | 2025-10-01 | 4732.2 | 2025-01-01 | 0.74743 | 0.99476 | 4707.419
Alpine Heath Residential | 2025-11-01 | 4822.2 | 2025-01-01 | 0.83231 | 0.99417 | 4794.0886
Alpine Heath Residential | 2025-12-01 | 4805.1 | 2025-01-01 | 0.91444 | 0.9936 | 4774.3329
Alpine Heath Residential | 2026-01-01 | 4801.5 | 2025-01-01 | 0.99932 | 0.993 | 4767.9124
Alpine Heath Residential | 2026-02-01 | 4303.8 | 2025-01-01 | 1.0842 | 0.99241 | 4271.1467
Alpine Heath Residential | 2026-03-01 | 4545.9 | 2025-01-01 | 1.1608 | 0.99188 | 4508.9811
Alpine Heath Residential | 2026-04-01 | 4619.7 | 2025-01-01 | 1.2457 | 0.99129 | 4579.4507
Alpine Heath Residential | 2026-05-01 | 4990.5 | 2025-01-01 | 1.3279 | 0.99072 | 4944.1666
Alpine Heath Residential | 2026-06-01 | 4761.9 | 2025-01-01 | 1.4127 | 0.99013 | 4714.8771
Alpine Heath Residential | 2026-07-01 | 4680.9 | 2025-01-01 | 1.4949 | 0.98955 | 4632.0037
Alpine Heath Residential | 2026-08-01 | 5249.7 | 2025-01-01 | 1.5797 | 0.98896 | 5191.7658
Alpine Heath Residential | 2026-09-01 | 4694.4 | 2025-01-01 | 1.6646 | 0.98837 | 4639.8268
Alpine Heath Residential | 2026-10-01 | 4732.2 | 2025-01-01 | 1.7467 | 0.9878 | 4674.4896
Alpine Heath Residential | 2026-11-01 | 4822.2 | 2025-01-01 | 1.8316 | 0.98722 | 4760.5529
Alpine Heath Residential | 2026-12-01 | 4805.1 | 2025-01-01 | 1.9138 | 0.98665 | 4740.9353
BP Parys | 2024-01-01 | 8151.3 | 2024-11-14 | 0 | 1 | 8151.3
BP Parys | 2024-02-01 | 7235.1 | 2024-11-14 | 0 | 1 | 7235.1
BP Parys | 2024-03-01 | 7075.8 | 2024-11-14 | 0 | 1 | 7075.8
BP Parys | 2024-04-01 | 5754.6 | 2024-11-14 | 0 | 1 | 5754.6
BP Parys | 2024-05-01 | 5424.3 | 2024-11-14 | 0 | 1 | 5424.3
BP Parys | 2024-06-01 | 4787.1 | 2024-11-14 | 0 | 1 | 4787.1
BP Parys | 2024-07-01 | 5360.4 | 2024-11-14 | 0 | 1 | 5360.4
BP Parys | 2024-08-01 | 6363 | 2024-11-14 | 0 | 1 | 6363
BP Parys | 2024-09-01 | 7218.9 | 2024-11-14 | 0 | 1 | 7218.9
BP Parys | 2024-10-01 | 7839 | 2024-11-14 | 0 | 1 | 7839
BP Parys | 2024-11-01 | 8191.8 | 2024-11-14 | 0 | 1 | 8191.8
BP Parys | 2024-12-01 | 8227.8 | 2024-11-14 | 0.046543 | 0.99967 | 8225.1104
BP Parys | 2025-01-01 | 8151.3 | 2024-11-14 | 0.13142 | 0.99908 | 8143.7786
BP Parys | 2025-02-01 | 7235.1 | 2024-11-14 | 0.21629 | 0.99848 | 7224.1157
BP Parys | 2025-03-01 | 7075.8 | 2024-11-14 | 0.29295 | 0.99794 | 7061.254
BP Parys | 2025-04-01 | 5754.6 | 2024-11-14 | 0.37782 | 0.99735 | 5739.3472
BP Parys | 2025-05-01 | 5424.3 | 2024-11-14 | 0.45996 | 0.99677 | 5406.8022
BP Parys | 2025-06-01 | 4787.1 | 2024-11-14 | 0.54483 | 0.99618 | 4768.8136
BP Parys | 2025-07-01 | 5360.4 | 2024-11-14 | 0.62697 | 0.99561 | 5336.8436
BP Parys | 2025-08-01 | 6363 | 2024-11-14 | 0.71184 | 0.99501 | 6331.2618
BP Parys | 2025-09-01 | 7218.9 | 2024-11-14 | 0.79671 | 0.99442 | 7178.6115
BP Parys | 2025-10-01 | 7839 | 2024-11-14 | 0.87885 | 0.99385 | 7790.7544
BP Parys | 2025-11-01 | 8191.8 | 2024-11-14 | 0.96372 | 0.99325 | 8136.5306
BP Parys | 2025-12-01 | 8227.8 | 2024-11-14 | 1.0459 | 0.99268 | 8167.5739
BP Parys | 2026-01-01 | 8151.3 | 2024-11-14 | 1.1307 | 0.99209 | 8086.811
BP Parys | 2026-02-01 | 7235.1 | 2024-11-14 | 1.2156 | 0.9915 | 7173.5813
BP Parys | 2026-03-01 | 7075.8 | 2024-11-14 | 1.2923 | 0.99096 | 7011.8589
BP Parys | 2026-04-01 | 5754.6 | 2024-11-14 | 1.3771 | 0.99037 | 5699.1991
BP Parys | 2026-05-01 | 5424.3 | 2024-11-14 | 1.4593 | 0.9898 | 5368.9804
BP Parys | 2026-06-01 | 4787.1 | 2024-11-14 | 1.5441 | 0.98921 | 4735.4547
BP Parys | 2026-07-01 | 5360.4 | 2024-11-14 | 1.6263 | 0.98864 | 5299.5112
BP Parys | 2026-08-01 | 6363 | 2024-11-14 | 1.7112 | 0.98805 | 6286.9732
BP Parys | 2026-09-01 | 7218.9 | 2024-11-14 | 1.796 | 0.98746 | 7128.3954
BP Parys | 2026-10-01 | 7839 | 2024-11-14 | 1.8782 | 0.98689 | 7736.2563
BP Parys | 2026-11-01 | 8191.8 | 2024-11-14 | 1.963 | 0.98631 | 8079.6137
BP Parys | 2026-12-01 | 8227.8 | 2024-11-14 | 2.0452 | 0.98574 | 8110.4398
Bendstore Plaza Shops | 2024-01-01 | 16262.2 | 2022-12-13 | 1.0513 | 0.99264 | 16142.5424
Bendstore Plaza Shops | 2024-02-01 | 13986.75 | 2022-12-13 | 1.1362 | 0.99205 | 13875.5601
Bendstore Plaza Shops | 2024-03-01 | 15463.2 | 2022-12-13 | 1.2156 | 0.9915 | 15331.7194
Bendstore Plaza Shops | 2024-04-01 | 14886.05 | 2022-12-13 | 1.3005 | 0.99091 | 14750.6798
Bendstore Plaza Shops | 2024-05-01 | 14411.75 | 2022-12-13 | 1.3826 | 0.99033 | 14272.4558
Bendstore Plaza Shops | 2024-06-01 | 13050.05 | 2022-12-13 | 1.4675 | 0.98974 | 12916.2141
Bendstore Plaza Shops | 2024-07-01 | 13735.15 | 2022-12-13 | 1.5496 | 0.98917 | 13586.4467
Bendstore Plaza Shops | 2024-08-01 | 15350.15 | 2022-12-13 | 1.6345 | 0.98858 | 15174.9119
Bendstore Plaza Shops | 2024-09-01 | 15431.75 | 2022-12-13 | 1.7194 | 0.98799 | 15246.4877
Bendstore Plaza Shops | 2024-10-01 | 14821.45 | 2022-12-13 | 1.8015 | 0.98742 | 14635.0681
Bendstore Plaza Shops | 2024-11-01 | 14695.65 | 2022-12-13 | 1.8864 | 0.98684 | 14502.2012
Bendstore Plaza Shops | 2024-12-01 | 16154.25 | 2022-12-13 | 1.9685 | 0.98627 | 15932.4055
Bendstore Plaza Shops | 2025-01-01 | 16262.2 | 2022-12-13 | 2.0534 | 0.98568 | 16029.3134
Bendstore Plaza Shops | 2025-02-01 | 13986.75 | 2022-12-13 | 2.1383 | 0.98509 | 13778.2325
Bendstore Plaza Shops | 2025-03-01 | 15463.2 | 2022-12-13 | 2.2149 | 0.98456 | 15224.4706
Bendstore Plaza Shops | 2025-04-01 | 14886.05 | 2022-12-13 | 2.2998 | 0.98397 | 14647.4954
Bendstore Plaza Shops | 2025-05-01 | 14411.75 | 2022-12-13 | 2.3819 | 0.98341 | 14172.6167
Bendstore Plaza Shops | 2025-06-01 | 13050.05 | 2022-12-13 | 2.4668 | 0.98282 | 12825.8622
Bendstore Plaza Shops | 2025-07-01 | 13735.15 | 2022-12-13 | 2.5489 | 0.98225 | 13491.4065
Bendstore Plaza Shops | 2025-08-01 | 15350.15 | 2022-12-13 | 2.6338 | 0.98167 | 15068.76
Bendstore Plaza Shops | 2025-09-01 | 15431.75 | 2022-12-13 | 2.7187 | 0.98108 | 15139.8351
Bendstore Plaza Shops | 2025-10-01 | 14821.45 | 2022-12-13 | 2.8008 | 0.98052 | 14532.6925
Bendstore Plaza Shops | 2025-11-01 | 14695.65 | 2022-12-13 | 2.8857 | 0.97993 | 14400.755
Bendstore Plaza Shops | 2025-12-01 | 16154.25 | 2022-12-13 | 2.9678 | 0.97937 | 15820.9547
Bendstore Plaza Shops | 2026-01-01 | 16262.2 | 2022-12-13 | 3.0527 | 0.97878 | 15917.1848
Bendstore Plaza Shops | 2026-02-01 | 13986.75 | 2022-12-13 | 3.1376 | 0.9782 | 13681.8506
Bendstore Plaza Shops | 2026-03-01 | 15463.2 | 2022-12-13 | 3.2142 | 0.97767 | 15117.972
Bendstore Plaza Shops | 2026-04-01 | 14886.05 | 2022-12-13 | 3.2991 | 0.97709 | 14545.0329
Bendstore Plaza Shops | 2026-05-01 | 14411.75 | 2022-12-13 | 3.3812 | 0.97653 | 14073.4761
Bendstore Plaza Shops | 2026-06-01 | 13050.05 | 2022-12-13 | 3.4661 | 0.97595 | 12736.1424
Bendstore Plaza Shops | 2026-07-01 | 13735.15 | 2022-12-13 | 3.5483 | 0.97538 | 13397.031
Bendstore Plaza Shops | 2026-08-01 | 15350.15 | 2022-12-13 | 3.6331 | 0.9748 | 14963.3506
Bendstore Plaza Shops | 2026-09-01 | 15431.75 | 2022-12-13 | 3.718 | 0.97422 | 15033.9285
Bendstore Plaza Shops | 2026-10-01 | 14821.45 | 2022-12-13 | 3.8001 | 0.97366 | 14431.033
Bendstore Plaza Shops | 2026-11-01 | 14695.65 | 2022-12-13 | 3.885 | 0.97308 | 14300.0185
Bendstore Plaza Shops | 2026-12-01 | 16154.25 | 2022-12-13 | 3.9671 | 0.97252 | 15710.2836
Bendstore Spar | 2024-01-01 | 51314.7347 | 2023-12-12 | 0.054757 | 0.99962 | 51295.0004
Bendstore Spar | 2024-02-01 | 44103.2907 | 2023-12-12 | 0.13963 | 0.99902 | 44060.0532
Bendstore Spar | 2024-03-01 | 48739.27 | 2023-12-12 | 0.21903 | 0.99846 | 48664.3381
Bendstore Spar | 2024-04-01 | 46849.8989 | 2023-12-12 | 0.3039 | 0.99787 | 46749.9908
Bendstore Spar | 2024-05-01 | 45273.2333 | 2023-12-12 | 0.38604 | 0.99729 | 45150.6295
Bendstore Spar | 2024-06-01 | 40943.9718 | 2023-12-12 | 0.47091 | 0.9967 | 40808.7544
Bendstore Spar | 2024-07-01 | 43112.803 | 2023-12-12 | 0.55305 | 0.99612 | 42945.6375
Bendstore Spar | 2024-08-01 | 48266.5027 | 2023-12-12 | 0.63792 | 0.99553 | 48050.6978
Bendstore Spar | 2024-09-01 | 48602.8914 | 2023-12-12 | 0.72279 | 0.99494 | 48356.7435
Bendstore Spar | 2024-10-01 | 46748.9108 | 2023-12-12 | 0.80493 | 0.99436 | 46485.3238
Bendstore Spar | 2024-11-01 | 46388.4816 | 2023-12-12 | 0.8898 | 0.99377 | 46099.4341
Bendstore Spar | 2024-12-01 | 50640.3114 | 2023-12-12 | 0.97194 | 0.9932 | 50295.7431
Bendstore Spar | 2025-01-01 | 51314.7347 | 2023-12-12 | 1.0568 | 0.9926 | 50935.2007
Bendstore Spar | 2025-02-01 | 44103.2907 | 2023-12-12 | 1.1417 | 0.99201 | 43751.0017
Bendstore Spar | 2025-03-01 | 48739.27 | 2023-12-12 | 1.2183 | 0.99148 | 48323.92
Bendstore Spar | 2025-04-01 | 46849.8989 | 2023-12-12 | 1.3032 | 0.99089 | 46422.9641
Bendstore Spar | 2025-05-01 | 45273.2333 | 2023-12-12 | 1.3854 | 0.99032 | 44834.7906
Bendstore Spar | 2025-06-01 | 40943.9718 | 2023-12-12 | 1.4702 | 0.98973 | 40523.288
Bendstore Spar | 2025-07-01 | 43112.803 | 2023-12-12 | 1.5524 | 0.98915 | 42645.2231
Bendstore Spar | 2025-08-01 | 48266.5027 | 2023-12-12 | 1.6372 | 0.98856 | 47714.5724
Bendstore Spar | 2025-09-01 | 48602.8914 | 2023-12-12 | 1.7221 | 0.98798 | 48018.4771
Bendstore Spar | 2025-10-01 | 46748.9108 | 2023-12-12 | 1.8042 | 0.98741 | 46160.1485
Bendstore Spar | 2025-11-01 | 46388.4816 | 2023-12-12 | 1.8891 | 0.98682 | 45776.9581
Bendstore Spar | 2025-12-01 | 50640.3114 | 2023-12-12 | 1.9713 | 0.98625 | 49943.9131
Bendstore Spar | 2026-01-01 | 51314.7347 | 2023-12-12 | 2.0561 | 0.98566 | 50578.8975
Bendstore Spar | 2026-02-01 | 44103.2907 | 2023-12-12 | 2.141 | 0.98507 | 43444.9536
Bendstore Spar | 2026-03-01 | 48739.27 | 2023-12-12 | 2.2177 | 0.98454 | 47985.8833
Bendstore Spar | 2026-04-01 | 46849.8989 | 2023-12-12 | 2.3025 | 0.98396 | 46098.225
Bendstore Spar | 2026-05-01 | 45273.2333 | 2023-12-12 | 2.3847 | 0.98339 | 44521.1612
Bendstore Spar | 2026-06-01 | 40943.9718 | 2023-12-12 | 2.4695 | 0.9828 | 40239.8184
Bendstore Spar | 2026-07-01 | 43112.803 | 2023-12-12 | 2.5517 | 0.98224 | 42346.9101
Bendstore Spar | 2026-08-01 | 48266.5027 | 2023-12-12 | 2.6366 | 0.98165 | 47380.7982
Bendstore Spar | 2026-09-01 | 48602.8914 | 2023-12-12 | 2.7214 | 0.98106 | 47682.577
Bendstore Spar | 2026-10-01 | 46748.9108 | 2023-12-12 | 2.8036 | 0.9805 | 45837.2479
Bendstore Spar | 2026-11-01 | 46388.4816 | 2023-12-12 | 2.8884 | 0.97991 | 45456.738
Bendstore Spar | 2026-12-01 | 50640.3114 | 2023-12-12 | 2.9706 | 0.97935 | 49594.5441
Beyerskloof | 2024-01-01 | 13787.1 | 2023-12-12 | 0.054757 | 0.99962 | 13781.7979
Beyerskloof | 2024-02-01 | 11359.8 | 2023-12-12 | 0.13963 | 0.99902 | 11348.6632
Beyerskloof | 2024-03-01 | 10881 | 2023-12-12 | 0.21903 | 0.99846 | 10864.2715
Beyerskloof | 2024-04-01 | 7828.2 | 2023-12-12 | 0.3039 | 0.99787 | 7811.5063
Beyerskloof | 2024-05-01 | 5953.5 | 2023-12-12 | 0.38604 | 0.99729 | 5937.3774
Beyerskloof | 2024-06-01 | 5166 | 2023-12-12 | 0.47091 | 0.9967 | 5148.9393
Beyerskloof | 2024-07-01 | 5564.7 | 2023-12-12 | 0.55305 | 0.99612 | 5543.1234
Beyerskloof | 2024-08-01 | 6960.6 | 2023-12-12 | 0.63792 | 0.99553 | 6929.4784
Beyerskloof | 2024-09-01 | 8946 | 2023-12-12 | 0.72279 | 0.99494 | 8900.6932
Beyerskloof | 2024-10-01 | 11314.8 | 2023-12-12 | 0.80493 | 0.99436 | 11251.0031
Beyerskloof | 2024-11-01 | 12713.4 | 2023-12-12 | 0.8898 | 0.99377 | 12634.1826
Beyerskloof | 2024-12-01 | 13878.9 | 2023-12-12 | 0.97194 | 0.9932 | 13784.4648
Beyerskloof | 2025-01-01 | 13787.1 | 2023-12-12 | 1.0568 | 0.9926 | 13685.1279
Beyerskloof | 2025-02-01 | 11359.8 | 2023-12-12 | 1.1417 | 0.99201 | 11269.06
Beyerskloof | 2025-03-01 | 10881 | 2023-12-12 | 1.2183 | 0.99148 | 10788.2735
Beyerskloof | 2025-04-01 | 7828.2 | 2023-12-12 | 1.3032 | 0.99089 | 7756.863
Beyerskloof | 2025-05-01 | 5953.5 | 2023-12-12 | 1.3854 | 0.99032 | 5895.8441
Beyerskloof | 2025-06-01 | 5166 | 2023-12-12 | 1.4702 | 0.98973 | 5112.9213
Beyerskloof | 2025-07-01 | 5564.7 | 2023-12-12 | 1.5524 | 0.98915 | 5504.348
Beyerskloof | 2025-08-01 | 6960.6 | 2023-12-12 | 1.6372 | 0.98856 | 6881.0051
Beyerskloof | 2025-09-01 | 8946 | 2023-12-12 | 1.7221 | 0.98798 | 8838.4309
Beyerskloof | 2025-10-01 | 11314.8 | 2023-12-12 | 1.8042 | 0.98741 | 11172.2998
Beyerskloof | 2025-11-01 | 12713.4 | 2023-12-12 | 1.8891 | 0.98682 | 12545.8036
Beyerskloof | 2025-12-01 | 13878.9 | 2023-12-12 | 1.9713 | 0.98625 | 13688.0393
Beyerskloof | 2026-01-01 | 13787.1 | 2023-12-12 | 2.0561 | 0.98566 | 13589.3973
Beyerskloof | 2026-02-01 | 11359.8 | 2023-12-12 | 2.141 | 0.98507 | 11190.2304
Beyerskloof | 2026-03-01 | 10881 | 2023-12-12 | 2.2177 | 0.98454 | 10712.8071
Beyerskloof | 2026-04-01 | 7828.2 | 2023-12-12 | 2.3025 | 0.98396 | 7702.602
Beyerskloof | 2026-05-01 | 5953.5 | 2023-12-12 | 2.3847 | 0.98339 | 5854.6013
Beyerskloof | 2026-06-01 | 5166 | 2023-12-12 | 2.4695 | 0.9828 | 5077.1553
Beyerskloof | 2026-07-01 | 5564.7 | 2023-12-12 | 2.5517 | 0.98224 | 5465.8439
Beyerskloof | 2026-08-01 | 6960.6 | 2023-12-12 | 2.6366 | 0.98165 | 6832.8709
Beyerskloof | 2026-09-01 | 8946 | 2023-12-12 | 2.7214 | 0.98106 | 8776.6041
Beyerskloof | 2026-10-01 | 11314.8 | 2023-12-12 | 2.8036 | 0.9805 | 11094.1471
Beyerskloof | 2026-11-01 | 12713.4 | 2023-12-12 | 2.8884 | 0.97991 | 12458.0429
Beyerskloof | 2026-12-01 | 13878.9 | 2023-12-12 | 2.9706 | 0.97935 | 13592.2884
Buffalo Rock | 2024-01-01 | 2202.3 | 2023-09-14 | 0.29843 | 0.99791 | 2197.6881
Buffalo Rock | 2024-02-01 | 1983.6 | 2023-09-14 | 0.3833 | 0.99731 | 1978.2663
Buffalo Rock | 2024-03-01 | 2127.6 | 2023-09-14 | 0.4627 | 0.99676 | 2120.696
Buffalo Rock | 2024-04-01 | 1767.6 | 2023-09-14 | 0.54757 | 0.99616 | 1760.814
Buffalo Rock | 2024-05-01 | 1631.7 | 2023-09-14 | 0.62971 | 0.99559 | 1624.4982
Buffalo Rock | 2024-06-01 | 1480.5 | 2023-09-14 | 0.71458 | 0.99499 | 1473.087
Buffalo Rock | 2024-07-01 | 1612.8 | 2023-09-14 | 0.79671 | 0.99442 | 1603.799
Buffalo Rock | 2024-08-01 | 1764 | 2023-09-14 | 0.88159 | 0.99383 | 1753.1096
Buffalo Rock | 2024-09-01 | 1868.4 | 2023-09-14 | 0.96646 | 0.99323 | 1855.7584
Buffalo Rock | 2024-10-01 | 1900.8 | 2023-09-14 | 1.0486 | 0.99266 | 1886.8502
Buffalo Rock | 2024-11-01 | 1835.1 | 2023-09-14 | 1.1335 | 0.99207 | 1820.5466
Buffalo Rock | 2024-12-01 | 1986.3 | 2023-09-14 | 1.2156 | 0.9915 | 1969.4109
Buffalo Rock | 2025-01-01 | 2202.3 | 2023-09-14 | 1.3005 | 0.99091 | 2182.2728
Buffalo Rock | 2025-02-01 | 1983.6 | 2023-09-14 | 1.3854 | 0.99032 | 1964.3901
Buffalo Rock | 2025-03-01 | 2127.6 | 2023-09-14 | 1.462 | 0.98978 | 2105.8612
Buffalo Rock | 2025-04-01 | 1767.6 | 2023-09-14 | 1.5469 | 0.98919 | 1748.4967
Buffalo Rock | 2025-05-01 | 1631.7 | 2023-09-14 | 1.629 | 0.98862 | 1613.1345
Buffalo Rock | 2025-06-01 | 1480.5 | 2023-09-14 | 1.7139 | 0.98803 | 1462.7825
Buffalo Rock | 2025-07-01 | 1612.8 | 2023-09-14 | 1.796 | 0.98746 | 1592.5801
Buffalo Rock | 2025-08-01 | 1764 | 2023-09-14 | 1.8809 | 0.98687 | 1740.8462
Buffalo Rock | 2025-09-01 | 1868.4 | 2023-09-14 | 1.9658 | 0.98629 | 1842.7769
Buffalo Rock | 2025-10-01 | 1900.8 | 2023-09-14 | 2.0479 | 0.98572 | 1873.6512
Buffalo Rock | 2025-11-01 | 1835.1 | 2023-09-14 | 2.1328 | 0.98513 | 1807.8115
Buffalo Rock | 2025-12-01 | 1986.3 | 2023-09-14 | 2.2149 | 0.98456 | 1955.6344
Buffalo Rock | 2026-01-01 | 2202.3 | 2023-09-14 | 2.2998 | 0.98397 | 2167.0073
Buffalo Rock | 2026-02-01 | 1983.6 | 2023-09-14 | 2.3847 | 0.98339 | 1950.6487
Buffalo Rock | 2026-03-01 | 2127.6 | 2023-09-14 | 2.4613 | 0.98286 | 2091.1302
Buffalo Rock | 2026-04-01 | 1767.6 | 2023-09-14 | 2.5462 | 0.98227 | 1736.2656
Buffalo Rock | 2026-05-01 | 1631.7 | 2023-09-14 | 2.6283 | 0.98171 | 1601.8502
Buffalo Rock | 2026-06-01 | 1480.5 | 2023-09-14 | 2.7132 | 0.98112 | 1452.55
Buffalo Rock | 2026-07-01 | 1612.8 | 2023-09-14 | 2.7953 | 0.98056 | 1581.4396
Buffalo Rock | 2026-08-01 | 1764 | 2023-09-14 | 2.8802 | 0.97997 | 1728.6686
Buffalo Rock | 2026-09-01 | 1868.4 | 2023-09-14 | 2.9651 | 0.97939 | 1829.8863
Buffalo Rock | 2026-10-01 | 1900.8 | 2023-09-14 | 3.0472 | 0.97882 | 1860.5446
Buffalo Rock | 2026-11-01 | 1835.1 | 2023-09-14 | 3.1321 | 0.97824 | 1795.1654
Buffalo Rock | 2026-12-01 | 1986.3 | 2023-09-14 | 3.2142 | 0.97767 | 1941.9543
Checkers De Aar | 2024-01-01 | 26689.5 | 2024-06-06 | 0 | 1 | 26689.5
Checkers De Aar | 2024-02-01 | 20674.8 | 2024-06-06 | 0 | 1 | 20674.8
Checkers De Aar | 2024-03-01 | 20095.2 | 2024-06-06 | 0 | 1 | 20095.2
Checkers De Aar | 2024-04-01 | 16286.4 | 2024-06-06 | 0 | 1 | 16286.4
Checkers De Aar | 2024-05-01 | 13518.9 | 2024-06-06 | 0 | 1 | 13518.9
Checkers De Aar | 2024-06-01 | 11864.7 | 2024-06-06 | 0 | 1 | 11864.7
Checkers De Aar | 2024-07-01 | 13589.1 | 2024-06-06 | 0.068446 | 0.99952 | 13582.5678
Checkers De Aar | 2024-08-01 | 17109 | 2024-06-06 | 0.15332 | 0.99892 | 17090.5833
Checkers De Aar | 2024-09-01 | 19506.6 | 2024-06-06 | 0.23819 | 0.99833 | 19473.9886
Checkers De Aar | 2024-10-01 | 24081.3 | 2024-06-06 | 0.32033 | 0.99775 | 24027.1735
Checkers De Aar | 2024-11-01 | 25889.4 | 2024-06-06 | 0.4052 | 0.99716 | 25815.8135
Checkers De Aar | 2024-12-01 | 27992.7 | 2024-06-06 | 0.48734 | 0.99658 | 27897.0348
Checkers De Aar | 2025-01-01 | 26689.5 | 2024-06-06 | 0.57221 | 0.99599 | 26582.4353
Checkers De Aar | 2025-02-01 | 20674.8 | 2024-06-06 | 0.65708 | 0.99539 | 20579.5899
Checkers De Aar | 2025-03-01 | 20095.2 | 2024-06-06 | 0.73374 | 0.99486 | 19991.8904
Checkers De Aar | 2025-04-01 | 16286.4 | 2024-06-06 | 0.81862 | 0.99427 | 16193.0143
Checkers De Aar | 2025-05-01 | 13518.9 | 2024-06-06 | 0.90075 | 0.99369 | 13433.63
Checkers De Aar | 2025-06-01 | 11864.7 | 2024-06-06 | 0.98563 | 0.9931 | 11782.8368
Checkers De Aar | 2025-07-01 | 13589.1 | 2024-06-06 | 1.0678 | 0.99253 | 13487.5547
Checkers De Aar | 2025-08-01 | 17109 | 2024-06-06 | 1.1526 | 0.99194 | 16971.0308
Checkers De Aar | 2025-09-01 | 19506.6 | 2024-06-06 | 1.2375 | 0.99134 | 19337.7636
Checkers De Aar | 2025-10-01 | 24081.3 | 2024-06-06 | 1.3196 | 0.99077 | 23859.098
Checkers De Aar | 2025-11-01 | 25889.4 | 2024-06-06 | 1.4045 | 0.99018 | 25635.2261
Checkers De Aar | 2025-12-01 | 27992.7 | 2024-06-06 | 1.4867 | 0.98961 | 27701.8888
Checkers De Aar | 2026-01-01 | 26689.5 | 2024-06-06 | 1.5715 | 0.98902 | 26396.4851
Checkers De Aar | 2026-02-01 | 20674.8 | 2024-06-06 | 1.6564 | 0.98843 | 20435.631
Checkers De Aar | 2026-03-01 | 20095.2 | 2024-06-06 | 1.7331 | 0.9879 | 19852.0426
Checkers De Aar | 2026-04-01 | 16286.4 | 2024-06-06 | 1.8179 | 0.98731 | 16079.7405
Checkers De Aar | 2026-05-01 | 13518.9 | 2024-06-06 | 1.9001 | 0.98674 | 13339.6587
Checkers De Aar | 2026-06-01 | 11864.7 | 2024-06-06 | 1.9849 | 0.98615 | 11700.4132
Checkers De Aar | 2026-07-01 | 13589.1 | 2024-06-06 | 2.0671 | 0.98558 | 13393.2062
Checkers De Aar | 2026-08-01 | 17109 | 2024-06-06 | 2.152 | 0.985 | 16852.3147
Checkers De Aar | 2026-09-01 | 19506.6 | 2024-06-06 | 2.2368 | 0.98441 | 19202.4916
Checkers De Aar | 2026-10-01 | 24081.3 | 2024-06-06 | 2.319 | 0.98384 | 23692.1983
Checkers De Aar | 2026-11-01 | 25889.4 | 2024-06-06 | 2.4038 | 0.98326 | 25455.9019
Checkers De Aar | 2026-12-01 | 27992.7 | 2024-06-06 | 2.486 | 0.98269 | 27508.1078
Checkers Silverlakes Gen | 2024-01-01 | 21105 | 2025/02/29 |  | 1 | 21105
Checkers Silverlakes Gen | 2024-02-01 | 18220.5 | 2025/02/29 |  | 1 | 18220.5
Checkers Silverlakes Gen | 2024-03-01 | 18368.1 | 2025/02/29 |  | 1 | 18368.1
Checkers Silverlakes Gen | 2024-04-01 | 15103.8 | 2025/02/29 |  | 1 | 15103.8
Checkers Silverlakes Gen | 2024-05-01 | 14130 | 2025/02/29 |  | 1 | 14130
Checkers Silverlakes Gen | 2024-06-01 | 12619.8 | 2025/02/29 |  | 1 | 12619.8
Checkers Silverlakes Gen | 2024-07-01 | 14002.2 | 2025/02/29 |  | 1 | 14002.2
Checkers Silverlakes Gen | 2024-08-01 | 16641.9 | 2025/02/29 |  | 1 | 16641.9
Checkers Silverlakes Gen | 2024-09-01 | 18626.4 | 2025/02/29 |  | 1 | 18626.4
Checkers Silverlakes Gen | 2024-10-01 | 20503.8 | 2025/02/29 |  | 1 | 20503.8
Checkers Silverlakes Gen | 2024-11-01 | 20601 | 2025/02/29 |  | 1 | 20601
Checkers Silverlakes Gen | 2024-12-01 | 22024.8 | 2025/02/29 |  | 1 | 22024.8
Checkers Silverlakes Gen | 2025-01-01 | 21105 | 2025/02/29 |  | 1 | 21105
Checkers Silverlakes Gen | 2025-02-01 | 18220.5 | 2025/02/29 |  | 1 | 18220.5
Checkers Silverlakes Gen | 2025-03-01 | 18368.1 | 2025/02/29 |  | 1 | 18368.1
Checkers Silverlakes Gen | 2025-04-01 | 15103.8 | 2025/02/29 |  | 1 | 15103.8
Checkers Silverlakes Gen | 2025-05-01 | 14130 | 2025/02/29 |  | 1 | 14130
Checkers Silverlakes Gen | 2025-06-01 | 12619.8 | 2025/02/29 |  | 1 | 12619.8
Checkers Silverlakes Gen | 2025-07-01 | 14002.2 | 2025/02/29 |  | 1 | 14002.2
Checkers Silverlakes Gen | 2025-08-01 | 16641.9 | 2025/02/29 |  | 1 | 16641.9
Checkers Silverlakes Gen | 2025-09-01 | 18626.4 | 2025/02/29 |  | 1 | 18626.4
Checkers Silverlakes Gen | 2025-10-01 | 20503.8 | 2025/02/29 |  | 1 | 20503.8
Checkers Silverlakes Gen | 2025-11-01 | 20601 | 2025/02/29 |  | 1 | 20601
Checkers Silverlakes Gen | 2025-12-01 | 22024.8 | 2025/02/29 |  | 1 | 22024.8
Checkers Silverlakes Gen | 2026-01-01 | 21105 | 2025/02/29 |  | 1 | 21105
Checkers Silverlakes Gen | 2026-02-01 | 18220.5 | 2025/02/29 |  | 1 | 18220.5
Checkers Silverlakes Gen | 2026-03-01 | 18368.1 | 2025/02/29 |  | 1 | 18368.1
Checkers Silverlakes Gen | 2026-04-01 | 15103.8 | 2025/02/29 |  | 1 | 15103.8
Checkers Silverlakes Gen | 2026-05-01 | 14130 | 2025/02/29 |  | 1 | 14130
Checkers Silverlakes Gen | 2026-06-01 | 12619.8 | 2025/02/29 |  | 1 | 12619.8
Checkers Silverlakes Gen | 2026-07-01 | 14002.2 | 2025/02/29 |  | 1 | 14002.2
Checkers Silverlakes Gen | 2026-08-01 | 16641.9 | 2025/02/29 |  | 1 | 16641.9
Checkers Silverlakes Gen | 2026-09-01 | 18626.4 | 2025/02/29 |  | 1 | 18626.4
Checkers Silverlakes Gen | 2026-10-01 | 20503.8 | 2025/02/29 |  | 1 | 20503.8
Checkers Silverlakes Gen | 2026-11-01 | 20601 | 2025/02/29 |  | 1 | 20601
Checkers Silverlakes Gen | 2026-12-01 | 22024.8 | 2025/02/29 |  | 1 | 22024.8
Checkers Silverlakes No Gen | 2024-01-01 | 21105 | 2025/02/29 |  | 1 | 21105
Checkers Silverlakes No Gen | 2024-02-01 | 18220.5 | 2025/02/29 |  | 1 | 18220.5
Checkers Silverlakes No Gen | 2024-03-01 | 18368.1 | 2025/02/29 |  | 1 | 18368.1
Checkers Silverlakes No Gen | 2024-04-01 | 15103.8 | 2025/02/29 |  | 1 | 15103.8
Checkers Silverlakes No Gen | 2024-05-01 | 14130 | 2025/02/29 |  | 1 | 14130
Checkers Silverlakes No Gen | 2024-06-01 | 12619.8 | 2025/02/29 |  | 1 | 12619.8
Checkers Silverlakes No Gen | 2024-07-01 | 14002.2 | 2025/02/29 |  | 1 | 14002.2
Checkers Silverlakes No Gen | 2024-08-01 | 16641.9 | 2025/02/29 |  | 1 | 16641.9
Checkers Silverlakes No Gen | 2024-09-01 | 18626.4 | 2025/02/29 |  | 1 | 18626.4
Checkers Silverlakes No Gen | 2024-10-01 | 20503.8 | 2025/02/29 |  | 1 | 20503.8
Checkers Silverlakes No Gen | 2024-11-01 | 20601 | 2025/02/29 |  | 1 | 20601
Checkers Silverlakes No Gen | 2024-12-01 | 22024.8 | 2025/02/29 |  | 1 | 22024.8
Checkers Silverlakes No Gen | 2025-01-01 | 21105 | 2025/02/29 |  | 1 | 21105
Checkers Silverlakes No Gen | 2025-02-01 | 18220.5 | 2025/02/29 |  | 1 | 18220.5
Checkers Silverlakes No Gen | 2025-03-01 | 18368.1 | 2025/02/29 |  | 1 | 18368.1
Checkers Silverlakes No Gen | 2025-04-01 | 15103.8 | 2025/02/29 |  | 1 | 15103.8
Checkers Silverlakes No Gen | 2025-05-01 | 14130 | 2025/02/29 |  | 1 | 14130
Checkers Silverlakes No Gen | 2025-06-01 | 12619.8 | 2025/02/29 |  | 1 | 12619.8
Checkers Silverlakes No Gen | 2025-07-01 | 14002.2 | 2025/02/29 |  | 1 | 14002.2
Checkers Silverlakes No Gen | 2025-08-01 | 16641.9 | 2025/02/29 |  | 1 | 16641.9
Checkers Silverlakes No Gen | 2025-09-01 | 18626.4 | 2025/02/29 |  | 1 | 18626.4
Checkers Silverlakes No Gen | 2025-10-01 | 20503.8 | 2025/02/29 |  | 1 | 20503.8
Checkers Silverlakes No Gen | 2025-11-01 | 20601 | 2025/02/29 |  | 1 | 20601
Checkers Silverlakes No Gen | 2025-12-01 | 22024.8 | 2025/02/29 |  | 1 | 22024.8
Checkers Silverlakes No Gen | 2026-01-01 | 21105 | 2025/02/29 |  | 1 | 21105
Checkers Silverlakes No Gen | 2026-02-01 | 18220.5 | 2025/02/29 |  | 1 | 18220.5
Checkers Silverlakes No Gen | 2026-03-01 | 18368.1 | 2025/02/29 |  | 1 | 18368.1
Checkers Silverlakes No Gen | 2026-04-01 | 15103.8 | 2025/02/29 |  | 1 | 15103.8
Checkers Silverlakes No Gen | 2026-05-01 | 14130 | 2025/02/29 |  | 1 | 14130
Checkers Silverlakes No Gen | 2026-06-01 | 12619.8 | 2025/02/29 |  | 1 | 12619.8
Checkers Silverlakes No Gen | 2026-07-01 | 14002.2 | 2025/02/29 |  | 1 | 14002.2
Checkers Silverlakes No Gen | 2026-08-01 | 16641.9 | 2025/02/29 |  | 1 | 16641.9
Checkers Silverlakes No Gen | 2026-09-01 | 18626.4 | 2025/02/29 |  | 1 | 18626.4
Checkers Silverlakes No Gen | 2026-10-01 | 20503.8 | 2025/02/29 |  | 1 | 20503.8
Checkers Silverlakes No Gen | 2026-11-01 | 20601 | 2025/02/29 |  | 1 | 20601
Checkers Silverlakes No Gen | 2026-12-01 | 22024.8 | 2025/02/29 |  | 1 | 22024.8
Checkrite Inanda | 2024-01-01 | 8664.3 | 2024-06-28 | 0 | 1 | 8664.3
Checkrite Inanda | 2024-02-01 | 8100 | 2024-06-28 | 0 | 1 | 8100
Checkrite Inanda | 2024-03-01 | 7805.7 | 2024-06-28 | 0 | 1 | 7805.7
Checkrite Inanda | 2024-04-01 | 6534 | 2024-06-28 | 0 | 1 | 6534
Checkrite Inanda | 2024-05-01 | 5592.6 | 2024-06-28 | 0 | 1 | 5592.6
Checkrite Inanda | 2024-06-01 | 5059.8 | 2024-06-28 | 0 | 1 | 5059.8
Checkrite Inanda | 2024-07-01 | 5372.1 | 2024-06-28 | 0.0082136 | 0.99994 | 5371.7901
Checkrite Inanda | 2024-08-01 | 6485.4 | 2024-06-28 | 0.093087 | 0.99935 | 6481.1606
Checkrite Inanda | 2024-09-01 | 6914.7 | 2024-06-28 | 0.17796 | 0.99875 | 6906.0613
Checkrite Inanda | 2024-10-01 | 8033.4 | 2024-06-28 | 0.2601 | 0.99817 | 8018.7358
Checkrite Inanda | 2024-11-01 | 8012.7 | 2024-06-28 | 0.34497 | 0.99758 | 7993.3065
Checkrite Inanda | 2024-12-01 | 8547.3 | 2024-06-28 | 0.4271 | 0.997 | 8521.6944
Checkrite Inanda | 2025-01-01 | 8664.3 | 2024-06-28 | 0.51198 | 0.99641 | 8633.1953
Checkrite Inanda | 2025-02-01 | 8100 | 2024-06-28 | 0.59685 | 0.99582 | 8066.1106
Checkrite Inanda | 2025-03-01 | 7805.7 | 2024-06-28 | 0.67351 | 0.99528 | 7768.8572
Checkrite Inanda | 2025-04-01 | 6534 | 2024-06-28 | 0.75838 | 0.99469 | 6499.2836
Checkrite Inanda | 2025-05-01 | 5592.6 | 2024-06-28 | 0.84052 | 0.99411 | 5559.6767
Checkrite Inanda | 2025-06-01 | 5059.8 | 2024-06-28 | 0.92539 | 0.99352 | 5027.0153
Checkrite Inanda | 2025-07-01 | 5372.1 | 2024-06-28 | 1.0075 | 0.99295 | 5334.2132
Checkrite Inanda | 2025-08-01 | 6485.4 | 2024-06-28 | 1.0924 | 0.99236 | 6435.8234
Checkrite Inanda | 2025-09-01 | 6914.7 | 2024-06-28 | 1.1773 | 0.99176 | 6857.7519
Checkrite Inanda | 2025-10-01 | 8033.4 | 2024-06-28 | 1.2594 | 0.99119 | 7962.6429
Checkrite Inanda | 2025-11-01 | 8012.7 | 2024-06-28 | 1.3443 | 0.9906 | 7937.3915
Checkrite Inanda | 2025-12-01 | 8547.3 | 2024-06-28 | 1.4264 | 0.99003 | 8462.0833
Checkrite Inanda | 2026-01-01 | 8664.3 | 2024-06-28 | 1.5113 | 0.98944 | 8572.8041
Checkrite Inanda | 2026-02-01 | 8100 | 2024-06-28 | 1.5962 | 0.98885 | 8009.6864
Checkrite Inanda | 2026-03-01 | 7805.7 | 2024-06-28 | 1.6728 | 0.98832 | 7714.5123
Checkrite Inanda | 2026-04-01 | 6534 | 2024-06-28 | 1.7577 | 0.98773 | 6453.8196
Checkrite Inanda | 2026-05-01 | 5592.6 | 2024-06-28 | 1.8398 | 0.98716 | 5520.7855
Checkrite Inanda | 2026-06-01 | 5059.8 | 2024-06-28 | 1.9247 | 0.98657 | 4991.8502
Checkrite Inanda | 2026-07-01 | 5372.1 | 2024-06-28 | 2.0068 | 0.986 | 5296.8991
Checkrite Inanda | 2026-08-01 | 6485.4 | 2024-06-28 | 2.0917 | 0.98541 | 6390.8034
Checkrite Inanda | 2026-09-01 | 6914.7 | 2024-06-28 | 2.1766 | 0.98483 | 6809.7803
Checkrite Inanda | 2026-10-01 | 8033.4 | 2024-06-28 | 2.2587 | 0.98426 | 7906.9424
Checkrite Inanda | 2026-11-01 | 8012.7 | 2024-06-28 | 2.3436 | 0.98367 | 7881.8677
Checkrite Inanda | 2026-12-01 | 8547.3 | 2024-06-28 | 2.4257 | 0.9831 | 8402.8891
Club Houghton | 2024-01-01 | 5767.2 | 2022-04-14 | 1.7166 | 0.98801 | 5698.0728
Club Houghton | 2024-02-01 | 4828.5 | 2022-04-14 | 1.8015 | 0.98742 | 4767.7809
Club Houghton | 2024-03-01 | 4913.1 | 2022-04-14 | 1.8809 | 0.98687 | 4848.612
Club Houghton | 2024-04-01 | 4149.9 | 2022-04-14 | 1.9658 | 0.98629 | 4092.9886
Club Houghton | 2024-05-01 | 3937.5 | 2022-04-14 | 2.0479 | 0.98572 | 3881.2614
Club Houghton | 2024-06-01 | 3463.2 | 2022-04-14 | 2.1328 | 0.98513 | 3411.7011
Club Houghton | 2024-07-01 | 3874.5 | 2022-04-14 | 2.2149 | 0.98456 | 3814.6833
Club Houghton | 2024-08-01 | 4560.3 | 2022-04-14 | 2.2998 | 0.98397 | 4487.2195
Club Houghton | 2024-09-01 | 5033.7 | 2022-04-14 | 2.3847 | 0.98339 | 4950.0809
Club Houghton | 2024-10-01 | 5613.3 | 2022-04-14 | 2.4668 | 0.98282 | 5516.8687
Club Houghton | 2024-11-01 | 5712.3 | 2022-04-14 | 2.5517 | 0.98224 | 5610.8218
Club Houghton | 2024-12-01 | 6027.3 | 2022-04-14 | 2.6338 | 0.98167 | 5916.8111
Club Houghton | 2025-01-01 | 5767.2 | 2022-04-14 | 2.7187 | 0.98108 | 5658.1047
Club Houghton | 2025-02-01 | 4828.5 | 2022-04-14 | 2.8036 | 0.9805 | 4734.3381
Club Houghton | 2025-03-01 | 4913.1 | 2022-04-14 | 2.8802 | 0.97997 | 4814.6949
Club Houghton | 2025-04-01 | 4149.9 | 2022-04-14 | 2.9651 | 0.97939 | 4064.3572
Club Houghton | 2025-05-01 | 3937.5 | 2022-04-14 | 3.0472 | 0.97882 | 3854.1111
Club Houghton | 2025-06-01 | 3463.2 | 2022-04-14 | 3.1321 | 0.97824 | 3387.8355
Club Houghton | 2025-07-01 | 3874.5 | 2022-04-14 | 3.2142 | 0.97767 | 3787.9988
Club Houghton | 2025-08-01 | 4560.3 | 2022-04-14 | 3.2991 | 0.97709 | 4455.8304
Club Houghton | 2025-09-01 | 5033.7 | 2022-04-14 | 3.384 | 0.97651 | 4915.454
Club Houghton | 2025-10-01 | 5613.3 | 2022-04-14 | 3.4661 | 0.97595 | 5478.277
Club Houghton | 2025-11-01 | 5712.3 | 2022-04-14 | 3.551 | 0.97536 | 5571.5728
Club Houghton | 2025-12-01 | 6027.3 | 2022-04-14 | 3.6331 | 0.9748 | 5875.4216
Club Houghton | 2026-01-01 | 5767.2 | 2022-04-14 | 3.718 | 0.97422 | 5618.525
Club Houghton | 2026-02-01 | 4828.5 | 2022-04-14 | 3.8029 | 0.97364 | 4701.2204
Club Houghton | 2026-03-01 | 4913.1 | 2022-04-14 | 3.8795 | 0.97312 | 4781.015
Club Houghton | 2026-04-01 | 4149.9 | 2022-04-14 | 3.9644 | 0.97254 | 4035.9261
Club Houghton | 2026-05-01 | 3937.5 | 2022-04-14 | 4.0465 | 0.97197 | 3827.1507
Club Houghton | 2026-06-01 | 3463.2 | 2022-04-14 | 4.1314 | 0.9714 | 3364.1368
Club Houghton | 2026-07-01 | 3874.5 | 2022-04-14 | 4.2136 | 0.97084 | 3761.5008
Club Houghton | 2026-08-01 | 4560.3 | 2022-04-14 | 4.2984 | 0.97026 | 4424.6608
Club Houghton | 2026-09-01 | 5033.7 | 2022-04-14 | 4.3833 | 0.96968 | 4881.0693
Club Houghton | 2026-10-01 | 5613.3 | 2022-04-14 | 4.4654 | 0.96912 | 5439.9552
Club Houghton | 2026-11-01 | 5712.3 | 2022-04-14 | 4.5503 | 0.96854 | 5532.5984
Club Houghton | 2026-12-01 | 6027.3 | 2022-04-14 | 4.6324 | 0.96798 | 5834.3217
Coldstar International | 2024-01-01 | 4897.02 | 2022-03-23 | 1.7769 | 0.9876 | 4836.2763
Coldstar International | 2024-02-01 | 4496.245 | 2022-03-23 | 1.8617 | 0.98701 | 4437.826
Coldstar International | 2024-03-01 | 4548.605 | 2022-03-23 | 1.9411 | 0.98646 | 4487.0024
Coldstar International | 2024-04-01 | 3805.195 | 2022-03-23 | 2.026 | 0.98587 | 3751.4232
Coldstar International | 2024-05-01 | 3522.57 | 2022-03-23 | 2.1081 | 0.9853 | 3470.7889
Coldstar International | 2024-06-01 | 3187.925 | 2022-03-23 | 2.193 | 0.98471 | 3139.191
Coldstar International | 2024-07-01 | 3416.15 | 2022-03-23 | 2.2752 | 0.98414 | 3361.9868
Coldstar International | 2024-08-01 | 3857.045 | 2022-03-23 | 2.36 | 0.98356 | 3793.6289
Coldstar International | 2024-09-01 | 3805.705 | 2022-03-23 | 2.4449 | 0.98297 | 3740.902
Coldstar International | 2024-10-01 | 4238.695 | 2022-03-23 | 2.527 | 0.98241 | 4164.1159
Coldstar International | 2024-11-01 | 4335.34 | 2022-03-23 | 2.6119 | 0.98182 | 4256.5219
Coldstar International | 2024-12-01 | 5058.01 | 2022-03-23 | 2.694 | 0.98125 | 4963.1891
Coldstar International | 2025-01-01 | 4897.02 | 2022-03-23 | 2.7789 | 0.98067 | 4802.3531
Coldstar International | 2025-02-01 | 4496.245 | 2022-03-23 | 2.8638 | 0.98008 | 4406.6976
Coldstar International | 2025-03-01 | 4548.605 | 2022-03-23 | 2.9405 | 0.97956 | 4455.6148
Coldstar International | 2025-04-01 | 3805.195 | 2022-03-23 | 3.0253 | 0.97897 | 3725.1812
Coldstar International | 2025-05-01 | 3522.57 | 2022-03-23 | 3.1075 | 0.97841 | 3446.51
Coldstar International | 2025-06-01 | 3187.925 | 2022-03-23 | 3.1923 | 0.97782 | 3117.2317
Coldstar International | 2025-07-01 | 3416.15 | 2022-03-23 | 3.2745 | 0.97726 | 3338.4689
Coldstar International | 2025-08-01 | 3857.045 | 2022-03-23 | 3.3593 | 0.97668 | 3767.0916
Coldstar International | 2025-09-01 | 3805.705 | 2022-03-23 | 3.4442 | 0.9761 | 3714.7336
Coldstar International | 2025-10-01 | 4238.695 | 2022-03-23 | 3.5264 | 0.97553 | 4134.987
Coldstar International | 2025-11-01 | 4335.34 | 2022-03-23 | 3.6112 | 0.97495 | 4226.7466
Coldstar International | 2025-12-01 | 5058.01 | 2022-03-23 | 3.6934 | 0.97439 | 4928.4705
Coldstar International | 2026-01-01 | 4897.02 | 2022-03-23 | 3.7782 | 0.97381 | 4768.7595
Coldstar International | 2026-02-01 | 4496.245 | 2022-03-23 | 3.8631 | 0.97323 | 4375.8718
Coldstar International | 2026-03-01 | 4548.605 | 2022-03-23 | 3.9398 | 0.9727 | 4424.4468
Coldstar International | 2026-04-01 | 3805.195 | 2022-03-23 | 4.0246 | 0.97212 | 3699.1227
Coldstar International | 2026-05-01 | 3522.57 | 2022-03-23 | 4.1068 | 0.97156 | 3422.4009
Coldstar International | 2026-06-01 | 3187.925 | 2022-03-23 | 4.1916 | 0.97098 | 3095.4259
Coldstar International | 2026-07-01 | 3416.15 | 2022-03-23 | 4.2738 | 0.97042 | 3315.1156
Coldstar International | 2026-08-01 | 3857.045 | 2022-03-23 | 4.3587 | 0.96985 | 3740.74
Coldstar International | 2026-09-01 | 3805.705 | 2022-03-23 | 4.4435 | 0.96927 | 3688.7482
Coldstar International | 2026-10-01 | 4238.695 | 2022-03-23 | 4.5257 | 0.96871 | 4106.0618
Coldstar International | 2026-11-01 | 4335.34 | 2022-03-23 | 4.6105 | 0.96813 | 4197.1796
Coldstar International | 2026-12-01 | 5058.01 | 2022-03-23 | 4.6927 | 0.96757 | 4893.9947
Cultura Fresh | 2024-01-01 | 11798.1 | 2024-08-05 | 0 | 1 | 11798.1
Cultura Fresh | 2024-02-01 | 10269.9 | 2024-08-05 | 0 | 1 | 10269.9
Cultura Fresh | 2024-03-01 | 10571.4 | 2024-08-05 | 0 | 1 | 10571.4
Cultura Fresh | 2024-04-01 | 8335.8 | 2024-08-05 | 0 | 1 | 8335.8
Cultura Fresh | 2024-05-01 | 6723.9 | 2024-08-05 | 0 | 1 | 6723.9
Cultura Fresh | 2024-06-01 | 5859.9 | 2024-08-05 | 0 | 1 | 5859.9
Cultura Fresh | 2024-07-01 | 6453 | 2024-08-05 | 0 | 1 | 6453
Cultura Fresh | 2024-08-01 | 7491.6 | 2024-08-05 | 0 | 1 | 7491.6
Cultura Fresh | 2024-09-01 | 8864.1 | 2024-08-05 | 0.073922 | 0.99948 | 8859.4983
Cultura Fresh | 2024-10-01 | 10361.7 | 2024-08-05 | 0.15606 | 0.9989 | 10350.3473
Cultura Fresh | 2024-11-01 | 10972.8 | 2024-08-05 | 0.24093 | 0.99831 | 10954.2448
Cultura Fresh | 2024-12-01 | 11630.7 | 2024-08-05 | 0.32307 | 0.99773 | 11604.335
Cultura Fresh | 2025-01-01 | 11798.1 | 2024-08-05 | 0.40794 | 0.99714 | 11764.3395
Cultura Fresh | 2025-02-01 | 10269.9 | 2024-08-05 | 0.49281 | 0.99654 | 10234.4089
Cultura Fresh | 2025-03-01 | 10571.4 | 2024-08-05 | 0.56947 | 0.99601 | 10529.1954
Cultura Fresh | 2025-04-01 | 8335.8 | 2024-08-05 | 0.65435 | 0.99541 | 8297.5722
Cultura Fresh | 2025-05-01 | 6723.9 | 2024-08-05 | 0.73648 | 0.99484 | 6689.2037
Cultura Fresh | 2025-06-01 | 5859.9 | 2024-08-05 | 0.82136 | 0.99425 | 5826.1875
Cultura Fresh | 2025-07-01 | 6453 | 2024-08-05 | 0.90349 | 0.99367 | 6412.1746
Cultura Fresh | 2025-08-01 | 7491.6 | 2024-08-05 | 0.98836 | 0.99308 | 7439.7669
Cultura Fresh | 2025-09-01 | 8864.1 | 2024-08-05 | 1.0732 | 0.99249 | 8797.5241
Cultura Fresh | 2025-10-01 | 10361.7 | 2024-08-05 | 1.1554 | 0.99192 | 10277.9443
Cultura Fresh | 2025-11-01 | 10972.8 | 2024-08-05 | 1.2402 | 0.99133 | 10877.6174
Cultura Fresh | 2025-12-01 | 11630.7 | 2024-08-05 | 1.3224 | 0.99075 | 11523.1601
Cultura Fresh | 2026-01-01 | 11798.1 | 2024-08-05 | 1.4073 | 0.99016 | 11682.0453
Cultura Fresh | 2026-02-01 | 10269.9 | 2024-08-05 | 1.4921 | 0.98957 | 10162.8169
Cultura Fresh | 2026-03-01 | 10571.4 | 2024-08-05 | 1.5688 | 0.98904 | 10455.5413
Cultura Fresh | 2026-04-01 | 8335.8 | 2024-08-05 | 1.6537 | 0.98845 | 8239.5288
Cultura Fresh | 2026-05-01 | 6723.9 | 2024-08-05 | 1.7358 | 0.98788 | 6642.4112
Cultura Fresh | 2026-06-01 | 5859.9 | 2024-08-05 | 1.8207 | 0.98729 | 5785.432
Cultura Fresh | 2026-07-01 | 6453 | 2024-08-05 | 1.9028 | 0.98672 | 6367.32
Cultura Fresh | 2026-08-01 | 7491.6 | 2024-08-05 | 1.9877 | 0.98613 | 7387.724
Cultura Fresh | 2026-09-01 | 8864.1 | 2024-08-05 | 2.0726 | 0.98555 | 8735.9834
Cultura Fresh | 2026-10-01 | 10361.7 | 2024-08-05 | 2.1547 | 0.98498 | 10206.0477
Cultura Fresh | 2026-11-01 | 10972.8 | 2024-08-05 | 2.2396 | 0.98439 | 10801.526
Cultura Fresh | 2026-12-01 | 11630.7 | 2024-08-05 | 2.3217 | 0.98382 | 11442.553
Demco | 2024-01-01 | 33516 | 2024-06-17 | 0 | 1 | 33516
Demco | 2024-02-01 | 28776.8 | 2024-06-17 | 0 | 1 | 28776.8
Demco | 2024-03-01 | 29186.4 | 2024-06-17 | 0 | 1 | 29186.4
Demco | 2024-04-01 | 24678.4 | 2024-06-17 | 0 | 1 | 24678.4
Demco | 2024-05-01 | 23380.8 | 2024-06-17 | 0 | 1 | 23380.8
Demco | 2024-06-01 | 20986.4 | 2024-06-17 | 0 | 1 | 20986.4
Demco | 2024-07-01 | 23255.2 | 2024-06-17 | 0.03833 | 0.99973 | 23248.9393
Demco | 2024-08-01 | 27306.4 | 2024-06-17 | 0.1232 | 0.99913 | 27282.7777
Demco | 2024-09-01 | 30312 | 2024-06-17 | 0.20808 | 0.99854 | 30267.7266
Demco | 2024-10-01 | 33024 | 2024-06-17 | 0.29021 | 0.99796 | 32956.7449
Demco | 2024-11-01 | 33214.4 | 2024-06-17 | 0.37509 | 0.99737 | 33127.0008
Demco | 2024-12-01 | 35066.4 | 2024-06-17 | 0.45722 | 0.99679 | 34953.9543
Demco | 2025-01-01 | 33516 | 2024-06-17 | 0.54209 | 0.9962 | 33388.6136
Demco | 2025-02-01 | 28776.8 | 2024-06-17 | 0.62697 | 0.99561 | 28650.3397
Demco | 2025-03-01 | 29186.4 | 2024-06-17 | 0.70363 | 0.99507 | 29042.4959
Demco | 2025-04-01 | 24678.4 | 2024-06-17 | 0.7885 | 0.99448 | 24542.0863
Demco | 2025-05-01 | 23380.8 | 2024-06-17 | 0.87064 | 0.9939 | 23238.2421
Demco | 2025-06-01 | 20986.4 | 2024-06-17 | 0.95551 | 0.99331 | 20846.0091
Demco | 2025-07-01 | 23255.2 | 2024-06-17 | 1.0376 | 0.99274 | 23086.3077
Demco | 2025-08-01 | 27306.4 | 2024-06-17 | 1.1225 | 0.99215 | 27091.9286
Demco | 2025-09-01 | 30312 | 2024-06-17 | 1.2074 | 0.99155 | 30055.997
Demco | 2025-10-01 | 33024 | 2024-06-17 | 1.2895 | 0.99098 | 32726.205
Demco | 2025-11-01 | 33214.4 | 2024-06-17 | 1.3744 | 0.99039 | 32895.27
Demco | 2025-12-01 | 35066.4 | 2024-06-17 | 1.4565 | 0.98982 | 34709.4435
Demco | 2026-01-01 | 33516 | 2024-06-17 | 1.5414 | 0.98923 | 33155.0527
Demco | 2026-02-01 | 28776.8 | 2024-06-17 | 1.6263 | 0.98864 | 28449.9241
Demco | 2026-03-01 | 29186.4 | 2024-06-17 | 1.7029 | 0.98811 | 28839.3371
Demco | 2026-04-01 | 24678.4 | 2024-06-17 | 1.7878 | 0.98752 | 24370.4088
Demco | 2026-05-01 | 23380.8 | 2024-06-17 | 1.87 | 0.98695 | 23075.6853
Demco | 2026-06-01 | 20986.4 | 2024-06-17 | 1.9548 | 0.98636 | 20700.1866
Demco | 2026-07-01 | 23255.2 | 2024-06-17 | 2.037 | 0.98579 | 22924.8138
Demco | 2026-08-01 | 27306.4 | 2024-06-17 | 2.1218 | 0.98521 | 26902.4144
Demco | 2026-09-01 | 30312 | 2024-06-17 | 2.2067 | 0.98462 | 29845.7485
Demco | 2026-10-01 | 33024 | 2024-06-17 | 2.2888 | 0.98405 | 32497.2778
Demco | 2026-11-01 | 33214.4 | 2024-06-17 | 2.3737 | 0.98346 | 32665.1602
Demco | 2026-12-01 | 35066.4 | 2024-06-17 | 2.4559 | 0.9829 | 34466.6432
Engen Lotus Gardens | 2024-01-01 | 2461.5 | 2025-10-21 | 0 | 1 | 2461.5
Engen Lotus Gardens | 2024-02-01 | 2300.4 | 2025-10-21 | 0 | 1 | 2300.4
Engen Lotus Gardens | 2024-03-01 | 2281.5 | 2025-10-21 | 0 | 1 | 2281.5
Engen Lotus Gardens | 2024-04-01 | 2197.8 | 2025-10-21 | 0 | 1 | 2197.8
Engen Lotus Gardens | 2024-05-01 | 2226.6 | 2025-10-21 | 0 | 1 | 2226.6
Engen Lotus Gardens | 2024-06-01 | 2480.4 | 2025-10-21 | 0 | 1 | 2480.4
Engen Lotus Gardens | 2024-07-01 | 2349.9 | 2025-10-21 | 0 | 1 | 2349.9
Engen Lotus Gardens | 2024-08-01 | 2520 | 2025-10-21 | 0 | 1 | 2520
Engen Lotus Gardens | 2024-09-01 | 2436.3 | 2025-10-21 | 0 | 1 | 2436.3
Engen Lotus Gardens | 2024-10-01 | 2425.5 | 2025-10-21 | 0 | 1 | 2425.5
Engen Lotus Gardens | 2024-11-01 | 2356.2 | 2025-10-21 | 0 | 1 | 2356.2
Engen Lotus Gardens | 2024-12-01 | 2437.2 | 2025-10-21 | 0 | 1 | 2437.2
Engen Lotus Gardens | 2025-01-01 | 2461.5 | 2025-10-21 | 0 | 1 | 2461.5
Engen Lotus Gardens | 2025-02-01 | 2300.4 | 2025-10-21 | 0 | 1 | 2300.4
Engen Lotus Gardens | 2025-03-01 | 2281.5 | 2025-10-21 | 0 | 1 | 2281.5
Engen Lotus Gardens | 2025-04-01 | 2197.8 | 2025-10-21 | 0 | 1 | 2197.8
Engen Lotus Gardens | 2025-05-01 | 2226.6 | 2025-10-21 | 0 | 1 | 2226.6
Engen Lotus Gardens | 2025-06-01 | 2480.4 | 2025-10-21 | 0 | 1 | 2480.4
Engen Lotus Gardens | 2025-07-01 | 2349.9 | 2025-10-21 | 0 | 1 | 2349.9
Engen Lotus Gardens | 2025-08-01 | 2520 | 2025-10-21 | 0 | 1 | 2520
Engen Lotus Gardens | 2025-09-01 | 2436.3 | 2025-10-21 | 0 | 1 | 2436.3
Engen Lotus Gardens | 2025-10-01 | 2425.5 | 2025-10-21 | 0 | 1 | 2425.5
Engen Lotus Gardens | 2025-11-01 | 2356.2 | 2025-10-21 | 0.030116 | 0.99979 | 2355.7016
Engen Lotus Gardens | 2025-12-01 | 2437.2 | 2025-10-21 | 0.11225 | 0.99921 | 2435.279
Engen Lotus Gardens | 2026-01-01 | 2461.5 | 2025-10-21 | 0.19713 | 0.99862 | 2458.0938
Engen Lotus Gardens | 2026-02-01 | 2300.4 | 2025-10-21 | 0.282 | 0.99802 | 2295.8476
Engen Lotus Gardens | 2026-03-01 | 2281.5 | 2025-10-21 | 0.35866 | 0.99748 | 2275.7591
Engen Lotus Gardens | 2026-04-01 | 2197.8 | 2025-10-21 | 0.44353 | 0.99689 | 2190.9631
Engen Lotus Gardens | 2026-05-01 | 2226.6 | 2025-10-21 | 0.52567 | 0.99631 | 2218.3932
Engen Lotus Gardens | 2026-06-01 | 2480.4 | 2025-10-21 | 0.61054 | 0.99572 | 2469.7848
Engen Lotus Gardens | 2026-07-01 | 2349.9 | 2025-10-21 | 0.69268 | 0.99515 | 2338.4937
Engen Lotus Gardens | 2026-08-01 | 2520 | 2025-10-21 | 0.77755 | 0.99455 | 2506.2733
Engen Lotus Gardens | 2026-09-01 | 2436.3 | 2025-10-21 | 0.86242 | 0.99396 | 2421.5851
Engen Lotus Gardens | 2026-10-01 | 2425.5 | 2025-10-21 | 0.94456 | 0.99339 | 2409.4597
Engen Lotus Gardens | 2026-11-01 | 2356.2 | 2025-10-21 | 1.0294 | 0.99279 | 2339.2229
Engen Lotus Gardens | 2026-12-01 | 2437.2 | 2025-10-21 | 1.1116 | 0.99222 | 2418.2436
Giba Gorge Main | 2024-01-01 | 13584 | 2021-10-10 | 2.2259 | 0.98449 | 13373.2539
Giba Gorge Main | 2024-02-01 | 12445.28 | 2021-10-10 | 2.3107 | 0.9839 | 12244.8977
Giba Gorge Main | 2024-03-01 | 12742.08 | 2021-10-10 | 2.3901 | 0.98335 | 12529.9285
Giba Gorge Main | 2024-04-01 | 10941.84 | 2021-10-10 | 2.475 | 0.98276 | 10753.2489
Giba Gorge Main | 2024-05-01 | 9881.28 | 2021-10-10 | 2.5572 | 0.9822 | 9705.3671
Giba Gorge Main | 2024-06-01 | 9234.88 | 2021-10-10 | 2.642 | 0.98161 | 9065.0685
Giba Gorge Main | 2024-07-01 | 9756.08 | 2021-10-10 | 2.7242 | 0.98105 | 9571.1608
Giba Gorge Main | 2024-08-01 | 10822.4 | 2021-10-10 | 2.809 | 0.98046 | 10610.9414
Giba Gorge Main | 2024-09-01 | 10915.68 | 2021-10-10 | 2.8939 | 0.97988 | 10696.0199
Giba Gorge Main | 2024-10-01 | 12133.12 | 2021-10-10 | 2.976 | 0.97931 | 11882.1033
Giba Gorge Main | 2024-11-01 | 12325.9898 | 2021-10-10 | 3.0609 | 0.97873 | 12063.7883
Giba Gorge Main | 2024-12-01 | 13473.8978 | 2021-10-10 | 3.1431 | 0.97816 | 13179.6712
Giba Gorge Main | 2025-01-01 | 13584 | 2021-10-10 | 3.2279 | 0.97758 | 13279.4495
Giba Gorge Main | 2025-02-01 | 12445.28 | 2021-10-10 | 3.3128 | 0.977 | 12159.008
Giba Gorge Main | 2025-03-01 | 12742.08 | 2021-10-10 | 3.3895 | 0.97647 | 12442.2788
Giba Gorge Main | 2025-04-01 | 10941.84 | 2021-10-10 | 3.4743 | 0.97589 | 10678.0275
Giba Gorge Main | 2025-05-01 | 9881.28 | 2021-10-10 | 3.5565 | 0.97533 | 9637.4759
Giba Gorge Main | 2025-06-01 | 9234.88 | 2021-10-10 | 3.6413 | 0.97475 | 9001.6563
Giba Gorge Main | 2025-07-01 | 9756.08 | 2021-10-10 | 3.7235 | 0.97418 | 9504.2084
Giba Gorge Main | 2025-08-01 | 10822.4 | 2021-10-10 | 3.8084 | 0.9736 | 10536.7154
Giba Gorge Main | 2025-09-01 | 10915.68 | 2021-10-10 | 3.8932 | 0.97302 | 10621.1988
Giba Gorge Main | 2025-10-01 | 12133.12 | 2021-10-10 | 3.9754 | 0.97246 | 11798.9853
Giba Gorge Main | 2025-11-01 | 12325.9898 | 2021-10-10 | 4.0602 | 0.97188 | 11979.3994
Giba Gorge Main | 2025-12-01 | 13473.8978 | 2021-10-10 | 4.1424 | 0.97132 | 13087.4765
Giba Gorge Main | 2026-01-01 | 13584 | 2021-10-10 | 4.2272 | 0.97074 | 13186.5568
Giba Gorge Main | 2026-02-01 | 12445.28 | 2021-10-10 | 4.3121 | 0.97016 | 12073.953
Giba Gorge Main | 2026-03-01 | 12742.08 | 2021-10-10 | 4.3888 | 0.96964 | 12355.2423
Giba Gorge Main | 2026-04-01 | 10941.84 | 2021-10-10 | 4.4736 | 0.96906 | 10603.3323
Giba Gorge Main | 2026-05-01 | 9881.28 | 2021-10-10 | 4.5558 | 0.9685 | 9570.0596
Giba Gorge Main | 2026-06-01 | 9234.88 | 2021-10-10 | 4.6407 | 0.96793 | 8938.6877
Giba Gorge Main | 2026-07-01 | 9756.08 | 2021-10-10 | 4.7228 | 0.96737 | 9437.7243
Giba Gorge Main | 2026-08-01 | 10822.4 | 2021-10-10 | 4.8077 | 0.96679 | 10463.0087
Giba Gorge Main | 2026-09-01 | 10915.68 | 2021-10-10 | 4.8925 | 0.96622 | 10546.9011
Giba Gorge Main | 2026-10-01 | 12133.12 | 2021-10-10 | 4.9747 | 0.96566 | 11716.4487
Giba Gorge Main | 2026-11-01 | 12325.9898 | 2021-10-10 | 5.0595 | 0.96508 | 11895.6008
Giba Gorge Main | 2026-12-01 | 13473.8978 | 2021-10-10 | 5.1417 | 0.96453 | 12995.9266
Giba Gorge Storage | 2024-01-01 | 11384.625 | 2021-10-10 | 2.2259 | 0.98449 | 11208.0006
Giba Gorge Storage | 2024-02-01 | 10143.6 | 2021-10-10 | 2.3107 | 0.9839 | 9980.2772
Giba Gorge Storage | 2024-03-01 | 10396.425 | 2021-10-10 | 2.3901 | 0.98335 | 10223.3279
Giba Gorge Storage | 2024-04-01 | 8842.275 | 2021-10-10 | 2.475 | 0.98276 | 8689.8715
Giba Gorge Storage | 2024-05-01 | 7963.725 | 2021-10-10 | 2.5572 | 0.9822 | 7821.9497
Giba Gorge Storage | 2024-06-01 | 7364.325 | 2021-10-10 | 2.642 | 0.98161 | 7228.9094
Giba Gorge Storage | 2024-07-01 | 7865.175 | 2021-10-10 | 2.7242 | 0.98105 | 7716.0965
Giba Gorge Storage | 2024-08-01 | 8758.725 | 2021-10-10 | 2.809 | 0.98046 | 8587.5885
Giba Gorge Storage | 2024-09-01 | 8956.35 | 2021-10-10 | 2.8939 | 0.97988 | 8776.1182
Giba Gorge Storage | 2024-10-01 | 9957.75 | 2021-10-10 | 2.976 | 0.97931 | 9751.7385
Giba Gorge Storage | 2024-11-01 | 10009.6634 | 2021-10-10 | 3.0609 | 0.97873 | 9796.7354
Giba Gorge Storage | 2024-12-01 | 11121.5007 | 2021-10-10 | 3.1431 | 0.97816 | 10878.6429
Giba Gorge Storage | 2025-01-01 | 11384.625 | 2021-10-10 | 3.2279 | 0.97758 | 11129.3841
Giba Gorge Storage | 2025-02-01 | 10143.6 | 2021-10-10 | 3.3128 | 0.977 | 9910.2723
Giba Gorge Storage | 2025-03-01 | 10396.425 | 2021-10-10 | 3.3895 | 0.97647 | 10151.8134
Giba Gorge Storage | 2025-04-01 | 8842.275 | 2021-10-10 | 3.4743 | 0.97589 | 8629.0839
Giba Gorge Storage | 2025-05-01 | 7963.725 | 2021-10-10 | 3.5565 | 0.97533 | 7767.2334
Giba Gorge Storage | 2025-06-01 | 7364.325 | 2021-10-10 | 3.6413 | 0.97475 | 7178.3415
Giba Gorge Storage | 2025-07-01 | 7865.175 | 2021-10-10 | 3.7235 | 0.97418 | 7662.1207
Giba Gorge Storage | 2025-08-01 | 8758.725 | 2021-10-10 | 3.8084 | 0.9736 | 8527.5163
Giba Gorge Storage | 2025-09-01 | 8956.35 | 2021-10-10 | 3.8932 | 0.97302 | 8714.7272
Giba Gorge Storage | 2025-10-01 | 9957.75 | 2021-10-10 | 3.9754 | 0.97246 | 9683.5229
Giba Gorge Storage | 2025-11-01 | 10009.6634 | 2021-10-10 | 4.0602 | 0.97188 | 9728.205
Giba Gorge Storage | 2025-12-01 | 11121.5007 | 2021-10-10 | 4.1424 | 0.97132 | 10802.5443
Giba Gorge Storage | 2026-01-01 | 11384.625 | 2021-10-10 | 4.2272 | 0.97074 | 11051.5315
Giba Gorge Storage | 2026-02-01 | 10143.6 | 2021-10-10 | 4.3121 | 0.97016 | 9840.9477
Giba Gorge Storage | 2026-03-01 | 10396.425 | 2021-10-10 | 4.3888 | 0.96964 | 10080.7992
Giba Gorge Storage | 2026-04-01 | 8842.275 | 2021-10-10 | 4.4736 | 0.96906 | 8568.7215
Giba Gorge Storage | 2026-05-01 | 7963.725 | 2021-10-10 | 4.5558 | 0.9685 | 7712.8998
Giba Gorge Storage | 2026-06-01 | 7364.325 | 2021-10-10 | 4.6407 | 0.96793 | 7128.1274
Giba Gorge Storage | 2026-07-01 | 7865.175 | 2021-10-10 | 4.7228 | 0.96737 | 7608.5224
Giba Gorge Storage | 2026-08-01 | 8758.725 | 2021-10-10 | 4.8077 | 0.96679 | 8467.8644
Giba Gorge Storage | 2026-09-01 | 8956.35 | 2021-10-10 | 4.8925 | 0.96622 | 8653.7657
Giba Gorge Storage | 2026-10-01 | 9957.75 | 2021-10-10 | 4.9747 | 0.96566 | 9615.7845
Giba Gorge Storage | 2026-11-01 | 10009.6634 | 2021-10-10 | 5.0595 | 0.96508 | 9660.154
Giba Gorge Storage | 2026-12-01 | 11121.5007 | 2021-10-10 | 5.1417 | 0.96453 | 10726.9781
Golden Spot Resort | 2024-01-01 | 4042.8 | 2023-05-27 | 0.59959 | 0.9958 | 4025.808
Golden Spot Resort | 2024-02-01 | 3650.4 | 2023-05-27 | 0.68446 | 0.9952 | 3632.8907
Golden Spot Resort | 2024-03-01 | 3957.3 | 2023-05-27 | 0.76386 | 0.99465 | 3936.1227
Golden Spot Resort | 2024-04-01 | 3279.6 | 2023-05-27 | 0.84873 | 0.99406 | 3260.1051
Golden Spot Resort | 2024-05-01 | 3050.1 | 2023-05-27 | 0.93087 | 0.99348 | 3030.2205
Golden Spot Resort | 2024-06-01 | 2790 | 2023-05-27 | 1.0157 | 0.99289 | 2770.1636
Golden Spot Resort | 2024-07-01 | 3044.7 | 2023-05-27 | 1.0979 | 0.99232 | 3021.3091
Golden Spot Resort | 2024-08-01 | 3298.5 | 2023-05-27 | 1.1828 | 0.99173 | 3271.2084
Golden Spot Resort | 2024-09-01 | 3492.9 | 2023-05-27 | 1.2676 | 0.99113 | 3461.9353
Golden Spot Resort | 2024-10-01 | 3509.1 | 2023-05-27 | 1.3498 | 0.99056 | 3475.9855
Golden Spot Resort | 2024-11-01 | 3348 | 2023-05-27 | 1.4346 | 0.98997 | 3314.4291
Golden Spot Resort | 2024-12-01 | 3591.9 | 2023-05-27 | 1.5168 | 0.9894 | 3553.8325
Golden Spot Resort | 2025-01-01 | 4042.8 | 2023-05-27 | 1.6016 | 0.98881 | 3997.5697
Golden Spot Resort | 2025-02-01 | 3650.4 | 2023-05-27 | 1.6865 | 0.98822 | 3607.4084
Golden Spot Resort | 2025-03-01 | 3957.3 | 2023-05-27 | 1.7632 | 0.98769 | 3908.5886
Golden Spot Resort | 2025-04-01 | 3279.6 | 2023-05-27 | 1.848 | 0.9871 | 3237.2999
Golden Spot Resort | 2025-05-01 | 3050.1 | 2023-05-27 | 1.9302 | 0.98653 | 3009.0234
Golden Spot Resort | 2025-06-01 | 2790 | 2023-05-27 | 2.0151 | 0.98594 | 2750.7857
Golden Spot Resort | 2025-07-01 | 3044.7 | 2023-05-27 | 2.0972 | 0.98538 | 3000.1743
Golden Spot Resort | 2025-08-01 | 3298.5 | 2023-05-27 | 2.1821 | 0.98479 | 3248.3255
Golden Spot Resort | 2025-09-01 | 3492.9 | 2023-05-27 | 2.2669 | 0.9842 | 3437.7183
Golden Spot Resort | 2025-10-01 | 3509.1 | 2023-05-27 | 2.3491 | 0.98363 | 3451.6702
Golden Spot Resort | 2025-11-01 | 3348 | 2023-05-27 | 2.4339 | 0.98305 | 3291.244
Golden Spot Resort | 2025-12-01 | 3591.9 | 2023-05-27 | 2.5161 | 0.98248 | 3528.9726
Golden Spot Resort | 2026-01-01 | 4042.8 | 2023-05-27 | 2.601 | 0.9819 | 3969.6058
Golden Spot Resort | 2026-02-01 | 3650.4 | 2023-05-27 | 2.6858 | 0.98131 | 3582.1738
Golden Spot Resort | 2026-03-01 | 3957.3 | 2023-05-27 | 2.7625 | 0.98078 | 3881.2472
Golden Spot Resort | 2026-04-01 | 3279.6 | 2023-05-27 | 2.8474 | 0.9802 | 3214.6543
Golden Spot Resort | 2026-05-01 | 3050.1 | 2023-05-27 | 2.9295 | 0.97963 | 2987.9746
Golden Spot Resort | 2026-06-01 | 2790 | 2023-05-27 | 3.0144 | 0.97905 | 2731.5434
Golden Spot Resort | 2026-07-01 | 3044.7 | 2023-05-27 | 3.0965 | 0.97848 | 2979.1874
Golden Spot Resort | 2026-08-01 | 3298.5 | 2023-05-27 | 3.1814 | 0.9779 | 3225.6027
Golden Spot Resort | 2026-09-01 | 3492.9 | 2023-05-27 | 3.2663 | 0.97732 | 3413.6706
Golden Spot Resort | 2026-10-01 | 3509.1 | 2023-05-27 | 3.3484 | 0.97675 | 3427.525
Golden Spot Resort | 2026-11-01 | 3348 | 2023-05-27 | 3.4333 | 0.97617 | 3268.221
Golden Spot Resort | 2026-12-01 | 3591.9 | 2023-05-27 | 3.5154 | 0.97561 | 3504.2866
Golden Spot Shops | 2024-01-01 | 3618 | 2023-05-26 | 0.60233 | 0.99578 | 3602.7242
Golden Spot Shops | 2024-02-01 | 3254.4 | 2023-05-26 | 0.6872 | 0.99518 | 3238.7278
Golden Spot Shops | 2024-03-01 | 3608.1 | 2023-05-26 | 0.7666 | 0.99463 | 3588.7224
Golden Spot Shops | 2024-04-01 | 2962.8 | 2023-05-26 | 0.85147 | 0.99404 | 2945.1316
Golden Spot Shops | 2024-05-01 | 2723.4 | 2023-05-26 | 0.93361 | 0.99346 | 2705.5978
Golden Spot Shops | 2024-06-01 | 2461.5 | 2023-05-26 | 1.0185 | 0.99287 | 2443.9522
Golden Spot Shops | 2024-07-01 | 2701.8 | 2023-05-26 | 1.1006 | 0.9923 | 2680.9918
Golden Spot Shops | 2024-08-01 | 2973.6 | 2023-05-26 | 1.1855 | 0.99171 | 2948.9399
Golden Spot Shops | 2024-09-01 | 3147.3 | 2023-05-26 | 1.2704 | 0.99112 | 3119.339
Golden Spot Shops | 2024-10-01 | 3179.7 | 2023-05-26 | 1.3525 | 0.99054 | 3149.6334
Golden Spot Shops | 2024-11-01 | 3013.2 | 2023-05-26 | 1.4374 | 0.98995 | 2982.9289
Golden Spot Shops | 2024-12-01 | 3204 | 2023-05-26 | 1.5195 | 0.98938 | 3169.9825
Golden Spot Shops | 2025-01-01 | 3618 | 2023-05-26 | 1.6044 | 0.98879 | 3577.4535
Golden Spot Shops | 2025-02-01 | 3254.4 | 2023-05-26 | 1.6893 | 0.9882 | 3216.0103
Golden Spot Shops | 2025-03-01 | 3608.1 | 2023-05-26 | 1.7659 | 0.98767 | 3563.6185
Golden Spot Shops | 2025-04-01 | 2962.8 | 2023-05-26 | 1.8508 | 0.98708 | 2924.5298
Golden Spot Shops | 2025-05-01 | 2723.4 | 2023-05-26 | 1.9329 | 0.98651 | 2686.6715
Golden Spot Shops | 2025-06-01 | 2461.5 | 2023-05-26 | 2.0178 | 0.98593 | 2426.8562
Golden Spot Shops | 2025-07-01 | 2701.8 | 2023-05-26 | 2.0999 | 0.98536 | 2662.2377
Golden Spot Shops | 2025-08-01 | 2973.6 | 2023-05-26 | 2.1848 | 0.98477 | 2928.3114
Golden Spot Shops | 2025-09-01 | 3147.3 | 2023-05-26 | 2.2697 | 0.98418 | 3097.5186
Golden Spot Shops | 2025-10-01 | 3179.7 | 2023-05-26 | 2.3518 | 0.98362 | 3127.601
Golden Spot Shops | 2025-11-01 | 3013.2 | 2023-05-26 | 2.4367 | 0.98303 | 2962.0626
Golden Spot Shops | 2025-12-01 | 3204 | 2023-05-26 | 2.5188 | 0.98246 | 3147.8078
Golden Spot Shops | 2026-01-01 | 3618 | 2023-05-26 | 2.6037 | 0.98188 | 3552.4284
Golden Spot Shops | 2026-02-01 | 3254.4 | 2023-05-26 | 2.6886 | 0.98129 | 3193.5136
Golden Spot Shops | 2026-03-01 | 3608.1 | 2023-05-26 | 2.7652 | 0.98076 | 3538.6902
Golden Spot Shops | 2026-04-01 | 2962.8 | 2023-05-26 | 2.8501 | 0.98018 | 2904.072
Golden Spot Shops | 2026-05-01 | 2723.4 | 2023-05-26 | 2.9322 | 0.97961 | 2667.8776
Golden Spot Shops | 2026-06-01 | 2461.5 | 2023-05-26 | 3.0171 | 0.97903 | 2409.8798
Golden Spot Shops | 2026-07-01 | 2701.8 | 2023-05-26 | 3.0992 | 0.97846 | 2643.6147
Golden Spot Shops | 2026-08-01 | 2973.6 | 2023-05-26 | 3.1841 | 0.97788 | 2907.8272
Golden Spot Shops | 2026-09-01 | 3147.3 | 2023-05-26 | 3.269 | 0.9773 | 3075.8507
Golden Spot Shops | 2026-10-01 | 3179.7 | 2023-05-26 | 3.3511 | 0.97673 | 3105.7228
Golden Spot Shops | 2026-11-01 | 3013.2 | 2023-05-26 | 3.436 | 0.97615 | 2941.3423
Golden Spot Shops | 2026-12-01 | 3204 | 2023-05-26 | 3.5181 | 0.97559 | 3125.7882
Grootpan | 2024-01-01 | 29074.5 | 2026-03-05 | 0 | 1 | 29074.5
Grootpan | 2024-02-01 | 26716.5 | 2026-03-05 | 0 | 1 | 26716.5
Grootpan | 2024-03-01 | 27941.4 | 2026-03-05 | 0 | 1 | 27941.4
Grootpan | 2024-04-01 | 25610.4 | 2026-03-05 | 0 | 1 | 25610.4
Grootpan | 2024-05-01 | 25802.1 | 2026-03-05 | 0 | 1 | 25802.1
Grootpan | 2024-06-01 | 23428.8 | 2026-03-05 | 0 | 1 | 23428.8
Grootpan | 2024-07-01 | 25632 | 2026-03-05 | 0 | 1 | 25632
Grootpan | 2024-08-01 | 28549.8 | 2026-03-05 | 0 | 1 | 28549.8
Grootpan | 2024-09-01 | 29561.4 | 2026-03-05 | 0 | 1 | 29561.4
Grootpan | 2024-10-01 | 31417.2 | 2026-03-05 | 0 | 1 | 31417.2
Grootpan | 2024-11-01 | 30121.2 | 2026-03-05 | 0 | 1 | 30121.2
Grootpan | 2024-12-01 | 29445.3 | 2026-03-05 | 0 | 1 | 29445.3
Grootpan | 2025-01-01 | 29074.5 | 2026-03-05 | 0 | 1 | 29074.5
Grootpan | 2025-02-01 | 26716.5 | 2026-03-05 | 0 | 1 | 26716.5
Grootpan | 2025-03-01 | 27941.4 | 2026-03-05 | 0 | 1 | 27941.4
Grootpan | 2025-04-01 | 25610.4 | 2026-03-05 | 0 | 1 | 25610.4
Grootpan | 2025-05-01 | 25802.1 | 2026-03-05 | 0 | 1 | 25802.1
Grootpan | 2025-06-01 | 23428.8 | 2026-03-05 | 0 | 1 | 23428.8
Grootpan | 2025-07-01 | 25632 | 2026-03-05 | 0 | 1 | 25632
Grootpan | 2025-08-01 | 28549.8 | 2026-03-05 | 0 | 1 | 28549.8
Grootpan | 2025-09-01 | 29561.4 | 2026-03-05 | 0 | 1 | 29561.4
Grootpan | 2025-10-01 | 31417.2 | 2026-03-05 | 0 | 1 | 31417.2
Grootpan | 2025-11-01 | 30121.2 | 2026-03-05 | 0 | 1 | 30121.2
Grootpan | 2025-12-01 | 29445.3 | 2026-03-05 | 0 | 1 | 29445.3
Grootpan | 2026-01-01 | 29074.5 | 2026-03-05 | 0 | 1 | 29074.5
Grootpan | 2026-02-01 | 26716.5 | 2026-03-05 | 0 | 1 | 26716.5
Grootpan | 2026-03-01 | 27941.4 | 2026-03-05 | 0 | 1 | 27941.4
Grootpan | 2026-04-01 | 25610.4 | 2026-03-05 | 0.073922 | 0.99948 | 25597.1047
Grootpan | 2026-04-01 | 25610.4 | 2026-03-05 | 0.073922 | 0.99948 | 25597.1047
Grootpan | 2026-05-01 | 25802.1 | 2026-03-05 | 0.15606 | 0.9989 | 25773.8301
Grootpan | 2026-06-01 | 23428.8 | 2026-03-05 | 0.24093 | 0.99831 | 23389.1815
Grootpan | 2026-07-01 | 25632 | 2026-03-05 | 0.32307 | 0.99773 | 25573.8963
Grootpan | 2026-08-01 | 28549.8 | 2026-03-05 | 0.40794 | 0.99714 | 28468.1042
Grootpan | 2026-09-01 | 29561.4 | 2026-03-05 | 0.49281 | 0.99654 | 29459.2406
Grootpan | 2026-10-01 | 31417.2 | 2026-03-05 | 0.57495 | 0.99597 | 31290.5683
Grootpan | 2026-11-01 | 30121.2 | 2026-03-05 | 0.65982 | 0.99538 | 29981.9114
Grootpan | 2026-12-01 | 29445.3 | 2026-03-05 | 0.74196 | 0.9948 | 29292.2313
HB Dunn | 2024-01-01 | 4235.4 | 2024-04-25 | 0 | 1 | 4235.4
HB Dunn | 2024-02-01 | 3699 | 2024-04-25 | 0 | 1 | 3699
HB Dunn | 2024-03-01 | 3788.1 | 2024-04-25 | 0 | 1 | 3788.1
HB Dunn | 2024-04-01 | 3184.2 | 2024-04-25 | 0 | 1 | 3184.2
HB Dunn | 2024-05-01 | 3052.8 | 2024-04-25 | 0.016427 | 0.99988 | 3052.4477
HB Dunn | 2024-06-01 | 2752.2 | 2024-04-25 | 0.1013 | 0.99929 | 2750.2422
HB Dunn | 2024-07-01 | 3029.4 | 2024-04-25 | 0.18344 | 0.99871 | 3025.4989
HB Dunn | 2024-08-01 | 3546.9 | 2024-04-25 | 0.26831 | 0.99812 | 3540.2212
HB Dunn | 2024-09-01 | 3911.4 | 2024-04-25 | 0.35318 | 0.99752 | 3901.708
HB Dunn | 2024-10-01 | 4103.1 | 2024-04-25 | 0.43532 | 0.99695 | 4090.5721
HB Dunn | 2024-11-01 | 4120.2 | 2024-04-25 | 0.52019 | 0.99635 | 4105.1717
HB Dunn | 2024-12-01 | 4377.6 | 2024-04-25 | 0.60233 | 0.99578 | 4359.117
HB Dunn | 2025-01-01 | 4235.4 | 2024-04-25 | 0.6872 | 0.99518 | 4215.0036
HB Dunn | 2025-02-01 | 3699 | 2024-04-25 | 0.77207 | 0.99459 | 3678.9927
HB Dunn | 2025-03-01 | 3788.1 | 2024-04-25 | 0.84873 | 0.99406 | 3765.5824
HB Dunn | 2025-04-01 | 3184.2 | 2024-04-25 | 0.93361 | 0.99346 | 3163.3856
HB Dunn | 2025-05-01 | 3052.8 | 2024-04-25 | 1.0157 | 0.99289 | 3031.0952
HB Dunn | 2025-06-01 | 2752.2 | 2024-04-25 | 1.1006 | 0.9923 | 2731.0037
HB Dunn | 2025-07-01 | 3029.4 | 2024-04-25 | 1.1828 | 0.99173 | 3004.3349
HB Dunn | 2025-08-01 | 3546.9 | 2024-04-25 | 1.2676 | 0.99113 | 3515.4566
HB Dunn | 2025-09-01 | 3911.4 | 2024-04-25 | 1.3525 | 0.99054 | 3874.4146
HB Dunn | 2025-10-01 | 4103.1 | 2024-04-25 | 1.4346 | 0.98997 | 4061.9576
HB Dunn | 2025-11-01 | 4120.2 | 2024-04-25 | 1.5195 | 0.98938 | 4076.4551
HB Dunn | 2025-12-01 | 4377.6 | 2024-04-25 | 1.6016 | 0.98881 | 4328.624
HB Dunn | 2026-01-01 | 4235.4 | 2024-04-25 | 1.6865 | 0.98822 | 4185.5187
HB Dunn | 2026-02-01 | 3699 | 2024-04-25 | 1.7714 | 0.98763 | 3653.2573
HB Dunn | 2026-03-01 | 3788.1 | 2024-04-25 | 1.848 | 0.9871 | 3739.2413
HB Dunn | 2026-04-01 | 3184.2 | 2024-04-25 | 1.9329 | 0.98651 | 3141.257
HB Dunn | 2026-05-01 | 3052.8 | 2024-04-25 | 2.0151 | 0.98594 | 3009.892
HB Dunn | 2026-06-01 | 2752.2 | 2024-04-25 | 2.0999 | 0.98536 | 2711.8997
HB Dunn | 2026-07-01 | 3029.4 | 2024-04-25 | 2.1821 | 0.98479 | 2983.3189
HB Dunn | 2026-08-01 | 3546.9 | 2024-04-25 | 2.2669 | 0.9842 | 3490.8651
HB Dunn | 2026-09-01 | 3911.4 | 2024-04-25 | 2.3518 | 0.98362 | 3847.3122
HB Dunn | 2026-10-01 | 4103.1 | 2024-04-25 | 2.4339 | 0.98305 | 4033.5433
HB Dunn | 2026-11-01 | 4120.2 | 2024-04-25 | 2.5188 | 0.98246 | 4047.9393
HB Dunn | 2026-12-01 | 4377.6 | 2024-04-25 | 2.601 | 0.9819 | 4298.3443
Helderberg Collage | 2024-01-01 | 39600.81 | 2019-08-23 | 4.3587 | 0.96985 | 38406.6905
Helderberg Collage | 2024-02-01 | 33064.92 | 2019-08-23 | 4.4435 | 0.96927 | 32048.7699
Helderberg Collage | 2024-03-01 | 32219.55 | 2019-08-23 | 4.5229 | 0.96873 | 31211.9668
Helderberg Collage | 2024-04-01 | 23614.38 | 2019-08-23 | 4.6078 | 0.96815 | 22862.2667
Helderberg Collage | 2024-05-01 | 17952.57 | 2019-08-23 | 4.6899 | 0.96759 | 17370.7589
Helderberg Collage | 2024-06-01 | 14925.6 | 2019-08-23 | 4.7748 | 0.96702 | 14433.2799
Helderberg Collage | 2024-07-01 | 16774.83 | 2019-08-23 | 4.8569 | 0.96646 | 16212.1565
Helderberg Collage | 2024-08-01 | 20886.75 | 2019-08-23 | 4.9418 | 0.96588 | 20174.1201
Helderberg Collage | 2024-09-01 | 26689.95 | 2019-08-23 | 5.0267 | 0.96531 | 25763.957
Helderberg Collage | 2024-10-01 | 33024.69 | 2019-08-23 | 5.1088 | 0.96475 | 31860.5288
Helderberg Collage | 2024-11-01 | 37111.77 | 2019-08-23 | 5.1937 | 0.96417 | 35782.1944
Helderberg Collage | 2024-12-01 | 40125.69 | 2019-08-23 | 5.2758 | 0.96362 | 38665.8215
Helderberg Collage | 2025-01-01 | 39600.81 | 2019-08-23 | 5.3607 | 0.96304 | 38137.2935
Helderberg Collage | 2025-02-01 | 33064.92 | 2019-08-23 | 5.4456 | 0.96247 | 31823.9695
Helderberg Collage | 2025-03-01 | 32219.55 | 2019-08-23 | 5.5222 | 0.96195 | 30993.6321
Helderberg Collage | 2025-04-01 | 23614.38 | 2019-08-23 | 5.6071 | 0.96138 | 22702.34
Helderberg Collage | 2025-05-01 | 17952.57 | 2019-08-23 | 5.6893 | 0.96082 | 17249.2465
Helderberg Collage | 2025-06-01 | 14925.6 | 2019-08-23 | 5.7741 | 0.96025 | 14332.3159
Helderberg Collage | 2025-07-01 | 16774.83 | 2019-08-23 | 5.8563 | 0.9597 | 16098.7488
Helderberg Collage | 2025-08-01 | 20886.75 | 2019-08-23 | 5.9411 | 0.95912 | 20032.9976
Helderberg Collage | 2025-09-01 | 26689.95 | 2019-08-23 | 6.026 | 0.95855 | 25583.7323
Helderberg Collage | 2025-10-01 | 33024.69 | 2019-08-23 | 6.1081 | 0.958 | 31637.6572
Helderberg Collage | 2025-11-01 | 37111.77 | 2019-08-23 | 6.193 | 0.95743 | 35531.8899
Helderberg Collage | 2025-12-01 | 40125.69 | 2019-08-23 | 6.2752 | 0.95688 | 38395.3453
Helderberg Collage | 2026-01-01 | 39600.81 | 2019-08-23 | 6.36 | 0.95631 | 37870.5146
Helderberg Collage | 2026-02-01 | 33064.92 | 2019-08-23 | 6.4449 | 0.95574 | 31601.3536
Helderberg Collage | 2026-03-01 | 32219.55 | 2019-08-23 | 6.5216 | 0.95522 | 30776.8246
Helderberg Collage | 2026-04-01 | 23614.38 | 2019-08-23 | 6.6064 | 0.95465 | 22543.532
Helderberg Collage | 2026-05-01 | 17952.57 | 2019-08-23 | 6.6886 | 0.9541 | 17128.5841
Helderberg Collage | 2026-06-01 | 14925.6 | 2019-08-23 | 6.7734 | 0.95353 | 14232.0581
Helderberg Collage | 2026-07-01 | 16774.83 | 2019-08-23 | 6.8556 | 0.95298 | 15986.1345
Helderberg Collage | 2026-08-01 | 20886.75 | 2019-08-23 | 6.9405 | 0.95242 | 19892.8622
Helderberg Collage | 2026-09-01 | 26689.95 | 2019-08-23 | 7.0253 | 0.95185 | 25404.7683
Helderberg Collage | 2026-10-01 | 33024.69 | 2019-08-23 | 7.1075 | 0.9513 | 31416.3447
Helderberg Collage | 2026-11-01 | 37111.77 | 2019-08-23 | 7.1923 | 0.95073 | 35283.3363
Helderberg Collage | 2026-12-01 | 40125.69 | 2019-08-23 | 7.2745 | 0.95018 | 38126.7612
Hilston Rotoflo | 2024-01-01 | 29391.3 | 2023-05-10 | 0.64613 | 0.99547 | 29258.2001
Hilston Rotoflo | 2024-02-01 | 25677 | 2023-05-10 | 0.73101 | 0.99488 | 25545.4856
Hilston Rotoflo | 2024-03-01 | 24204.6 | 2023-05-10 | 0.8104 | 0.99432 | 24067.2001
Hilston Rotoflo | 2024-04-01 | 21550.5 | 2023-05-10 | 0.89528 | 0.99373 | 21415.3947
Hilston Rotoflo | 2024-05-01 | 19301.4 | 2023-05-10 | 0.97741 | 0.99316 | 19169.3315
Hilston Rotoflo | 2024-06-01 | 17076.6 | 2023-05-10 | 1.0623 | 0.99257 | 16949.6461
Hilston Rotoflo | 2024-07-01 | 19010.7 | 2023-05-10 | 1.1444 | 0.99199 | 18858.4833
Hilston Rotoflo | 2024-08-01 | 22169.7 | 2023-05-10 | 1.2293 | 0.9914 | 21979.0817
Hilston Rotoflo | 2024-09-01 | 24661.8 | 2023-05-10 | 1.3142 | 0.99081 | 24435.1816
Hilston Rotoflo | 2024-10-01 | 27450.9 | 2023-05-10 | 1.3963 | 0.99024 | 27182.9641
Hilston Rotoflo | 2024-11-01 | 28825.2 | 2023-05-10 | 1.4812 | 0.98965 | 28526.8373
Hilston Rotoflo | 2024-12-01 | 28327.5 | 2023-05-10 | 1.5633 | 0.98908 | 28018.1186
Hilston Rotoflo | 2025-01-01 | 29391.3 | 2023-05-10 | 1.6482 | 0.98849 | 29052.9736
Hilston Rotoflo | 2025-02-01 | 25677 | 2023-05-10 | 1.7331 | 0.9879 | 25366.3013
Hilston Rotoflo | 2025-03-01 | 24204.6 | 2023-05-10 | 1.8097 | 0.98737 | 23898.8446
Hilston Rotoflo | 2025-04-01 | 21550.5 | 2023-05-10 | 1.8946 | 0.98678 | 21265.5892
Hilston Rotoflo | 2025-05-01 | 19301.4 | 2023-05-10 | 1.9767 | 0.98621 | 19035.2377
Hilston Rotoflo | 2025-06-01 | 17076.6 | 2023-05-10 | 2.0616 | 0.98562 | 16831.0795
Hilston Rotoflo | 2025-07-01 | 19010.7 | 2023-05-10 | 2.1437 | 0.98505 | 18726.564
Hilston Rotoflo | 2025-08-01 | 22169.7 | 2023-05-10 | 2.2286 | 0.98447 | 21825.333
Hilston Rotoflo | 2025-09-01 | 24661.8 | 2023-05-10 | 2.3135 | 0.98388 | 24264.252
Hilston Rotoflo | 2025-10-01 | 27450.9 | 2023-05-10 | 2.3956 | 0.98331 | 26992.8131
Hilston Rotoflo | 2025-11-01 | 28825.2 | 2023-05-10 | 2.4805 | 0.98273 | 28327.2857
Hilston Rotoflo | 2025-12-01 | 28327.5 | 2023-05-10 | 2.5626 | 0.98216 | 27822.1255
Hilston Rotoflo | 2026-01-01 | 29391.3 | 2023-05-10 | 2.6475 | 0.98157 | 28849.7415
Hilston Rotoflo | 2026-02-01 | 25677 | 2023-05-10 | 2.7324 | 0.98099 | 25188.8583
Hilston Rotoflo | 2026-03-01 | 24204.6 | 2023-05-10 | 2.809 | 0.98046 | 23731.6668
Hilston Rotoflo | 2026-04-01 | 21550.5 | 2023-05-10 | 2.8939 | 0.97988 | 21116.8316
Hilston Rotoflo | 2026-05-01 | 19301.4 | 2023-05-10 | 2.976 | 0.97931 | 18902.0819
Hilston Rotoflo | 2026-06-01 | 17076.6 | 2023-05-10 | 3.0609 | 0.97873 | 16713.3423
Hilston Rotoflo | 2026-07-01 | 19010.7 | 2023-05-10 | 3.1431 | 0.97816 | 18595.5675
Hilston Rotoflo | 2026-08-01 | 22169.7 | 2023-05-10 | 3.2279 | 0.97758 | 21672.6599
Hilston Rotoflo | 2026-09-01 | 24661.8 | 2023-05-10 | 3.3128 | 0.977 | 24094.518
Hilston Rotoflo | 2026-10-01 | 27450.9 | 2023-05-10 | 3.3949 | 0.97643 | 26803.9923
Hilston Rotoflo | 2026-11-01 | 28825.2 | 2023-05-10 | 3.4798 | 0.97585 | 28129.1299
Hilston Rotoflo | 2026-12-01 | 28327.5 | 2023-05-10 | 3.5619 | 0.97529 | 27627.5035
Huis Herfsblaar | 2024-01-01 | 30214.8 | 2024-06-20 | 0 | 1 | 30214.8
Huis Herfsblaar | 2024-02-01 | 26381.7 | 2024-06-20 | 0 | 1 | 26381.7
Huis Herfsblaar | 2024-03-01 | 27566.1 | 2024-06-20 | 0 | 1 | 27566.1
Huis Herfsblaar | 2024-04-01 | 23747.4 | 2024-06-20 | 0 | 1 | 23747.4
Huis Herfsblaar | 2024-05-01 | 22569.3 | 2024-06-20 | 0 | 1 | 22569.3
Huis Herfsblaar | 2024-06-01 | 20228.4 | 2024-06-20 | 0 | 1 | 20228.4
Huis Herfsblaar | 2024-07-01 | 22354.2 | 2024-06-20 | 0.030116 | 0.99979 | 22349.4713
Huis Herfsblaar | 2024-08-01 | 26968.5 | 2024-06-20 | 0.11499 | 0.99919 | 26946.7248
Huis Herfsblaar | 2024-09-01 | 28840.5 | 2024-06-20 | 0.19986 | 0.9986 | 28800.0375
Huis Herfsblaar | 2024-10-01 | 30258 | 2024-06-20 | 0.282 | 0.99802 | 30198.1203
Huis Herfsblaar | 2024-11-01 | 29380.5 | 2024-06-20 | 0.36687 | 0.99743 | 29304.88
Huis Herfsblaar | 2024-12-01 | 31219.2 | 2024-06-20 | 0.44901 | 0.99685 | 31120.8865
Huis Herfsblaar | 2025-01-01 | 30214.8 | 2024-06-20 | 0.53388 | 0.99626 | 30101.6974
Huis Herfsblaar | 2025-02-01 | 26381.7 | 2024-06-20 | 0.61875 | 0.99566 | 26267.2805
Huis Herfsblaar | 2025-03-01 | 27566.1 | 2024-06-20 | 0.69541 | 0.99513 | 27431.7675
Huis Herfsblaar | 2025-04-01 | 23747.4 | 2024-06-20 | 0.78029 | 0.99453 | 23617.5914
Huis Herfsblaar | 2025-05-01 | 22569.3 | 2024-06-20 | 0.86242 | 0.99396 | 22432.9842
Huis Herfsblaar | 2025-06-01 | 20228.4 | 2024-06-20 | 0.9473 | 0.99337 | 20094.2392
Huis Herfsblaar | 2025-07-01 | 22354.2 | 2024-06-20 | 1.0294 | 0.99279 | 22193.1317
Huis Herfsblaar | 2025-08-01 | 26968.5 | 2024-06-20 | 1.1143 | 0.9922 | 26758.2263
Huis Herfsblaar | 2025-09-01 | 28840.5 | 2024-06-20 | 1.1992 | 0.99161 | 28598.5747
Huis Herfsblaar | 2025-10-01 | 30258 | 2024-06-20 | 1.2813 | 0.99104 | 29986.8776
Huis Herfsblaar | 2025-11-01 | 29380.5 | 2024-06-20 | 1.3662 | 0.99045 | 29099.8857
Huis Herfsblaar | 2025-12-01 | 31219.2 | 2024-06-20 | 1.4483 | 0.98988 | 30903.1889
Huis Herfsblaar | 2026-01-01 | 30214.8 | 2024-06-20 | 1.5332 | 0.98929 | 29891.1293
Huis Herfsblaar | 2026-02-01 | 26381.7 | 2024-06-20 | 1.6181 | 0.9887 | 26083.535
Huis Herfsblaar | 2026-03-01 | 27566.1 | 2024-06-20 | 1.6947 | 0.98817 | 27239.8761
Huis Herfsblaar | 2026-04-01 | 23747.4 | 2024-06-20 | 1.7796 | 0.98758 | 23452.381
Huis Herfsblaar | 2026-05-01 | 22569.3 | 2024-06-20 | 1.8617 | 0.98701 | 22276.0604
Huis Herfsblaar | 2026-06-01 | 20228.4 | 2024-06-20 | 1.9466 | 0.98642 | 19953.6754
Huis Herfsblaar | 2026-07-01 | 22354.2 | 2024-06-20 | 2.0287 | 0.98585 | 22037.8858
Huis Herfsblaar | 2026-08-01 | 26968.5 | 2024-06-20 | 2.1136 | 0.98526 | 26571.0465
Huis Herfsblaar | 2026-09-01 | 28840.5 | 2024-06-20 | 2.1985 | 0.98468 | 28398.5212
Huis Herfsblaar | 2026-10-01 | 30258 | 2024-06-20 | 2.2806 | 0.98411 | 29777.1127
Huis Herfsblaar | 2026-11-01 | 29380.5 | 2024-06-20 | 2.3655 | 0.98352 | 28896.3255
Huis Herfsblaar | 2026-12-01 | 31219.2 | 2024-06-20 | 2.4476 | 0.98295 | 30687.0141
IPID - Floor 4 | 2024-01-01 | 7573.5 | 2025-10-04 | 0 | 1 | 7573.5
IPID - Floor 4 | 2024-02-01 | 6513.75 | 2025-10-04 | 0 | 1 | 6513.75
IPID - Floor 4 | 2024-03-01 | 6841.35 | 2025-10-04 | 0 | 1 | 6841.35
IPID - Floor 4 | 2024-04-01 | 618.3 | 2025-10-04 | 0 | 1 | 618.3
IPID - Floor 4 | 2024-05-01 | 5924.7 | 2025-10-04 | 0 | 1 | 5924.7
IPID - Floor 4 | 2024-06-01 | 5295.6 | 2025-10-04 | 0 | 1 | 5295.6
IPID - Floor 4 | 2024-07-01 | 5785.2 | 2025-10-04 | 0 | 1 | 5785.2
IPID - Floor 4 | 2024-08-01 | 6585.3 | 2025-10-04 | 0 | 1 | 6585.3
IPID - Floor 4 | 2024-09-01 | 7018.65 | 2025-10-04 | 0 | 1 | 7018.65
IPID - Floor 4 | 2024-10-01 | 7479.45 | 2025-10-04 | 0 | 1 | 7479.45
IPID - Floor 4 | 2024-11-01 | 7552.8 | 2025-10-04 | 0 | 1 | 7552.8
IPID - Floor 4 | 2024-12-01 | 7415.1 | 2025-10-04 | 0 | 1 | 7415.1
IPID - Floor 4 | 2025-01-01 | 7573.5 | 2025-10-04 | 0 | 1 | 7573.5
IPID - Floor 4 | 2025-02-01 | 6513.75 | 2025-10-04 | 0 | 1 | 6513.75
IPID - Floor 4 | 2025-03-01 | 6841.35 | 2025-10-04 | 0 | 1 | 6841.35
IPID - Floor 4 | 2025-04-01 | 618.3 | 2025-10-04 | 0 | 1 | 618.3
IPID - Floor 4 | 2025-05-01 | 5924.7 | 2025-10-04 | 0 | 1 | 5924.7
IPID - Floor 4 | 2025-06-01 | 5295.6 | 2025-10-04 | 0 | 1 | 5295.6
IPID - Floor 4 | 2025-07-01 | 5785.2 | 2025-10-04 | 0 | 1 | 5785.2
IPID - Floor 4 | 2025-08-01 | 6585.3 | 2025-10-04 | 0 | 1 | 6585.3
IPID - Floor 4 | 2025-09-01 | 7018.65 | 2025-10-04 | 0 | 1 | 7018.65
IPID - Floor 4 | 2025-10-01 | 7479.45 | 2025-10-04 | 0 | 1 | 7479.45
IPID - Floor 4 | 2025-11-01 | 7552.8 | 2025-10-04 | 0.07666 | 0.99946 | 7548.7339
IPID - Floor 4 | 2025-12-01 | 7415.1 | 2025-10-04 | 0.1588 | 0.99889 | 7406.8332
IPID - Floor 4 | 2026-01-01 | 7573.5 | 2025-10-04 | 0.24367 | 0.99829 | 7560.5477
IPID - Floor 4 | 2026-02-01 | 6513.75 | 2025-10-04 | 0.32854 | 0.99769 | 6498.7344
IPID - Floor 4 | 2026-03-01 | 6841.35 | 2025-10-04 | 0.4052 | 0.99716 | 6821.9046
IPID - Floor 4 | 2026-04-01 | 6183 | 2025-10-04 | 0.49008 | 0.99656 | 6161.7511
IPID - Floor 4 | 2026-05-01 | 5924.7 | 2025-10-04 | 0.57221 | 0.99599 | 5900.9331
IPID - Floor 4 | 2026-06-01 | 5295.6 | 2025-10-04 | 0.65708 | 0.99539 | 5271.2131
IPID - Floor 4 | 2026-07-01 | 5785.2 | 2025-10-04 | 0.73922 | 0.99482 | 5755.2369
IPID - Floor 4 | 2026-08-01 | 6585.3 | 2025-10-04 | 0.82409 | 0.99423 | 6547.2882
IPID - Floor 4 | 2026-09-01 | 7018.65 | 2025-10-04 | 0.90897 | 0.99364 | 6973.9777
IPID - Floor 4 | 2026-10-01 | 7479.45 | 2025-10-04 | 0.9911 | 0.99306 | 7427.5581
IPID - Floor 4 | 2026-11-01 | 7552.8 | 2025-10-04 | 1.076 | 0.99247 | 7495.9288
IPID - Floor 4 | 2026-12-01 | 7415.1 | 2025-10-04 | 1.1581 | 0.9919 | 7355.0208
IPID - Floor 6 | 2024-01-01 | 7573.5 | 2025-10-04 | 0 | 1 | 7573.5
IPID - Floor 6 | 2024-02-01 | 6513.75 | 2025-10-04 | 0 | 1 | 6513.75
IPID - Floor 6 | 2024-03-01 | 6841.35 | 2025-10-04 | 0 | 1 | 6841.35
IPID - Floor 6 | 2024-04-01 | 618.3 | 2025-10-04 | 0 | 1 | 618.3
IPID - Floor 6 | 2024-05-01 | 5924.7 | 2025-10-04 | 0 | 1 | 5924.7
IPID - Floor 6 | 2024-06-01 | 5295.6 | 2025-10-04 | 0 | 1 | 5295.6
IPID - Floor 6 | 2024-07-01 | 5785.2 | 2025-10-04 | 0 | 1 | 5785.2
IPID - Floor 6 | 2024-08-01 | 6585.3 | 2025-10-04 | 0 | 1 | 6585.3
IPID - Floor 6 | 2024-09-01 | 7018.65 | 2025-10-04 | 0 | 1 | 7018.65
IPID - Floor 6 | 2024-10-01 | 7479.45 | 2025-10-04 | 0 | 1 | 7479.45
IPID - Floor 6 | 2024-11-01 | 7552.8 | 2025-10-04 | 0 | 1 | 7552.8
IPID - Floor 6 | 2024-12-01 | 7415.1 | 2025-10-04 | 0 | 1 | 7415.1
IPID - Floor 6 | 2025-01-01 | 7573.5 | 2025-10-04 | 0 | 1 | 7573.5
IPID - Floor 6 | 2025-02-01 | 6513.75 | 2025-10-04 | 0 | 1 | 6513.75
IPID - Floor 6 | 2025-03-01 | 6841.35 | 2025-10-04 | 0 | 1 | 6841.35
IPID - Floor 6 | 2025-04-01 | 618.3 | 2025-10-04 | 0 | 1 | 618.3
IPID - Floor 6 | 2025-05-01 | 5924.7 | 2025-10-04 | 0 | 1 | 5924.7
IPID - Floor 6 | 2025-06-01 | 5295.6 | 2025-10-04 | 0 | 1 | 5295.6
IPID - Floor 6 | 2025-07-01 | 5785.2 | 2025-10-04 | 0 | 1 | 5785.2
IPID - Floor 6 | 2025-08-01 | 6585.3 | 2025-10-04 | 0 | 1 | 6585.3
IPID - Floor 6 | 2025-09-01 | 7018.65 | 2025-10-04 | 0 | 1 | 7018.65
IPID - Floor 6 | 2025-10-01 | 7479.45 | 2025-10-04 | 0 | 1 | 7479.45
IPID - Floor 6 | 2025-11-01 | 7552.8 | 2025-10-04 | 0.07666 | 0.99946 | 7548.7339
IPID - Floor 6 | 2025-12-01 | 7415.1 | 2025-10-04 | 0.1588 | 0.99889 | 7406.8332
IPID - Floor 6 | 2026-01-01 | 7573.5 | 2025-10-04 | 0.24367 | 0.99829 | 7560.5477
IPID - Floor 6 | 2026-02-01 | 6513.75 | 2025-10-04 | 0.32854 | 0.99769 | 6498.7344
IPID - Floor 6 | 2026-03-01 | 6841.35 | 2025-10-04 | 0.4052 | 0.99716 | 6821.9046
IPID - Floor 6 | 2026-04-01 | 6183 | 2025-10-04 | 0.49008 | 0.99656 | 6161.7511
IPID - Floor 6 | 2026-05-01 | 5924.7 | 2025-10-04 | 0.57221 | 0.99599 | 5900.9331
IPID - Floor 6 | 2026-06-01 | 5295.6 | 2025-10-04 | 0.65708 | 0.99539 | 5271.2131
IPID - Floor 6 | 2026-07-01 | 5785.2 | 2025-10-04 | 0.73922 | 0.99482 | 5755.2369
IPID - Floor 6 | 2026-08-01 | 6585.3 | 2025-10-04 | 0.82409 | 0.99423 | 6547.2882
IPID - Floor 6 | 2026-09-01 | 7018.65 | 2025-10-04 | 0.90897 | 0.99364 | 6973.9777
IPID - Floor 6 | 2026-10-01 | 7479.45 | 2025-10-04 | 0.9911 | 0.99306 | 7427.5581
IPID - Floor 6 | 2026-11-01 | 7552.8 | 2025-10-04 | 1.076 | 0.99247 | 7495.9288
IPID - Floor 6 | 2026-12-01 | 7415.1 | 2025-10-04 | 1.1581 | 0.9919 | 7355.0208
Kool Village | 2024-01-01 | 12213 | 2022/16/12 |  | 1 | 12213
Kool Village | 2024-02-01 | 10570.5 | 2022/16/12 |  | 1 | 10570.5
Kool Village | 2024-03-01 | 10619.1 | 2022/16/12 |  | 1 | 10619.1
Kool Village | 2024-04-01 | 9139.5 | 2022/16/12 |  | 1 | 9139.5
Kool Village | 2024-05-01 | 8593.2 | 2022/16/12 |  | 1 | 8593.2
Kool Village | 2024-06-01 | 7680.6 | 2022/16/12 |  | 1 | 7680.6
Kool Village | 2024-07-01 | 8550.9 | 2022/16/12 |  | 1 | 8550.9
Kool Village | 2024-08-01 | 9997.2 | 2022/16/12 |  | 1 | 9997.2
Kool Village | 2024-09-01 | 10701.9 | 2022/16/12 |  | 1 | 10701.9
Kool Village | 2024-10-01 | 11834.1 | 2022/16/12 |  | 1 | 11834.1
Kool Village | 2024-11-01 | 12129.3 | 2022/16/12 |  | 1 | 12129.3
Kool Village | 2024-12-01 | 12998.7 | 2022/16/12 |  | 1 | 12998.7
Kool Village | 2025-01-01 | 12213 | 2022/16/12 |  | 1 | 12213
Kool Village | 2025-02-01 | 10570.5 | 2022/16/12 |  | 1 | 10570.5
Kool Village | 2025-03-01 | 10619.1 | 2022/16/12 |  | 1 | 10619.1
Kool Village | 2025-04-01 | 9139.5 | 2022/16/12 |  | 1 | 9139.5
Kool Village | 2025-05-01 | 8593.2 | 2022/16/12 |  | 1 | 8593.2
Kool Village | 2025-06-01 | 7680.6 | 2022/16/12 |  | 1 | 7680.6
Kool Village | 2025-07-01 | 8550.9 | 2022/16/12 |  | 1 | 8550.9
Kool Village | 2025-08-01 | 9997.2 | 2022/16/12 |  | 1 | 9997.2
Kool Village | 2025-09-01 | 10701.9 | 2022/16/12 |  | 1 | 10701.9
Kool Village | 2025-10-01 | 11834.1 | 2022/16/12 |  | 1 | 11834.1
Kool Village | 2025-11-01 | 12129.3 | 2022/16/12 |  | 1 | 12129.3
Kool Village | 2025-12-01 | 12998.7 | 2022/16/12 |  | 1 | 12998.7
Kool Village | 2026-01-01 | 12213 | 2022/16/12 |  | 1 | 12213
Kool Village | 2026-02-01 | 10570.5 | 2022/16/12 |  | 1 | 10570.5
Kool Village | 2026-03-01 | 10619.1 | 2022/16/12 |  | 1 | 10619.1
Kool Village | 2026-04-01 | 9139.5 | 2022/16/12 |  | 1 | 9139.5
Kool Village | 2026-05-01 | 8593.2 | 2022/16/12 |  | 1 | 8593.2
Kool Village | 2026-06-01 | 7680.6 | 2022/16/12 |  | 1 | 7680.6
Kool Village | 2026-07-01 | 8550.9 | 2022/16/12 |  | 1 | 8550.9
Kool Village | 2026-08-01 | 9997.2 | 2022/16/12 |  | 1 | 9997.2
Kool Village | 2026-09-01 | 10701.9 | 2022/16/12 |  | 1 | 10701.9
Kool Village | 2026-10-01 | 11834.1 | 2022/16/12 |  | 1 | 11834.1
Kool Village | 2026-11-01 | 12129.3 | 2022/16/12 |  | 1 | 12129.3
Kool Village | 2026-12-01 | 12998.7 | 2022/16/12 |  | 1 | 12998.7
Makalali | 2024-01-01 | 16602.9395 | 2023-05-04 | 0.66256 | 0.99536 | 16525.8451
Makalali | 2024-02-01 | 14966.051 | 2023-05-04 | 0.74743 | 0.99476 | 14887.6787
Makalali | 2024-03-01 | 16335.4855 | 2023-05-04 | 0.82683 | 0.99421 | 16240.8813
Makalali | 2024-04-01 | 15100.3508 | 2023-05-04 | 0.9117 | 0.99362 | 15003.9515
Makalali | 2024-05-01 | 15271.0454 | 2023-05-04 | 0.99384 | 0.99304 | 15164.8043
Makalali | 2024-06-01 | 14168.0073 | 2023-05-04 | 1.0787 | 0.99245 | 14061.0544
Makalali | 2024-07-01 | 15171.29 | 2023-05-04 | 1.1608 | 0.99188 | 15048.0785
Makalali | 2024-08-01 | 16365.4474 | 2023-05-04 | 1.2457 | 0.99129 | 16222.8628
Makalali | 2024-09-01 | 16283.9335 | 2023-05-04 | 1.3306 | 0.9907 | 16132.4379
Makalali | 2024-10-01 | 15891.0803 | 2023-05-04 | 1.4127 | 0.99013 | 15734.1588
Makalali | 2024-11-01 | 15343.2183 | 2023-05-04 | 1.4976 | 0.98954 | 15182.6523
Makalali | 2024-12-01 | 16261.6383 | 2023-05-04 | 1.5797 | 0.98896 | 16082.1794
Makalali | 2025-01-01 | 16602.9395 | 2023-05-04 | 1.6646 | 0.98837 | 16409.9275
Makalali | 2025-02-01 | 14966.051 | 2023-05-04 | 1.7495 | 0.98779 | 14783.2517
Makalali | 2025-03-01 | 16335.4855 | 2023-05-04 | 1.8261 | 0.98725 | 16127.2727
Makalali | 2025-04-01 | 15100.3508 | 2023-05-04 | 1.911 | 0.98667 | 14898.9955
Makalali | 2025-05-01 | 15271.0454 | 2023-05-04 | 1.9932 | 0.9861 | 15058.7231
Makalali | 2025-06-01 | 14168.0073 | 2023-05-04 | 2.078 | 0.98551 | 13962.6941
Makalali | 2025-07-01 | 15171.29 | 2023-05-04 | 2.1602 | 0.98494 | 14942.8138
Makalali | 2025-08-01 | 16365.4474 | 2023-05-04 | 2.245 | 0.98435 | 16109.3802
Makalali | 2025-09-01 | 16283.9335 | 2023-05-04 | 2.3299 | 0.98377 | 16019.5879
Makalali | 2025-10-01 | 15891.0803 | 2023-05-04 | 2.412 | 0.9832 | 15624.0948
Makalali | 2025-11-01 | 15343.2183 | 2023-05-04 | 2.4969 | 0.98261 | 15076.4462
Makalali | 2025-12-01 | 16261.6383 | 2023-05-04 | 2.5791 | 0.98205 | 15969.681
Makalali | 2026-01-01 | 16602.9395 | 2023-05-04 | 2.6639 | 0.98146 | 16295.1364
Makalali | 2026-02-01 | 14966.051 | 2023-05-04 | 2.7488 | 0.98088 | 14679.8396
Makalali | 2026-03-01 | 16335.4855 | 2023-05-04 | 2.8255 | 0.98035 | 16014.4588
Makalali | 2026-04-01 | 15100.3508 | 2023-05-04 | 2.9103 | 0.97976 | 14794.7737
Makalali | 2026-05-01 | 15271.0454 | 2023-05-04 | 2.9925 | 0.9792 | 14953.3839
Makalali | 2026-06-01 | 14168.0073 | 2023-05-04 | 3.0773 | 0.97861 | 13865.0219
Makalali | 2026-07-01 | 15171.29 | 2023-05-04 | 3.1595 | 0.97805 | 14838.2854
Makalali | 2026-08-01 | 16365.4474 | 2023-05-04 | 3.2444 | 0.97747 | 15996.6915
Makalali | 2026-09-01 | 16283.9335 | 2023-05-04 | 3.3292 | 0.97688 | 15907.5273
Makalali | 2026-10-01 | 15891.0803 | 2023-05-04 | 3.4114 | 0.97632 | 15514.8008
Makalali | 2026-11-01 | 15343.2183 | 2023-05-04 | 3.4962 | 0.97574 | 14970.9831
Makalali | 2026-12-01 | 16261.6383 | 2023-05-04 | 3.5784 | 0.97518 | 15857.9694
Mambha Cash & Carry | 2024-01-01 | 22241.7 | 2022-11-14 | 1.1307 | 0.99209 | 22065.7348
Mambha Cash & Carry | 2024-02-01 | 19450.8 | 2022-11-14 | 1.2156 | 0.9915 | 19285.4136
Mambha Cash & Carry | 2024-03-01 | 19575 | 2022-11-14 | 1.295 | 0.99094 | 19397.7357
Mambha Cash & Carry | 2024-04-01 | 15792.3 | 2022-11-14 | 1.3799 | 0.99035 | 15639.9631
Mambha Cash & Carry | 2024-05-01 | 13477.5 | 2022-11-14 | 1.462 | 0.98978 | 13339.7934
Mambha Cash & Carry | 2024-06-01 | 12124.8 | 2022-11-14 | 1.5469 | 0.98919 | 11993.7618
Mambha Cash & Carry | 2024-07-01 | 13099.5 | 2022-11-14 | 1.629 | 0.98862 | 12950.4536
Mambha Cash & Carry | 2024-08-01 | 15450.3 | 2022-11-14 | 1.7139 | 0.98803 | 15265.4022
Mambha Cash & Carry | 2024-09-01 | 16583.4 | 2022-11-14 | 1.7988 | 0.98744 | 16375.1762
Mambha Cash & Carry | 2024-10-01 | 19432.8 | 2022-11-14 | 1.8809 | 0.98687 | 19177.7305
Mambha Cash & Carry | 2024-11-01 | 20010.6 | 2022-11-14 | 1.9658 | 0.98629 | 19736.1762
Mambha Cash & Carry | 2024-12-01 | 22485.6 | 2022-11-14 | 2.0479 | 0.98572 | 22164.4423
Mambha Cash & Carry | 2025-01-01 | 22241.7 | 2022-11-14 | 2.1328 | 0.98513 | 21910.9586
Mambha Cash & Carry | 2025-02-01 | 19450.8 | 2022-11-14 | 2.2177 | 0.98454 | 19150.1395
Mambha Cash & Carry | 2025-03-01 | 19575 | 2022-11-14 | 2.2943 | 0.98401 | 19262.0441
Mambha Cash & Carry | 2025-04-01 | 15792.3 | 2022-11-14 | 2.3792 | 0.98343 | 15530.558
Mambha Cash & Carry | 2025-05-01 | 13477.5 | 2022-11-14 | 2.4613 | 0.98286 | 13246.4786
Mambha Cash & Carry | 2025-06-01 | 12124.8 | 2022-11-14 | 2.5462 | 0.98227 | 11909.8627
Mambha Cash & Carry | 2025-07-01 | 13099.5 | 2022-11-14 | 2.6283 | 0.98171 | 12859.8623
Mambha Cash & Carry | 2025-08-01 | 15450.3 | 2022-11-14 | 2.7132 | 0.98112 | 15158.6172
Mambha Cash & Carry | 2025-09-01 | 16583.4 | 2022-11-14 | 2.7981 | 0.98054 | 16260.6282
Mambha Cash & Carry | 2025-10-01 | 19432.8 | 2022-11-14 | 2.8802 | 0.97997 | 19043.578
Mambha Cash & Carry | 2025-11-01 | 20010.6 | 2022-11-14 | 2.9651 | 0.97939 | 19598.1172
Mambha Cash & Carry | 2025-12-01 | 22485.6 | 2022-11-14 | 3.0472 | 0.97882 | 22009.3971
Mambha Cash & Carry | 2026-01-01 | 22241.7 | 2022-11-14 | 3.1321 | 0.97824 | 21757.6866
Mambha Cash & Carry | 2026-02-01 | 19450.8 | 2022-11-14 | 3.217 | 0.97766 | 19016.1799
Mambha Cash & Carry | 2026-03-01 | 19575 | 2022-11-14 | 3.2936 | 0.97713 | 19127.3018
Mambha Cash & Carry | 2026-04-01 | 15792.3 | 2022-11-14 | 3.3785 | 0.97655 | 15421.9183
Mambha Cash & Carry | 2026-05-01 | 13477.5 | 2022-11-14 | 3.4606 | 0.97598 | 13153.8165
Mambha Cash & Carry | 2026-06-01 | 12124.8 | 2022-11-14 | 3.5455 | 0.9754 | 11826.5506
Mambha Cash & Carry | 2026-07-01 | 13099.5 | 2022-11-14 | 3.6277 | 0.97484 | 12769.9046
Mambha Cash & Carry | 2026-08-01 | 15450.3 | 2022-11-14 | 3.7125 | 0.97426 | 15052.5793
Mambha Cash & Carry | 2026-09-01 | 16583.4 | 2022-11-14 | 3.7974 | 0.97368 | 16146.8814
Mambha Cash & Carry | 2026-10-01 | 19432.8 | 2022-11-14 | 3.8795 | 0.97312 | 18910.3638
Mambha Cash & Carry | 2026-11-01 | 20010.6 | 2022-11-14 | 3.9644 | 0.97254 | 19461.024
Mambha Cash & Carry | 2026-12-01 | 22485.6 | 2022-11-14 | 4.0465 | 0.97197 | 21855.4364
Mathe Group Company | 2024-01-01 | 61302.85 | 2022-05-11 | 1.6427 | 0.98853 | 60599.5172
Mathe Group Company | 2024-02-01 | 55639.3 | 2022-05-11 | 1.7276 | 0.98794 | 54968.1636
Mathe Group Company | 2024-03-01 | 58024.4 | 2022-05-11 | 1.807 | 0.98739 | 57292.5308
Mathe Group Company | 2024-04-01 | 48946.4 | 2022-05-11 | 1.8919 | 0.9868 | 48300.2274
Mathe Group Company | 2024-05-01 | 44310.5 | 2022-05-11 | 1.974 | 0.98623 | 43700.3079
Mathe Group Company | 2024-06-01 | 40933.45 | 2022-05-11 | 2.0589 | 0.98564 | 40345.7012
Mathe Group Company | 2024-07-01 | 43977.3 | 2022-05-11 | 2.141 | 0.98507 | 43320.8436
Mathe Group Company | 2024-08-01 | 48620.85 | 2022-05-11 | 2.2259 | 0.98449 | 47866.5319
Mathe Group Company | 2024-09-01 | 50331.05 | 2022-05-11 | 2.3107 | 0.9839 | 49520.6662
Mathe Group Company | 2024-10-01 | 55230.45 | 2022-05-11 | 2.3929 | 0.98333 | 54309.8364
Mathe Group Company | 2024-11-01 | 56583.65 | 2022-05-11 | 2.4778 | 0.98275 | 55607.3174
Mathe Group Company | 2024-12-01 | 61075.9 | 2022-05-11 | 2.5599 | 0.98218 | 59987.4341
Mathe Group Company | 2025-01-01 | 61302.85 | 2022-05-11 | 2.6448 | 0.98159 | 60174.4526
Mathe Group Company | 2025-02-01 | 55639.3 | 2022-05-11 | 2.7296 | 0.98101 | 54582.5992
Mathe Group Company | 2025-03-01 | 58024.4 | 2022-05-11 | 2.8063 | 0.98048 | 56891.7566
Mathe Group Company | 2025-04-01 | 48946.4 | 2022-05-11 | 2.8912 | 0.9799 | 47962.3565
Mathe Group Company | 2025-05-01 | 44310.5 | 2022-05-11 | 2.9733 | 0.97933 | 43394.6143
Mathe Group Company | 2025-06-01 | 40933.45 | 2022-05-11 | 3.0582 | 0.97875 | 40063.4739
Mathe Group Company | 2025-07-01 | 43977.3 | 2022-05-11 | 3.1403 | 0.97818 | 43017.8045
Mathe Group Company | 2025-08-01 | 48620.85 | 2022-05-11 | 3.2252 | 0.9776 | 47531.6947
Mathe Group Company | 2025-09-01 | 50331.05 | 2022-05-11 | 3.3101 | 0.97702 | 49174.258
Mathe Group Company | 2025-10-01 | 55230.45 | 2022-05-11 | 3.3922 | 0.97645 | 53929.9269
Mathe Group Company | 2025-11-01 | 56583.65 | 2022-05-11 | 3.4771 | 0.97587 | 55218.3316
Mathe Group Company | 2025-12-01 | 61075.9 | 2022-05-11 | 3.5592 | 0.97531 | 59567.8084
Mathe Group Company | 2026-01-01 | 61302.85 | 2022-05-11 | 3.6441 | 0.97473 | 59753.5187
Mathe Group Company | 2026-02-01 | 55639.3 | 2022-05-11 | 3.729 | 0.97415 | 54200.7816
Mathe Group Company | 2026-03-01 | 58024.4 | 2022-05-11 | 3.8056 | 0.97362 | 56493.7859
Mathe Group Company | 2026-04-01 | 48946.4 | 2022-05-11 | 3.8905 | 0.97304 | 47626.849
Mathe Group Company | 2026-05-01 | 44310.5 | 2022-05-11 | 3.9726 | 0.97248 | 43091.0592
Mathe Group Company | 2026-06-01 | 40933.45 | 2022-05-11 | 4.0575 | 0.9719 | 39783.2209
Mathe Group Company | 2026-07-01 | 43977.3 | 2022-05-11 | 4.1396 | 0.97134 | 42716.8853
Mathe Group Company | 2026-08-01 | 48620.85 | 2022-05-11 | 4.2245 | 0.97076 | 47199.1998
Mathe Group Company | 2026-09-01 | 50331.05 | 2022-05-11 | 4.3094 | 0.97018 | 48830.273
Mathe Group Company | 2026-10-01 | 55230.45 | 2022-05-11 | 4.3915 | 0.96962 | 53552.6749
Mathe Group Company | 2026-11-01 | 56583.65 | 2022-05-11 | 4.4764 | 0.96904 | 54832.0669
Mathe Group Company | 2026-12-01 | 61075.9 | 2022-05-11 | 4.5585 | 0.96849 | 59151.1182
Mdluli | 2024-01-01 | 15870.6 | 2024-04-17 | 0 | 1 | 15870.6
Mdluli | 2024-02-01 | 14825.7 | 2024-04-17 | 0 | 1 | 14825.7
Mdluli | 2024-03-01 | 17314.2 | 2024-04-17 | 0 | 1 | 17314.2
Mdluli | 2024-04-01 | 15358.5 | 2024-04-17 | 0 | 1 | 15358.5
Mdluli | 2024-05-01 | 15197.4 | 2024-04-17 | 0.03833 | 0.99973 | 15193.3086
Mdluli | 2024-06-01 | 14489.1 | 2024-04-17 | 0.1232 | 0.99913 | 14476.5658
Mdluli | 2024-07-01 | 15390.9 | 2024-04-17 | 0.20534 | 0.99856 | 15368.7158
Mdluli | 2024-08-01 | 15613.2 | 2024-04-17 | 0.29021 | 0.99796 | 15581.4029
Mdluli | 2024-09-01 | 15191.1 | 2024-04-17 | 0.37509 | 0.99737 | 15151.1267
Mdluli | 2024-10-01 | 14349.6 | 2024-04-17 | 0.45722 | 0.99679 | 14303.5859
Mdluli | 2024-11-01 | 13257.9 | 2024-04-17 | 0.54209 | 0.9962 | 13207.5099
Mdluli | 2024-12-01 | 13839.3 | 2024-04-17 | 0.62423 | 0.99562 | 13778.7479
Mdluli | 2025-01-01 | 15870.6 | 2024-04-17 | 0.7091 | 0.99503 | 15791.7423
Mdluli | 2025-02-01 | 14825.7 | 2024-04-17 | 0.79398 | 0.99444 | 14743.2416
Mdluli | 2025-03-01 | 17314.2 | 2024-04-17 | 0.87064 | 0.9939 | 17208.6315
Mdluli | 2025-04-01 | 15358.5 | 2024-04-17 | 0.95551 | 0.99331 | 15255.7576
Mdluli | 2025-05-01 | 15197.4 | 2024-04-17 | 1.0376 | 0.99274 | 15087.028
Mdluli | 2025-06-01 | 14489.1 | 2024-04-17 | 1.1225 | 0.99215 | 14375.2989
Mdluli | 2025-07-01 | 15390.9 | 2024-04-17 | 1.2047 | 0.99157 | 15261.2081
Mdluli | 2025-08-01 | 15613.2 | 2024-04-17 | 1.2895 | 0.99098 | 15472.4075
Mdluli | 2025-09-01 | 15191.1 | 2024-04-17 | 1.3744 | 0.99039 | 15045.1411
Mdluli | 2025-10-01 | 14349.6 | 2024-04-17 | 1.4565 | 0.98982 | 14203.529
Mdluli | 2025-11-01 | 13257.9 | 2024-04-17 | 1.5414 | 0.98923 | 13115.1203
Mdluli | 2025-12-01 | 13839.3 | 2024-04-17 | 1.6235 | 0.98866 | 13682.3624
Mdluli | 2026-01-01 | 15870.6 | 2024-04-17 | 1.7084 | 0.98807 | 15681.2755
Mdluli | 2026-02-01 | 14825.7 | 2024-04-17 | 1.7933 | 0.98748 | 14640.1093
Mdluli | 2026-03-01 | 17314.2 | 2024-04-17 | 1.87 | 0.98695 | 17088.2532
Mdluli | 2026-04-01 | 15358.5 | 2024-04-17 | 1.9548 | 0.98636 | 15149.0401
Mdluli | 2026-05-01 | 15197.4 | 2024-04-17 | 2.037 | 0.98579 | 14981.4908
Mdluli | 2026-06-01 | 14489.1 | 2024-04-17 | 2.1218 | 0.98521 | 14274.7405
Mdluli | 2026-07-01 | 15390.9 | 2024-04-17 | 2.204 | 0.98464 | 15154.4525
Mdluli | 2026-08-01 | 15613.2 | 2024-04-17 | 2.2888 | 0.98405 | 15364.1745
Mdluli | 2026-09-01 | 15191.1 | 2024-04-17 | 2.3737 | 0.98346 | 14939.897
Mdluli | 2026-10-01 | 14349.6 | 2024-04-17 | 2.4559 | 0.9829 | 14104.1722
Mdluli | 2026-11-01 | 13257.9 | 2024-04-17 | 2.5407 | 0.98231 | 13023.3771
Mdluli | 2026-12-01 | 13839.3 | 2024-04-17 | 2.6229 | 0.98174 | 13586.6512
Medipost | 2024-01-01 | 53361.9 | 2025-02-25 | 0 | 1 | 53361.9
Medipost | 2024-02-01 | 43750.8 | 2025-02-25 | 0 | 1 | 43750.8
Medipost | 2024-03-01 | 40931.1 | 2025-02-25 | 0 | 1 | 40931.1
Medipost | 2024-04-01 | 29080.8 | 2025-02-25 | 0 | 1 | 29080.8
Medipost | 2024-05-01 | 21434.4 | 2025-02-25 | 0 | 1 | 21434.4
Medipost | 2024-06-01 | 17483.4 | 2025-02-25 | 0 | 1 | 17483.4
Medipost | 2024-07-01 | 19783.8 | 2025-02-25 | 0 | 1 | 19783.8
Medipost | 2024-08-01 | 25524 | 2025-02-25 | 0 | 1 | 25524
Medipost | 2024-09-01 | 33381.9 | 2025-02-25 | 0 | 1 | 33381.9
Medipost | 2024-10-01 | 43038 | 2025-02-25 | 0 | 1 | 43038
Medipost | 2024-11-01 | 49565.7 | 2025-02-25 | 0 | 1 | 49565.7
Medipost | 2024-12-01 | 54135.9 | 2025-02-25 | 0 | 1 | 54135.9
Medipost | 2025-01-01 | 53361.9 | 2025-02-25 | 0 | 1 | 53361.9
Medipost | 2025-02-01 | 43750.8 | 2025-02-25 | 0 | 1 | 43750.8
Medipost | 2025-03-01 | 40931.1 | 2025-02-25 | 0.010951 | 0.99992 | 40927.9513
Medipost | 2025-04-01 | 29080.8 | 2025-02-25 | 0.095825 | 0.99933 | 29061.2314
Medipost | 2025-05-01 | 21434.4 | 2025-02-25 | 0.17796 | 0.99875 | 21407.6215
Medipost | 2025-06-01 | 17483.4 | 2025-02-25 | 0.26283 | 0.99816 | 17451.1501
Medipost | 2025-07-01 | 19783.8 | 2025-02-25 | 0.34497 | 0.99758 | 19735.9164
Medipost | 2025-08-01 | 25524 | 2025-02-25 | 0.42984 | 0.99699 | 25447.0471
Medipost | 2025-09-01 | 33381.9 | 2025-02-25 | 0.51472 | 0.99639 | 33261.4196
Medipost | 2025-10-01 | 43038 | 2025-02-25 | 0.59685 | 0.99582 | 42857.9344
Medipost | 2025-11-01 | 49565.7 | 2025-02-25 | 0.68172 | 0.99522 | 49328.9045
Medipost | 2025-12-01 | 54135.9 | 2025-02-25 | 0.76386 | 0.99465 | 53846.1942
Medipost | 2026-01-01 | 53361.9 | 2025-02-25 | 0.84873 | 0.99406 | 53044.7014
Medipost | 2026-02-01 | 43750.8 | 2025-02-25 | 0.93361 | 0.99346 | 43464.811
Medipost | 2026-03-01 | 40931.1 | 2025-02-25 | 1.0103 | 0.99293 | 40641.6511
Medipost | 2026-04-01 | 29080.8 | 2025-02-25 | 1.0951 | 0.99234 | 28857.9415
Medipost | 2026-05-01 | 21434.4 | 2025-02-25 | 1.1773 | 0.99176 | 21257.8704
Medipost | 2026-06-01 | 17483.4 | 2025-02-25 | 1.2621 | 0.99117 | 17329.0754
Medipost | 2026-07-01 | 19783.8 | 2025-02-25 | 1.3443 | 0.9906 | 19597.8593
Medipost | 2026-08-01 | 25524 | 2025-02-25 | 1.4292 | 0.99001 | 25269.0392
Medipost | 2026-09-01 | 33381.9 | 2025-02-25 | 1.514 | 0.98942 | 33028.7485
Medipost | 2026-10-01 | 43038 | 2025-02-25 | 1.5962 | 0.98885 | 42558.1335
Medipost | 2026-11-01 | 49565.7 | 2025-02-25 | 1.681 | 0.98826 | 48983.8377
Medipost | 2026-12-01 | 54135.9 | 2025-02-25 | 1.7632 | 0.98769 | 53469.5279
Meredale Heights | 2024-01-01 | 5063.45 | 2023-11-18 | 0.12047 | 0.99915 | 5059.167
Meredale Heights | 2024-02-01 | 4598.5 | 2023-11-18 | 0.20534 | 0.99856 | 4591.8718
Meredale Heights | 2024-03-01 | 5071.95 | 2023-11-18 | 0.28474 | 0.998 | 5061.8154
Meredale Heights | 2024-04-01 | 4864.55 | 2023-11-18 | 0.36961 | 0.99741 | 4851.9362
Meredale Heights | 2024-05-01 | 5173.1 | 2023-11-18 | 0.45175 | 0.99683 | 5156.71
Meredale Heights | 2024-06-01 | 5002.25 | 2023-11-18 | 0.53662 | 0.99624 | 4983.4293
Meredale Heights | 2024-07-01 | 5383.9 | 2023-11-18 | 0.61875 | 0.99566 | 5360.5496
Meredale Heights | 2024-08-01 | 5638.05 | 2023-11-18 | 0.70363 | 0.99507 | 5610.2515
Meredale Heights | 2024-09-01 | 5587.05 | 2023-11-18 | 0.7885 | 0.99448 | 5556.1893
Meredale Heights | 2024-10-01 | 5491.85 | 2023-11-18 | 0.87064 | 0.9939 | 5458.365
Meredale Heights | 2024-11-01 | 5110.2 | 2023-11-18 | 0.95551 | 0.99331 | 5076.0147
Meredale Heights | 2024-12-01 | 5223.25 | 2023-11-18 | 1.0376 | 0.99274 | 5185.3158
Meredale Heights | 2025-01-01 | 5063.45 | 2023-11-18 | 1.1225 | 0.99215 | 5023.6804
Meredale Heights | 2025-02-01 | 4598.5 | 2023-11-18 | 1.2074 | 0.99155 | 4559.6629
Meredale Heights | 2025-03-01 | 5071.95 | 2023-11-18 | 1.2841 | 0.99102 | 5026.4069
Meredale Heights | 2025-04-01 | 4864.55 | 2023-11-18 | 1.3689 | 0.99043 | 4817.9958
Meredale Heights | 2025-05-01 | 5173.1 | 2023-11-18 | 1.4511 | 0.98986 | 5120.6377
Meredale Heights | 2025-06-01 | 5002.25 | 2023-11-18 | 1.5359 | 0.98927 | 4948.5691
Meredale Heights | 2025-07-01 | 5383.9 | 2023-11-18 | 1.6181 | 0.9887 | 5323.0514
Meredale Heights | 2025-08-01 | 5638.05 | 2023-11-18 | 1.7029 | 0.98811 | 5571.0065
Meredale Heights | 2025-09-01 | 5587.05 | 2023-11-18 | 1.7878 | 0.98752 | 5517.3225
Meredale Heights | 2025-10-01 | 5491.85 | 2023-11-18 | 1.87 | 0.98695 | 5420.1825
Meredale Heights | 2025-11-01 | 5110.2 | 2023-11-18 | 1.9548 | 0.98636 | 5040.5069
Meredale Heights | 2025-12-01 | 5223.25 | 2023-11-18 | 2.037 | 0.98579 | 5149.0434
Meredale Heights | 2026-01-01 | 5063.45 | 2023-11-18 | 2.1218 | 0.98521 | 4988.5386
Meredale Heights | 2026-02-01 | 4598.5 | 2023-11-18 | 2.2067 | 0.98462 | 4527.767
Meredale Heights | 2026-03-01 | 5071.95 | 2023-11-18 | 2.2834 | 0.98409 | 4991.246
Meredale Heights | 2026-04-01 | 4864.55 | 2023-11-18 | 2.3682 | 0.9835 | 4784.2929
Meredale Heights | 2026-05-01 | 5173.1 | 2023-11-18 | 2.4504 | 0.98293 | 5084.8177
Meredale Heights | 2026-06-01 | 5002.25 | 2023-11-18 | 2.5352 | 0.98235 | 4913.9527
Meredale Heights | 2026-07-01 | 5383.9 | 2023-11-18 | 2.6174 | 0.98178 | 5285.8154
Meredale Heights | 2026-08-01 | 5638.05 | 2023-11-18 | 2.7023 | 0.9812 | 5532.0361
Meredale Heights | 2026-09-01 | 5587.05 | 2023-11-18 | 2.7871 | 0.98061 | 5478.7276
Meredale Heights | 2026-10-01 | 5491.85 | 2023-11-18 | 2.8693 | 0.98005 | 5382.2671
Meredale Heights | 2026-11-01 | 5110.2 | 2023-11-18 | 2.9541 | 0.97946 | 5005.2474
Meredale Heights | 2026-12-01 | 5223.25 | 2023-11-18 | 3.0363 | 0.9789 | 5113.0247
Monument Park Checkers | 2024-01-01 | 40416.3 | 2024-02-29 | 0 | 1 | 40416.3
Monument Park Checkers | 2024-02-01 | 33988.5 | 2024-02-29 | 0 | 1 | 33988.5
Monument Park Checkers | 2024-03-01 | 35132.4 | 2024-02-29 | 0.0027379 | 0.99998 | 35131.7243
Monument Park Checkers | 2024-04-01 | 29903.4 | 2024-02-29 | 0.087611 | 0.99938 | 29885.0021
Monument Park Checkers | 2024-05-01 | 28383.3 | 2024-02-29 | 0.16975 | 0.99881 | 28349.4758
Monument Park Checkers | 2024-06-01 | 25641.9 | 2024-02-29 | 0.25462 | 0.99821 | 25596.0777
Monument Park Checkers | 2024-07-01 | 28361.7 | 2024-02-29 | 0.33676 | 0.99764 | 28294.6875
Monument Park Checkers | 2024-08-01 | 33006.6 | 2024-02-29 | 0.42163 | 0.99704 | 32908.9863
Monument Park Checkers | 2024-09-01 | 36521.1 | 2024-02-29 | 0.5065 | 0.99645 | 36391.3894
Monument Park Checkers | 2024-10-01 | 39682.8 | 2024-02-29 | 0.58864 | 0.99587 | 39519.0522
Monument Park Checkers | 2024-11-01 | 39748.5 | 2024-02-29 | 0.67351 | 0.99528 | 39560.8877
Monument Park Checkers | 2024-12-01 | 42519.6 | 2024-02-29 | 0.75565 | 0.99471 | 42294.4985
Monument Park Checkers | 2025-01-01 | 40416.3 | 2024-02-29 | 0.84052 | 0.99411 | 40178.3719
Monument Park Checkers | 2025-02-01 | 33988.5 | 2024-02-29 | 0.92539 | 0.99352 | 33768.2732
Monument Park Checkers | 2025-03-01 | 35132.4 | 2024-02-29 | 1.0021 | 0.99299 | 34885.97
Monument Park Checkers | 2025-04-01 | 29903.4 | 2024-02-29 | 1.0869 | 0.99239 | 29675.9497
Monument Park Checkers | 2025-05-01 | 28383.3 | 2024-02-29 | 1.1691 | 0.99182 | 28151.1648
Monument Park Checkers | 2025-06-01 | 25641.9 | 2024-02-29 | 1.2539 | 0.99123 | 25417.0273
Monument Park Checkers | 2025-07-01 | 28361.7 | 2024-02-29 | 1.3361 | 0.99066 | 28096.7597
Monument Park Checkers | 2025-08-01 | 33006.6 | 2024-02-29 | 1.4209 | 0.99007 | 32678.7805
Monument Park Checkers | 2025-09-01 | 36521.1 | 2024-02-29 | 1.5058 | 0.98948 | 36136.8234
Monument Park Checkers | 2025-10-01 | 39682.8 | 2024-02-29 | 1.588 | 0.98891 | 39242.6075
Monument Park Checkers | 2025-11-01 | 39748.5 | 2024-02-29 | 1.6728 | 0.98832 | 39284.1504
Monument Park Checkers | 2025-12-01 | 42519.6 | 2024-02-29 | 1.755 | 0.98775 | 41998.6389
Monument Park Checkers | 2026-01-01 | 40416.3 | 2024-02-29 | 1.8398 | 0.98716 | 39897.3151
Monument Park Checkers | 2026-02-01 | 33988.5 | 2024-02-29 | 1.9247 | 0.98657 | 33532.0565
Monument Park Checkers | 2026-03-01 | 35132.4 | 2024-02-29 | 2.0014 | 0.98604 | 34641.9348
Monument Park Checkers | 2026-04-01 | 29903.4 | 2024-02-29 | 2.0862 | 0.98545 | 29468.3598
Monument Park Checkers | 2026-05-01 | 28383.3 | 2024-02-29 | 2.1684 | 0.98488 | 27954.241
Monument Park Checkers | 2026-06-01 | 25641.9 | 2024-02-29 | 2.2533 | 0.9843 | 25239.2295
Monument Park Checkers | 2026-07-01 | 28361.7 | 2024-02-29 | 2.3354 | 0.98373 | 27900.2166
Monument Park Checkers | 2026-08-01 | 33006.6 | 2024-02-29 | 2.4203 | 0.98314 | 32450.1851
Monument Park Checkers | 2026-09-01 | 36521.1 | 2024-02-29 | 2.5051 | 0.98256 | 35884.0382
Monument Park Checkers | 2026-10-01 | 39682.8 | 2024-02-29 | 2.5873 | 0.98199 | 38968.0966
Monument Park Checkers | 2026-11-01 | 39748.5 | 2024-02-29 | 2.6721 | 0.9814 | 39009.3489
Monument Park Checkers | 2026-12-01 | 42519.6 | 2024-02-29 | 2.7543 | 0.98084 | 41704.849
Nkambeni Industrial | 2024-01-01 | 23544 | 2023-09-13 | 0.30116 | 0.99789 | 23494.2439
Nkambeni Industrial | 2024-02-01 | 21677 | 2023-09-13 | 0.38604 | 0.99729 | 21618.2968
Nkambeni Industrial | 2024-03-01 | 24212 | 2023-09-13 | 0.46543 | 0.99674 | 24132.9682
Nkambeni Industrial | 2024-04-01 | 20861 | 2023-09-13 | 0.55031 | 0.99614 | 20780.5133
Nkambeni Industrial | 2024-05-01 | 20012 | 2023-09-13 | 0.63244 | 0.99557 | 19923.2904
Nkambeni Industrial | 2024-06-01 | 18485 | 2023-09-13 | 0.71732 | 0.99497 | 18392.0907
Nkambeni Industrial | 2024-07-01 | 20016 | 2023-09-13 | 0.79945 | 0.9944 | 19903.9083
Nkambeni Industrial | 2024-08-01 | 21052 | 2023-09-13 | 0.88433 | 0.99381 | 20921.6293
Nkambeni Industrial | 2024-09-01 | 21403 | 2023-09-13 | 0.9692 | 0.99321 | 21257.7779
Nkambeni Industrial | 2024-10-01 | 20962 | 2023-09-13 | 1.0513 | 0.99264 | 20807.7612
Nkambeni Industrial | 2024-11-01 | 19856 | 2023-09-13 | 1.1362 | 0.99205 | 19698.1516
Nkambeni Industrial | 2024-12-01 | 21184 | 2023-09-13 | 1.2183 | 0.99148 | 21003.4726
Nkambeni Industrial | 2025-01-01 | 23544 | 2023-09-13 | 1.3032 | 0.99089 | 23329.4477
Nkambeni Industrial | 2025-02-01 | 21677 | 2023-09-13 | 1.3881 | 0.9903 | 21466.6591
Nkambeni Industrial | 2025-03-01 | 24212 | 2023-09-13 | 1.4648 | 0.98976 | 23964.1526
Nkambeni Industrial | 2025-04-01 | 20861 | 2023-09-13 | 1.5496 | 0.98917 | 20635.1489
Nkambeni Industrial | 2025-05-01 | 20012 | 2023-09-13 | 1.6318 | 0.9886 | 19783.9225
Nkambeni Industrial | 2025-06-01 | 18485 | 2023-09-13 | 1.7166 | 0.98801 | 18263.4338
Nkambeni Industrial | 2025-07-01 | 20016 | 2023-09-13 | 1.7988 | 0.98744 | 19764.6759
Nkambeni Industrial | 2025-08-01 | 21052 | 2023-09-13 | 1.8836 | 0.98686 | 20775.2778
Nkambeni Industrial | 2025-09-01 | 21403 | 2023-09-13 | 1.9685 | 0.98627 | 21109.075
Nkambeni Industrial | 2025-10-01 | 20962 | 2023-09-13 | 2.0507 | 0.9857 | 20662.2062
Nkambeni Industrial | 2025-11-01 | 19856 | 2023-09-13 | 2.1355 | 0.98511 | 19560.3586
Nkambeni Industrial | 2025-12-01 | 21184 | 2023-09-13 | 2.2177 | 0.98454 | 20856.5486
Nkambeni Industrial | 2026-01-01 | 23544 | 2023-09-13 | 2.3025 | 0.98396 | 23166.253
Nkambeni Industrial | 2026-02-01 | 21677 | 2023-09-13 | 2.3874 | 0.98337 | 21316.4949
Nkambeni Industrial | 2026-03-01 | 24212 | 2023-09-13 | 2.4641 | 0.98284 | 23796.5179
Nkambeni Industrial | 2026-04-01 | 20861 | 2023-09-13 | 2.5489 | 0.98225 | 20490.8014
Nkambeni Industrial | 2026-05-01 | 20012 | 2023-09-13 | 2.6311 | 0.98169 | 19645.5295
Nkambeni Industrial | 2026-06-01 | 18485 | 2023-09-13 | 2.7159 | 0.9811 | 18135.677
Nkambeni Industrial | 2026-07-01 | 20016 | 2023-09-13 | 2.7981 | 0.98054 | 19626.4176
Nkambeni Industrial | 2026-08-01 | 21052 | 2023-09-13 | 2.883 | 0.97995 | 20629.95
Nkambeni Industrial | 2026-09-01 | 21403 | 2023-09-13 | 2.9678 | 0.97937 | 20961.4122
Nkambeni Industrial | 2026-10-01 | 20962 | 2023-09-13 | 3.05 | 0.9788 | 20517.6695
Nkambeni Industrial | 2026-11-01 | 19856 | 2023-09-13 | 3.1348 | 0.97822 | 19423.5295
Nkambeni Industrial | 2026-12-01 | 21184 | 2023-09-13 | 3.217 | 0.97766 | 20710.6523
Olievenhoutbosch 1 | 2024-01-01 | 46872 | 2025-09-24 | 0 | 1 | 46872
Olievenhoutbosch 1 | 2024-02-01 | 40989.6 | 2025-09-24 | 0 | 1 | 40989.6
Olievenhoutbosch 1 | 2024-03-01 | 39989.7 | 2025-09-24 | 0 | 1 | 39989.7
Olievenhoutbosch 1 | 2024-04-01 | 34783.2 | 2025-09-24 | 0 | 1 | 34783.2
Olievenhoutbosch 1 | 2024-05-01 | 32139 | 2025-09-24 | 0 | 1 | 32139
Olievenhoutbosch 1 | 2024-06-01 | 28357.2 | 2025-09-24 | 0 | 1 | 28357.2
Olievenhoutbosch 1 | 2024-07-01 | 31229.1 | 2025-09-24 | 0 | 1 | 31229.1
Olievenhoutbosch 1 | 2024-08-01 | 36815.4 | 2025-09-24 | 0 | 1 | 36815.4
Olievenhoutbosch 1 | 2024-09-01 | 40778.1 | 2025-09-24 | 0 | 1 | 40778.1
Olievenhoutbosch 1 | 2024-10-01 | 46212.3 | 2025-09-24 | 0 | 1 | 46212.3
Olievenhoutbosch 1 | 2024-11-01 | 46653.3 | 2025-09-24 | 0 | 1 | 46653.3
Olievenhoutbosch 1 | 2024-12-01 | 47656.8 | 2025-09-24 | 0 | 1 | 47656.8
Olievenhoutbosch 1 | 2025-01-01 | 46872 | 2025-09-24 | 0 | 1 | 46872
Olievenhoutbosch 1 | 2025-02-01 | 40989.6 | 2025-09-24 | 0 | 1 | 40989.6
Olievenhoutbosch 1 | 2025-03-01 | 39989.7 | 2025-09-24 | 0 | 1 | 39989.7
Olievenhoutbosch 1 | 2025-04-01 | 34783.2 | 2025-09-24 | 0 | 1 | 34783.2
Olievenhoutbosch 1 | 2025-05-01 | 32139 | 2025-09-24 | 0 | 1 | 32139
Olievenhoutbosch 1 | 2025-06-01 | 28357.2 | 2025-09-24 | 0 | 1 | 28357.2
Olievenhoutbosch 1 | 2025-07-01 | 31229.1 | 2025-09-24 | 0 | 1 | 31229.1
Olievenhoutbosch 1 | 2025-08-01 | 36815.4 | 2025-09-24 | 0 | 1 | 36815.4
Olievenhoutbosch 1 | 2025-09-01 | 40778.1 | 2025-09-24 | 0 | 1 | 40778.1
Olievenhoutbosch 1 | 2025-10-01 | 46212.3 | 2025-09-24 | 0.019165 | 0.99987 | 46206.079
Olievenhoutbosch 1 | 2025-11-01 | 46653.3 | 2025-09-24 | 0.10404 | 0.99927 | 46619.2169
Olievenhoutbosch 1 | 2025-12-01 | 47656.8 | 2025-09-24 | 0.18617 | 0.99869 | 47594.5152
Olievenhoutbosch 1 | 2026-01-01 | 46872 | 2025-09-24 | 0.27105 | 0.9981 | 46782.8405
Olievenhoutbosch 1 | 2026-02-01 | 40989.6 | 2025-09-24 | 0.35592 | 0.9975 | 40887.2456
Olievenhoutbosch 1 | 2026-03-01 | 39989.7 | 2025-09-24 | 0.43258 | 0.99697 | 39868.3673
Olievenhoutbosch 1 | 2026-04-01 | 34783.2 | 2025-09-24 | 0.51745 | 0.99637 | 34656.9956
Olievenhoutbosch 1 | 2026-05-01 | 32139 | 2025-09-24 | 0.59959 | 0.9958 | 32003.9189
Olievenhoutbosch 1 | 2026-06-01 | 28357.2 | 2025-09-24 | 0.68446 | 0.9952 | 28221.1834
Olievenhoutbosch 1 | 2026-07-01 | 31229.1 | 2025-09-24 | 0.7666 | 0.99463 | 31061.3815
Olievenhoutbosch 1 | 2026-08-01 | 36815.4 | 2025-09-24 | 0.85147 | 0.99404 | 36595.8548
Olievenhoutbosch 1 | 2026-09-01 | 40778.1 | 2025-09-24 | 0.93634 | 0.99344 | 40510.7637
Olievenhoutbosch 1 | 2026-10-01 | 46212.3 | 2025-09-24 | 1.0185 | 0.99287 | 45882.8571
Olievenhoutbosch 1 | 2026-11-01 | 46653.3 | 2025-09-24 | 1.1034 | 0.99228 | 46293.1049
Olievenhoutbosch 1 | 2026-12-01 | 47656.8 | 2025-09-24 | 1.1855 | 0.99171 | 47261.5808
Olievenhoutbosch 2 | 2024-01-01 | 12369.6 | 2025-09-24 | 0 | 1 | 12369.6
Olievenhoutbosch 2 | 2024-02-01 | 10801.8 | 2025-09-24 | 0 | 1 | 10801.8
Olievenhoutbosch 2 | 2024-03-01 | 10537.2 | 2025-09-24 | 0 | 1 | 10537.2
Olievenhoutbosch 2 | 2024-04-01 | 9173.7 | 2025-09-24 | 0 | 1 | 9173.7
Olievenhoutbosch 2 | 2024-05-01 | 8503.2 | 2025-09-24 | 0 | 1 | 8503.2
Olievenhoutbosch 2 | 2024-06-01 | 7545.6 | 2025-09-24 | 0 | 1 | 7545.6
Olievenhoutbosch 2 | 2024-07-01 | 8307 | 2025-09-24 | 0 | 1 | 8307
Olievenhoutbosch 2 | 2024-08-01 | 9720.9 | 2025-09-24 | 0 | 1 | 9720.9
Olievenhoutbosch 2 | 2024-09-01 | 10755.9 | 2025-09-24 | 0 | 1 | 10755.9
Olievenhoutbosch 2 | 2024-10-01 | 12190.5 | 2025-09-24 | 0 | 1 | 12190.5
Olievenhoutbosch 2 | 2024-11-01 | 12263.4 | 2025-09-24 | 0 | 1 | 12263.4
Olievenhoutbosch 2 | 2024-12-01 | 12539.7 | 2025-09-24 | 0 | 1 | 12539.7
Olievenhoutbosch 2 | 2025-01-01 | 12369.6 | 2025-09-24 | 0 | 1 | 12369.6
Olievenhoutbosch 2 | 2025-02-01 | 10801.8 | 2025-09-24 | 0 | 1 | 10801.8
Olievenhoutbosch 2 | 2025-03-01 | 10537.2 | 2025-09-24 | 0 | 1 | 10537.2
Olievenhoutbosch 2 | 2025-04-01 | 9173.7 | 2025-09-24 | 0 | 1 | 9173.7
Olievenhoutbosch 2 | 2025-05-01 | 8503.2 | 2025-09-24 | 0 | 1 | 8503.2
Olievenhoutbosch 2 | 2025-06-01 | 7545.6 | 2025-09-24 | 0 | 1 | 7545.6
Olievenhoutbosch 2 | 2025-07-01 | 8307 | 2025-09-24 | 0 | 1 | 8307
Olievenhoutbosch 2 | 2025-08-01 | 9720.9 | 2025-09-24 | 0 | 1 | 9720.9
Olievenhoutbosch 2 | 2025-09-01 | 10755.9 | 2025-09-24 | 0 | 1 | 10755.9
Olievenhoutbosch 2 | 2025-10-01 | 12190.5 | 2025-09-24 | 0.019165 | 0.99987 | 12188.8589
Olievenhoutbosch 2 | 2025-11-01 | 12263.4 | 2025-09-24 | 0.10404 | 0.99927 | 12254.4408
Olievenhoutbosch 2 | 2025-12-01 | 12539.7 | 2025-09-24 | 0.18617 | 0.99869 | 12523.3113
Olievenhoutbosch 2 | 2026-01-01 | 12369.6 | 2025-09-24 | 0.27105 | 0.9981 | 12346.0707
Olievenhoutbosch 2 | 2026-02-01 | 10801.8 | 2025-09-24 | 0.35592 | 0.9975 | 10774.827
Olievenhoutbosch 2 | 2026-03-01 | 10537.2 | 2025-09-24 | 0.43258 | 0.99697 | 10505.2291
Olievenhoutbosch 2 | 2026-04-01 | 9173.7 | 2025-09-24 | 0.51745 | 0.99637 | 9140.4149
Olievenhoutbosch 2 | 2026-05-01 | 8503.2 | 2025-09-24 | 0.59959 | 0.9958 | 8467.4608
Olievenhoutbosch 2 | 2026-06-01 | 7545.6 | 2025-09-24 | 0.68446 | 0.9952 | 7509.4072
Olievenhoutbosch 2 | 2026-07-01 | 8307 | 2025-09-24 | 0.7666 | 0.99463 | 8262.3866
Olievenhoutbosch 2 | 2026-08-01 | 9720.9 | 2025-09-24 | 0.85147 | 0.99404 | 9662.9303
Olievenhoutbosch 2 | 2026-09-01 | 10755.9 | 2025-09-24 | 0.93634 | 0.99344 | 10685.3856
Olievenhoutbosch 2 | 2026-10-01 | 12190.5 | 2025-09-24 | 1.0185 | 0.99287 | 12103.5951
Olievenhoutbosch 2 | 2026-11-01 | 12263.4 | 2025-09-24 | 1.1034 | 0.99228 | 12168.7182
Olievenhoutbosch 2 | 2026-12-01 | 12539.7 | 2025-09-24 | 1.1855 | 0.99171 | 12435.7079
Opal Students | 2024-01-01 | 5685.3 | 2023-09-05 | 0.32307 | 0.99773 | 5672.4123
Opal Students | 2024-02-01 | 4780.8 | 2023-09-05 | 0.40794 | 0.99714 | 4767.1197
Opal Students | 2024-03-01 | 4935.6 | 2023-09-05 | 0.48734 | 0.99658 | 4918.7326
Opal Students | 2024-04-01 | 4359.6 | 2023-09-05 | 0.57221 | 0.99599 | 4342.1115
Opal Students | 2024-05-01 | 4194 | 2023-09-05 | 0.65435 | 0.99541 | 4174.7664
Opal Students | 2024-06-01 | 3818.7 | 2023-09-05 | 0.73922 | 0.99482 | 3798.9219
Opal Students | 2024-07-01 | 4217.4 | 2023-09-05 | 0.82136 | 0.99425 | 4193.1369
Opal Students | 2024-08-01 | 4844.7 | 2023-09-05 | 0.90623 | 0.99365 | 4813.957
Opal Students | 2024-09-01 | 5300.1 | 2023-09-05 | 0.9911 | 0.99306 | 5263.3283
Opal Students | 2024-10-01 | 5667.3 | 2023-09-05 | 1.0732 | 0.99249 | 5624.7344
Opal Students | 2024-11-01 | 5624.1 | 2023-09-05 | 1.1581 | 0.9919 | 5578.532
Opal Students | 2024-12-01 | 5995.8 | 2023-09-05 | 1.2402 | 0.99133 | 5943.79
Opal Students | 2025-01-01 | 5685.3 | 2023-09-05 | 1.3251 | 0.99073 | 5632.6242
Opal Students | 2025-02-01 | 4780.8 | 2023-09-05 | 1.41 | 0.99014 | 4733.6815
Opal Students | 2025-03-01 | 4935.6 | 2023-09-05 | 1.4867 | 0.98961 | 4884.3249
Opal Students | 2025-04-01 | 4359.6 | 2023-09-05 | 1.5715 | 0.98902 | 4311.7374
Opal Students | 2025-05-01 | 4194 | 2023-09-05 | 1.6537 | 0.98845 | 4145.563
Opal Students | 2025-06-01 | 3818.7 | 2023-09-05 | 1.7385 | 0.98786 | 3772.3476
Opal Students | 2025-07-01 | 4217.4 | 2023-09-05 | 1.8207 | 0.98729 | 4163.805
Opal Students | 2025-08-01 | 4844.7 | 2023-09-05 | 1.9055 | 0.9867 | 4780.2823
Opal Students | 2025-09-01 | 5300.1 | 2023-09-05 | 1.9904 | 0.98612 | 5226.5101
Opal Students | 2025-10-01 | 5667.3 | 2023-09-05 | 2.0726 | 0.98555 | 5585.3881
Opal Students | 2025-11-01 | 5624.1 | 2023-09-05 | 2.1574 | 0.98496 | 5539.5089
Opal Students | 2025-12-01 | 5995.8 | 2023-09-05 | 2.2396 | 0.98439 | 5902.2118
Opal Students | 2026-01-01 | 5685.3 | 2023-09-05 | 2.3244 | 0.9838 | 5593.2227
Opal Students | 2026-02-01 | 4780.8 | 2023-09-05 | 2.4093 | 0.98322 | 4700.5684
Opal Students | 2026-03-01 | 4935.6 | 2023-09-05 | 2.486 | 0.98269 | 4850.158
Opal Students | 2026-04-01 | 4359.6 | 2023-09-05 | 2.5708 | 0.9821 | 4281.5759
Opal Students | 2026-05-01 | 4194 | 2023-09-05 | 2.653 | 0.98154 | 4116.5638
Opal Students | 2026-06-01 | 3818.7 | 2023-09-05 | 2.7379 | 0.98095 | 3745.9592
Opal Students | 2026-07-01 | 4217.4 | 2023-09-05 | 2.82 | 0.98039 | 4134.6782
Opal Students | 2026-08-01 | 4844.7 | 2023-09-05 | 2.9049 | 0.9798 | 4746.8432
Opal Students | 2026-09-01 | 5300.1 | 2023-09-05 | 2.9897 | 0.97922 | 5189.9495
Opal Students | 2026-10-01 | 5667.3 | 2023-09-05 | 3.0719 | 0.97865 | 5546.3171
Opal Students | 2026-11-01 | 5624.1 | 2023-09-05 | 3.1567 | 0.97807 | 5500.7588
Opal Students | 2026-12-01 | 5995.8 | 2023-09-05 | 3.2389 | 0.97751 | 5860.9245
Orthochem Bethlehem | 2024-01-01 | 41208.48 | 2023-06-24 | 0.52293 | 0.99633 | 41057.3833
Orthochem Bethlehem | 2024-02-01 | 35976.15 | 2023-06-24 | 0.6078 | 0.99574 | 35822.8744
Orthochem Bethlehem | 2024-03-01 | 36559.98 | 2023-06-24 | 0.6872 | 0.99518 | 36383.9186
Orthochem Bethlehem | 2024-04-01 | 33604.11 | 2023-06-24 | 0.77207 | 0.99459 | 33422.3507
Orthochem Bethlehem | 2024-05-01 | 32958.63 | 2023-06-24 | 0.85421 | 0.99402 | 32761.4542
Orthochem Bethlehem | 2024-06-01 | 30018.2212 | 2023-06-24 | 0.93908 | 0.99343 | 29820.8518
Orthochem Bethlehem | 2024-07-01 | 32459.8096 | 2023-06-24 | 1.0212 | 0.99285 | 32227.787
Orthochem Bethlehem | 2024-08-01 | 36506.1257 | 2023-06-24 | 1.1061 | 0.99226 | 36223.577
Orthochem Bethlehem | 2024-09-01 | 37370.8698 | 2023-06-24 | 1.191 | 0.99167 | 37059.5266
Orthochem Bethlehem | 2024-10-01 | 40182.9863 | 2023-06-24 | 1.2731 | 0.9911 | 39825.2302
Orthochem Bethlehem | 2024-11-01 | 40330.5361 | 2023-06-24 | 1.358 | 0.99051 | 39947.6424
Orthochem Bethlehem | 2024-12-01 | 42601.4278 | 2023-06-24 | 1.4401 | 0.98993 | 42172.6352
Orthochem Bethlehem | 2025-01-01 | 41208.48 | 2023-06-24 | 1.525 | 0.98934 | 40769.3936
Orthochem Bethlehem | 2025-02-01 | 35976.15 | 2023-06-24 | 1.6099 | 0.98876 | 35571.6011
Orthochem Bethlehem | 2025-03-01 | 36559.98 | 2023-06-24 | 1.6865 | 0.98822 | 36129.4049
Orthochem Bethlehem | 2025-04-01 | 33604.11 | 2023-06-24 | 1.7714 | 0.98763 | 33188.5538
Orthochem Bethlehem | 2025-05-01 | 32958.63 | 2023-06-24 | 1.8535 | 0.98706 | 32532.2804
Orthochem Bethlehem | 2025-06-01 | 30018.2212 | 2023-06-24 | 1.9384 | 0.98648 | 29612.2483
Orthochem Bethlehem | 2025-07-01 | 32459.8096 | 2023-06-24 | 2.0205 | 0.98591 | 32002.3464
Orthochem Bethlehem | 2025-08-01 | 36506.1257 | 2023-06-24 | 2.1054 | 0.98532 | 35970.1849
Orthochem Bethlehem | 2025-09-01 | 37370.8698 | 2023-06-24 | 2.1903 | 0.98473 | 36800.2869
Orthochem Bethlehem | 2025-10-01 | 40182.9863 | 2023-06-24 | 2.2724 | 0.98416 | 39546.6438
Orthochem Bethlehem | 2025-11-01 | 40330.5361 | 2023-06-24 | 2.3573 | 0.98358 | 39668.1997
Orthochem Bethlehem | 2025-12-01 | 42601.4278 | 2023-06-24 | 2.4394 | 0.98301 | 41877.6281
Orthochem Bethlehem | 2026-01-01 | 41208.48 | 2023-06-24 | 2.5243 | 0.98242 | 40484.2025
Orthochem Bethlehem | 2026-02-01 | 35976.15 | 2023-06-24 | 2.6092 | 0.98184 | 35322.7698
Orthochem Bethlehem | 2026-03-01 | 36559.98 | 2023-06-24 | 2.6858 | 0.98131 | 35876.6715
Orthochem Bethlehem | 2026-04-01 | 33604.11 | 2023-06-24 | 2.7707 | 0.98073 | 32956.3924
Orthochem Bethlehem | 2026-05-01 | 32958.63 | 2023-06-24 | 2.8528 | 0.98016 | 32304.7098
Orthochem Bethlehem | 2026-06-01 | 30018.2212 | 2023-06-24 | 2.9377 | 0.97958 | 29405.1039
Orthochem Bethlehem | 2026-07-01 | 32459.8096 | 2023-06-24 | 3.0198 | 0.97901 | 31778.4827
Orthochem Bethlehem | 2026-08-01 | 36506.1257 | 2023-06-24 | 3.1047 | 0.97843 | 35718.5654
Orthochem Bethlehem | 2026-09-01 | 37370.8698 | 2023-06-24 | 3.1896 | 0.97784 | 36542.8606
Orthochem Bethlehem | 2026-10-01 | 40182.9863 | 2023-06-24 | 3.2717 | 0.97728 | 39270.0061
Orthochem Bethlehem | 2026-11-01 | 40330.5361 | 2023-06-24 | 3.3566 | 0.9767 | 39390.7117
Orthochem Bethlehem | 2026-12-01 | 42601.4278 | 2023-06-24 | 3.4387 | 0.97613 | 41584.6846
PNB Unlimited | 2024-01-01 | 11540.96 | 2020-11-26 | 3.0965 | 0.97848 | 11292.6341
PNB Unlimited | 2024-02-01 | 9862.32 | 2020-11-26 | 3.1814 | 0.9779 | 9644.3615
PNB Unlimited | 2024-03-01 | 10345.44 | 2020-11-26 | 3.2608 | 0.97735 | 10111.1636
PNB Unlimited | 2024-04-01 | 8819.52 | 2020-11-26 | 3.3457 | 0.97677 | 8614.661
PNB Unlimited | 2024-05-01 | 8538.08 | 2020-11-26 | 3.4278 | 0.97621 | 8334.9478
PNB Unlimited | 2024-06-01 | 7700 | 2020-11-26 | 3.5127 | 0.97563 | 7512.3267
PNB Unlimited | 2024-07-01 | 8487.2 | 2020-11-26 | 3.5948 | 0.97506 | 8275.564
PNB Unlimited | 2024-08-01 | 9810.48 | 2020-11-26 | 3.6797 | 0.97448 | 9560.1453
PNB Unlimited | 2024-09-01 | 10706.48 | 2020-11-26 | 3.7645 | 0.9739 | 10427.0635
PNB Unlimited | 2024-10-01 | 11410.4 | 2020-11-26 | 3.8467 | 0.97334 | 11106.2029
PNB Unlimited | 2024-11-01 | 11340.4 | 2020-11-26 | 3.9316 | 0.97276 | 11031.4901
PNB Unlimited | 2024-12-01 | 12102.56 | 2020-11-26 | 4.0137 | 0.9722 | 11766.0984
PNB Unlimited | 2025-01-01 | 11540.96 | 2020-11-26 | 4.0986 | 0.97162 | 11213.4239
PNB Unlimited | 2025-02-01 | 9862.32 | 2020-11-26 | 4.1834 | 0.97104 | 9576.7129
PNB Unlimited | 2025-03-01 | 10345.44 | 2020-11-26 | 4.2601 | 0.97052 | 10040.4337
PNB Unlimited | 2025-04-01 | 8819.52 | 2020-11-26 | 4.345 | 0.96994 | 8554.3995
PNB Unlimited | 2025-05-01 | 8538.08 | 2020-11-26 | 4.4271 | 0.96938 | 8276.643
PNB Unlimited | 2025-06-01 | 7700 | 2020-11-26 | 4.512 | 0.9688 | 7459.7762
PNB Unlimited | 2025-07-01 | 8487.2 | 2020-11-26 | 4.5941 | 0.96824 | 8217.6745
PNB Unlimited | 2025-08-01 | 9810.48 | 2020-11-26 | 4.679 | 0.96767 | 9493.2699
PNB Unlimited | 2025-09-01 | 10706.48 | 2020-11-26 | 4.7639 | 0.96709 | 10354.1239
PNB Unlimited | 2025-10-01 | 11410.4 | 2020-11-26 | 4.846 | 0.96653 | 11028.5125
PNB Unlimited | 2025-11-01 | 11340.4 | 2020-11-26 | 4.9309 | 0.96596 | 10954.3223
PNB Unlimited | 2025-12-01 | 12102.56 | 2020-11-26 | 5.013 | 0.9654 | 11683.7919
PNB Unlimited | 2026-01-01 | 11540.96 | 2020-11-26 | 5.0979 | 0.96482 | 11134.9835
PNB Unlimited | 2026-02-01 | 9862.32 | 2020-11-26 | 5.1828 | 0.96425 | 9509.7216
PNB Unlimited | 2026-03-01 | 10345.44 | 2020-11-26 | 5.2594 | 0.96373 | 9970.1986
PNB Unlimited | 2026-04-01 | 8819.52 | 2020-11-26 | 5.3443 | 0.96315 | 8494.5595
PNB Unlimited | 2026-05-01 | 8538.08 | 2020-11-26 | 5.4264 | 0.9626 | 8218.746
PNB Unlimited | 2026-06-01 | 7700 | 2020-11-26 | 5.5113 | 0.96203 | 7407.5934
PNB Unlimited | 2026-07-01 | 8487.2 | 2020-11-26 | 5.5934 | 0.96147 | 8160.1901
PNB Unlimited | 2026-08-01 | 9810.48 | 2020-11-26 | 5.6783 | 0.9609 | 9426.8624
PNB Unlimited | 2026-09-01 | 10706.48 | 2020-11-26 | 5.7632 | 0.96032 | 10281.6944
PNB Unlimited | 2026-10-01 | 11410.4 | 2020-11-26 | 5.8453 | 0.95977 | 10951.3656
PNB Unlimited | 2026-11-01 | 11340.4 | 2020-11-26 | 5.9302 | 0.9592 | 10877.6944
PNB Unlimited | 2026-12-01 | 12102.56 | 2020-11-26 | 6.0123 | 0.95865 | 11602.0611
Plastiplate | 2024-01-01 | 8591.025 | 2022-05-07 | 1.6537 | 0.98845 | 8491.8061
Plastiplate | 2024-02-01 | 7466.475 | 2022-05-07 | 1.7385 | 0.98786 | 7375.8449
Plastiplate | 2024-03-01 | 7931.85 | 2022-05-07 | 1.8179 | 0.98731 | 7831.2021
Plastiplate | 2024-04-01 | 6987.15 | 2022-05-07 | 1.9028 | 0.98672 | 6894.3778
Plastiplate | 2024-05-01 | 6858.525 | 2022-05-07 | 1.9849 | 0.98615 | 6763.5571
Plastiplate | 2024-06-01 | 6375.45 | 2022-05-07 | 2.0698 | 0.98557 | 6283.4238
Plastiplate | 2024-07-01 | 6946.725 | 2022-05-07 | 2.152 | 0.985 | 6842.5037
Plastiplate | 2024-08-01 | 7852.65 | 2022-05-07 | 2.2368 | 0.98441 | 7730.227
Plastiplate | 2024-09-01 | 8347.05 | 2022-05-07 | 2.3217 | 0.98382 | 8212.0218
Plastiplate | 2024-10-01 | 8786.625 | 2022-05-07 | 2.4038 | 0.98326 | 8639.4997
Plastiplate | 2024-11-01 | 8551.8 | 2022-05-07 | 2.4887 | 0.98267 | 8403.5949
Plastiplate | 2024-12-01 | 9109.05 | 2022-05-07 | 2.5708 | 0.9821 | 8946.0246
Plastiplate | 2025-01-01 | 8591.025 | 2022-05-07 | 2.6557 | 0.98152 | 8432.2419
Plastiplate | 2025-02-01 | 7466.475 | 2022-05-07 | 2.7406 | 0.98093 | 7324.1083
Plastiplate | 2025-03-01 | 7931.85 | 2022-05-07 | 2.8172 | 0.9804 | 7776.4211
Plastiplate | 2025-04-01 | 6987.15 | 2022-05-07 | 2.9021 | 0.97982 | 6846.1501
Plastiplate | 2025-05-01 | 6858.525 | 2022-05-07 | 2.9843 | 0.97925 | 6716.2445
Plastiplate | 2025-06-01 | 6375.45 | 2022-05-07 | 3.0691 | 0.97867 | 6239.4698
Plastiplate | 2025-07-01 | 6946.725 | 2022-05-07 | 3.1513 | 0.97811 | 6794.6388
Plastiplate | 2025-08-01 | 7852.65 | 2022-05-07 | 3.2361 | 0.97752 | 7676.1523
Plastiplate | 2025-09-01 | 8347.05 | 2022-05-07 | 3.321 | 0.97694 | 8154.5768
Plastiplate | 2025-10-01 | 8786.625 | 2022-05-07 | 3.4031 | 0.97638 | 8579.0645
Plastiplate | 2025-11-01 | 8551.8 | 2022-05-07 | 3.488 | 0.9758 | 8344.8099
Plastiplate | 2025-12-01 | 9109.05 | 2022-05-07 | 3.5702 | 0.97523 | 8883.4451
Plastiplate | 2026-01-01 | 8591.025 | 2022-05-07 | 3.655 | 0.97465 | 8373.2564
Plastiplate | 2026-02-01 | 7466.475 | 2022-05-07 | 3.7399 | 0.97407 | 7272.8746
Plastiplate | 2026-03-01 | 7931.85 | 2022-05-07 | 3.8166 | 0.97355 | 7722.0232
Plastiplate | 2026-04-01 | 6987.15 | 2022-05-07 | 3.9014 | 0.97297 | 6798.2597
Plastiplate | 2026-05-01 | 6858.525 | 2022-05-07 | 3.9836 | 0.9724 | 6669.2629
Plastiplate | 2026-06-01 | 6375.45 | 2022-05-07 | 4.0684 | 0.97183 | 6195.8233
Plastiplate | 2026-07-01 | 6946.725 | 2022-05-07 | 4.1506 | 0.97126 | 6747.1088
Plastiplate | 2026-08-01 | 7852.65 | 2022-05-07 | 4.2355 | 0.97069 | 7622.4559
Plastiplate | 2026-09-01 | 8347.05 | 2022-05-07 | 4.3203 | 0.97011 | 8097.5337
Plastiplate | 2026-10-01 | 8786.625 | 2022-05-07 | 4.4025 | 0.96955 | 8519.052
Plastiplate | 2026-11-01 | 8551.8 | 2022-05-07 | 4.4873 | 0.96897 | 8286.4361
Plastiplate | 2026-12-01 | 9109.05 | 2022-05-07 | 4.5695 | 0.96841 | 8821.3034
Q-lity Meat | 2024-01-01 | 4894.29 | 2023-06-15 | 0.54757 | 0.99616 | 4875.5004
Q-lity Meat | 2024-02-01 | 4527.45 | 2023-06-15 | 0.63244 | 0.99557 | 4507.3806
Q-lity Meat | 2024-03-01 | 4754.25 | 2023-06-15 | 0.71184 | 0.99501 | 4730.5361
Q-lity Meat | 2024-04-01 | 4171.59 | 2023-06-15 | 0.79671 | 0.99442 | 4148.3084
Q-lity Meat | 2024-05-01 | 4117.5 | 2023-06-15 | 0.87885 | 0.99385 | 4092.1586
Q-lity Meat | 2024-06-01 | 3729.06 | 2023-06-15 | 0.96372 | 0.99325 | 3703.9003
Q-lity Meat | 2024-07-01 | 4105.53 | 2023-06-15 | 1.0459 | 0.99268 | 4075.4782
Q-lity Meat | 2024-08-01 | 4624.83 | 2023-06-15 | 1.1307 | 0.99209 | 4588.2407
Q-lity Meat | 2024-09-01 | 4797 | 2023-06-15 | 1.2156 | 0.9915 | 4756.212
Q-lity Meat | 2024-10-01 | 5068.98 | 2023-06-15 | 1.2977 | 0.99093 | 5022.9805
Q-lity Meat | 2024-11-01 | 4862.88 | 2023-06-15 | 1.3826 | 0.99033 | 4815.8787
Q-lity Meat | 2024-12-01 | 5082.39 | 2023-06-15 | 1.4648 | 0.98976 | 5030.3638
Q-lity Meat | 2025-01-01 | 4894.29 | 2023-06-15 | 1.5496 | 0.98917 | 4841.3021
Q-lity Meat | 2025-02-01 | 4527.45 | 2023-06-15 | 1.6345 | 0.98858 | 4475.7644
Q-lity Meat | 2025-03-01 | 4754.25 | 2023-06-15 | 1.7112 | 0.98805 | 4697.445
Q-lity Meat | 2025-04-01 | 4171.59 | 2023-06-15 | 1.796 | 0.98746 | 4119.2901
Q-lity Meat | 2025-05-01 | 4117.5 | 2023-06-15 | 1.8782 | 0.98689 | 4063.533
Q-lity Meat | 2025-06-01 | 3729.06 | 2023-06-15 | 1.963 | 0.98631 | 3677.9907
Q-lity Meat | 2025-07-01 | 4105.53 | 2023-06-15 | 2.0452 | 0.98574 | 4046.9693
Q-lity Meat | 2025-08-01 | 4624.83 | 2023-06-15 | 2.13 | 0.98515 | 4556.1449
Q-lity Meat | 2025-09-01 | 4797 | 2023-06-15 | 2.2149 | 0.98456 | 4722.9413
Q-lity Meat | 2025-10-01 | 5068.98 | 2023-06-15 | 2.2971 | 0.98399 | 4987.8436
Q-lity Meat | 2025-11-01 | 4862.88 | 2023-06-15 | 2.3819 | 0.98341 | 4782.1905
Q-lity Meat | 2025-12-01 | 5082.39 | 2023-06-15 | 2.4641 | 0.98284 | 4995.1753
Q-lity Meat | 2026-01-01 | 4894.29 | 2023-06-15 | 2.5489 | 0.98225 | 4807.4361
Q-lity Meat | 2026-02-01 | 4527.45 | 2023-06-15 | 2.6338 | 0.98167 | 4444.4554
Q-lity Meat | 2026-03-01 | 4754.25 | 2023-06-15 | 2.7105 | 0.98114 | 4664.5853
Q-lity Meat | 2026-04-01 | 4171.59 | 2023-06-15 | 2.7953 | 0.98056 | 4090.4747
Q-lity Meat | 2026-05-01 | 4117.5 | 2023-06-15 | 2.8775 | 0.97999 | 4035.1077
Q-lity Meat | 2026-06-01 | 3729.06 | 2023-06-15 | 2.9624 | 0.97941 | 3652.2623
Q-lity Meat | 2026-07-01 | 4105.53 | 2023-06-15 | 3.0445 | 0.97884 | 4018.6598
Q-lity Meat | 2026-08-01 | 4624.83 | 2023-06-15 | 3.1294 | 0.97826 | 4524.2736
Q-lity Meat | 2026-09-01 | 4797 | 2023-06-15 | 3.2142 | 0.97767 | 4689.9032
Q-lity Meat | 2026-10-01 | 5068.98 | 2023-06-15 | 3.2964 | 0.97711 | 4952.9525
Q-lity Meat | 2026-11-01 | 4862.88 | 2023-06-15 | 3.3812 | 0.97653 | 4748.738
Q-lity Meat | 2026-12-01 | 5082.39 | 2023-06-15 | 3.4634 | 0.97596 | 4960.2329
Quintondale | 2024-01-01 | 5902.47 | 2022-04-12 | 1.7221 | 0.98798 | 5831.4971
Quintondale | 2024-02-01 | 5299.2 | 2022-04-12 | 1.807 | 0.98739 | 5232.3605
Quintondale | 2024-03-01 | 5701.86 | 2022-04-12 | 1.8864 | 0.98684 | 5626.8025
Quintondale | 2024-04-01 | 5085.9 | 2022-04-12 | 1.9713 | 0.98625 | 5015.9594
Quintondale | 2024-05-01 | 5204.61 | 2022-04-12 | 2.0534 | 0.98568 | 5130.0762
Quintondale | 2024-06-01 | 4824.36 | 2022-04-12 | 2.1383 | 0.98509 | 4752.4374
Quintondale | 2024-07-01 | 5303.16 | 2022-04-12 | 2.2204 | 0.98452 | 5221.086
Quintondale | 2024-08-01 | 5833.08 | 2022-04-12 | 2.3053 | 0.98394 | 5739.3819
Quintondale | 2024-09-01 | 6021.81 | 2022-04-12 | 2.3901 | 0.98335 | 5921.5488
Quintondale | 2024-10-01 | 6128.91 | 2022-04-12 | 2.4723 | 0.98278 | 6023.3893
Quintondale | 2024-11-01 | 5928.57 | 2022-04-12 | 2.5572 | 0.9822 | 5823.0258
Quintondale | 2024-12-01 | 6186.69 | 2022-04-12 | 2.6393 | 0.98163 | 6073.0456
Quintondale | 2025-01-01 | 5902.47 | 2022-04-12 | 2.7242 | 0.98105 | 5790.5931
Quintondale | 2025-02-01 | 5299.2 | 2022-04-12 | 2.809 | 0.98046 | 5195.659
Quintondale | 2025-03-01 | 5701.86 | 2022-04-12 | 2.8857 | 0.97993 | 5587.4418
Quintondale | 2025-04-01 | 5085.9 | 2022-04-12 | 2.9706 | 0.97935 | 4980.8717
Quintondale | 2025-05-01 | 5204.61 | 2022-04-12 | 3.0527 | 0.97878 | 5094.1901
Quintondale | 2025-06-01 | 4824.36 | 2022-04-12 | 3.1376 | 0.9782 | 4719.193
Quintondale | 2025-07-01 | 5303.16 | 2022-04-12 | 3.2197 | 0.97764 | 5184.5634
Quintondale | 2025-08-01 | 5833.08 | 2022-04-12 | 3.3046 | 0.97705 | 5699.2337
Quintondale | 2025-09-01 | 6021.81 | 2022-04-12 | 3.3895 | 0.97647 | 5880.1262
Quintondale | 2025-10-01 | 6128.91 | 2022-04-12 | 3.4716 | 0.97591 | 5981.2543
Quintondale | 2025-11-01 | 5928.57 | 2022-04-12 | 3.5565 | 0.97533 | 5782.2924
Quintondale | 2025-12-01 | 6186.69 | 2022-04-12 | 3.6386 | 0.97476 | 6030.5633
Quintondale | 2026-01-01 | 5902.47 | 2022-04-12 | 3.7235 | 0.97418 | 5750.0866
Quintondale | 2026-02-01 | 5299.2 | 2022-04-12 | 3.8084 | 0.9736 | 5159.3142
Quintondale | 2026-03-01 | 5701.86 | 2022-04-12 | 3.885 | 0.97308 | 5548.3564
Quintondale | 2026-04-01 | 5085.9 | 2022-04-12 | 3.9699 | 0.9725 | 4946.0293
Quintondale | 2026-05-01 | 5204.61 | 2022-04-12 | 4.052 | 0.97194 | 5058.5551
Quintondale | 2026-06-01 | 4824.36 | 2022-04-12 | 4.1369 | 0.97136 | 4686.1812
Quintondale | 2026-07-01 | 5303.16 | 2022-04-12 | 4.219 | 0.9708 | 5148.2962
Quintondale | 2026-08-01 | 5833.08 | 2022-04-12 | 4.3039 | 0.97022 | 5659.3662
Quintondale | 2026-09-01 | 6021.81 | 2022-04-12 | 4.3888 | 0.96964 | 5838.9934
Quintondale | 2026-10-01 | 6128.91 | 2022-04-12 | 4.4709 | 0.96908 | 5939.4141
Quintondale | 2026-11-01 | 5928.57 | 2022-04-12 | 4.5558 | 0.9685 | 5741.844
Quintondale | 2026-12-01 | 6186.69 | 2022-04-12 | 4.6379 | 0.96795 | 5988.3781
Riverside Lodge | 2024-01-01 | 17099.45 | 2023-05-12 | 0.64066 | 0.99551 | 17022.6691
Riverside Lodge | 2024-02-01 | 15031.4 | 2023-05-12 | 0.72553 | 0.99492 | 14954.9863
Riverside Lodge | 2024-03-01 | 16289.4 | 2023-05-12 | 0.80493 | 0.99436 | 16197.5546
Riverside Lodge | 2024-04-01 | 14250.25 | 2023-05-12 | 0.8898 | 0.99377 | 14161.4564
Riverside Lodge | 2024-05-01 | 14783.2 | 2023-05-12 | 0.97194 | 0.9932 | 14682.6117
Riverside Lodge | 2024-06-01 | 13871.15 | 2023-05-12 | 1.0568 | 0.9926 | 13768.5562
Riverside Lodge | 2024-07-01 | 15110.45 | 2023-05-12 | 1.1389 | 0.99203 | 14990.0388
Riverside Lodge | 2024-08-01 | 16763.7 | 2023-05-12 | 1.2238 | 0.99144 | 16620.2025
Riverside Lodge | 2024-09-01 | 16935.4 | 2023-05-12 | 1.3087 | 0.99085 | 16780.4253
Riverside Lodge | 2024-10-01 | 17583.95 | 2023-05-12 | 1.3908 | 0.99028 | 17412.9907
Riverside Lodge | 2024-11-01 | 16597.1 | 2023-05-12 | 1.4757 | 0.98969 | 16425.9392
Riverside Lodge | 2024-12-01 | 17731 | 2023-05-12 | 1.5578 | 0.98912 | 17538.0238
Riverside Lodge | 2025-01-01 | 17099.45 | 2023-05-12 | 1.6427 | 0.98853 | 16903.2666
Riverside Lodge | 2025-02-01 | 15031.4 | 2023-05-12 | 1.7276 | 0.98794 | 14850.0872
Riverside Lodge | 2025-03-01 | 16289.4 | 2023-05-12 | 1.8042 | 0.98741 | 16084.249
Riverside Lodge | 2025-04-01 | 14250.25 | 2023-05-12 | 1.8891 | 0.98682 | 14062.3938
Riverside Lodge | 2025-05-01 | 14783.2 | 2023-05-12 | 1.9713 | 0.98625 | 14579.9035
Riverside Lodge | 2025-06-01 | 13871.15 | 2023-05-12 | 2.0561 | 0.98566 | 13672.2421
Riverside Lodge | 2025-07-01 | 15110.45 | 2023-05-12 | 2.1383 | 0.98509 | 14885.1801
Riverside Lodge | 2025-08-01 | 16763.7 | 2023-05-12 | 2.2231 | 0.9845 | 16503.9405
Riverside Lodge | 2025-09-01 | 16935.4 | 2023-05-12 | 2.308 | 0.98392 | 16663.0424
Riverside Lodge | 2025-10-01 | 17583.95 | 2023-05-12 | 2.3901 | 0.98335 | 17291.1829
Riverside Lodge | 2025-11-01 | 16597.1 | 2023-05-12 | 2.475 | 0.98276 | 16311.0361
Riverside Lodge | 2025-12-01 | 17731 | 2023-05-12 | 2.5572 | 0.9822 | 17415.3414
Riverside Lodge | 2026-01-01 | 17099.45 | 2023-05-12 | 2.642 | 0.98161 | 16785.0244
Riverside Lodge | 2026-02-01 | 15031.4 | 2023-05-12 | 2.7269 | 0.98103 | 14746.2075
Riverside Lodge | 2026-03-01 | 16289.4 | 2023-05-12 | 2.8036 | 0.9805 | 15971.7361
Riverside Lodge | 2026-04-01 | 14250.25 | 2023-05-12 | 2.8884 | 0.97991 | 13964.0242
Riverside Lodge | 2026-05-01 | 14783.2 | 2023-05-12 | 2.9706 | 0.97935 | 14477.9138
Riverside Lodge | 2026-06-01 | 13871.15 | 2023-05-12 | 3.0554 | 0.97877 | 13576.6016
Riverside Lodge | 2026-07-01 | 15110.45 | 2023-05-12 | 3.1376 | 0.9782 | 14781.0549
Riverside Lodge | 2026-08-01 | 16763.7 | 2023-05-12 | 3.2225 | 0.97762 | 16388.4917
Riverside Lodge | 2026-09-01 | 16935.4 | 2023-05-12 | 3.3073 | 0.97704 | 16546.4807
Riverside Lodge | 2026-10-01 | 17583.95 | 2023-05-12 | 3.3895 | 0.97647 | 17170.2272
Riverside Lodge | 2026-11-01 | 16597.1 | 2023-05-12 | 3.4743 | 0.97589 | 16196.9367
Riverside Lodge | 2026-12-01 | 17731 | 2023-05-12 | 3.5565 | 0.97533 | 17293.5172
Roan Foods | 2024-01-01 | 20178 | 2026-04-02 | 0 | 1 | 20178
Roan Foods | 2024-02-01 | 17954 | 2026-04-02 | 0 | 1 | 17954
Roan Foods | 2024-03-01 | 19150 | 2026-04-02 | 0 | 1 | 19150
Roan Foods | 2024-04-01 | 18060 | 2026-04-02 | 0 | 1 | 18060
Roan Foods | 2024-05-01 | 18124 | 2026-04-02 | 0 | 1 | 18124
Roan Foods | 2024-06-01 | 15908 | 2026-04-02 | 0 | 1 | 15908
Roan Foods | 2024-07-01 | 16827 | 2026-04-02 | 0 | 1 | 16827
Roan Foods | 2024-08-01 | 19405 | 2026-04-02 | 0 | 1 | 19405
Roan Foods | 2024-09-01 | 19981 | 2026-04-02 | 0 | 1 | 19981
Roan Foods | 2024-10-01 | 22401 | 2026-04-02 | 0 | 1 | 22401
Roan Foods | 2024-11-01 | 20125 | 2026-04-02 | 0 | 1 | 20125
Roan Foods | 2024-12-01 | 20771 | 2026-04-02 | 0 | 1 | 20771
Roan Foods | 2025-01-01 | 20178 | 2026-04-02 | 0 | 1 | 20178
Roan Foods | 2025-02-01 | 17954 | 2026-04-02 | 0 | 1 | 17954
Roan Foods | 2025-03-01 | 19150 | 2026-04-02 | 0 | 1 | 19150
Roan Foods | 2025-04-01 | 18060 | 2026-04-02 | 0 | 1 | 18060
Roan Foods | 2025-05-01 | 18124 | 2026-04-02 | 0 | 1 | 18124
Roan Foods | 2025-06-01 | 15908 | 2026-04-02 | 0 | 1 | 15908
Roan Foods | 2025-07-01 | 16827 | 2026-04-02 | 0 | 1 | 16827
Roan Foods | 2025-08-01 | 19405 | 2026-04-02 | 0 | 1 | 19405
Roan Foods | 2025-09-01 | 19981 | 2026-04-02 | 0 | 1 | 19981
Roan Foods | 2025-10-01 | 22401 | 2026-04-02 | 0 | 1 | 22401
Roan Foods | 2025-11-01 | 20125 | 2026-04-02 | 0 | 1 | 20125
Roan Foods | 2025-12-01 | 20771 | 2026-04-02 | 0 | 1 | 20771
Roan Foods | 2026-01-01 | 20178 | 2026-04-02 | 0 | 1 | 20178
Roan Foods | 2026-02-01 | 17954 | 2026-04-02 | 0 | 1 | 17954
Roan Foods | 2026-03-01 | 19150 | 2026-04-02 | 0 | 1 | 19150
Roan Foods | 2026-04-01 | 18060 | 2026-04-02 | 0 | 1 | 18060
Roan Foods | 2026-05-01 | 18124 | 2026-04-02 | 0.079398 | 0.99944 | 18113.8944
Roan Foods | 2026-06-01 | 15908 | 2026-04-02 | 0.16427 | 0.99885 | 15889.6537
Roan Foods | 2026-07-01 | 16827 | 2026-04-02 | 0.24641 | 0.99827 | 16797.8991
Roan Foods | 2026-08-01 | 19405 | 2026-04-02 | 0.33128 | 0.99768 | 19359.8949
Roan Foods | 2026-09-01 | 19981 | 2026-04-02 | 0.41615 | 0.99708 | 19922.6745
Roan Foods | 2026-10-01 | 22401 | 2026-04-02 | 0.49829 | 0.99651 | 22322.7271
Roan Foods | 2026-11-01 | 20125 | 2026-04-02 | 0.58316 | 0.99591 | 20042.7268
Roan Foods | 2026-12-01 | 20771 | 2026-04-02 | 0.6653 | 0.99534 | 20674.154
SR Morula TF 1 | 2024-01-01 | 9307.8 | 2025-08-20 | 0 | 1 | 9307.8
SR Morula TF 1 | 2024-02-01 | 8001.9 | 2025-08-20 | 0 | 1 | 8001.9
SR Morula TF 1 | 2024-03-01 | 7803.9 | 2025-08-20 | 0 | 1 | 7803.9
SR Morula TF 1 | 2024-04-01 | 6785.1 | 2025-08-20 | 0 | 1 | 6785.1
SR Morula TF 1 | 2024-05-01 | 6244.2 | 2025-08-20 | 0 | 1 | 6244.2
SR Morula TF 1 | 2024-06-01 | 5524.2 | 2025-08-20 | 0 | 1 | 5524.2
SR Morula TF 1 | 2024-07-01 | 6086.7 | 2025-08-20 | 0 | 1 | 6086.7
SR Morula TF 1 | 2024-08-01 | 2298.1935 | 2025-08-20 | 0 | 1 | 2298.1935
SR Morula TF 1 | 2024-09-01 | 7864.2 | 2025-08-20 | 0 | 1 | 7864.2
SR Morula TF 1 | 2024-10-01 | 9007.2 | 2025-08-20 | 0 | 1 | 9007.2
SR Morula TF 1 | 2024-11-01 | 8999.1 | 2025-08-20 | 0 | 1 | 8999.1
SR Morula TF 1 | 2024-12-01 | 9241.2 | 2025-08-20 | 0 | 1 | 9241.2
SR Morula TF 1 | 2025-01-01 | 9307.8 | 2025-08-20 | 0 | 1 | 9307.8
SR Morula TF 1 | 2025-02-01 | 8001.9 | 2025-08-20 | 0 | 1 | 8001.9
SR Morula TF 1 | 2025-03-01 | 7803.9 | 2025-08-20 | 0 | 1 | 7803.9
SR Morula TF 1 | 2025-04-01 | 6785.1 | 2025-08-20 | 0 | 1 | 6785.1
SR Morula TF 1 | 2025-05-01 | 6244.2 | 2025-08-20 | 0 | 1 | 6244.2
SR Morula TF 1 | 2025-06-01 | 5524.2 | 2025-08-20 | 0 | 1 | 5524.2
SR Morula TF 1 | 2025-07-01 | 6086.7 | 2025-08-20 | 0 | 1 | 6086.7
SR Morula TF 1 | 2025-08-01 | 2298.1935 | 2025-08-20 | 0 | 1 | 2298.1935
SR Morula TF 1 | 2025-09-01 | 7864.2 | 2025-08-20 | 0.032854 | 0.99977 | 7862.3852
SR Morula TF 1 | 2025-10-01 | 9007.2 | 2025-08-20 | 0.11499 | 0.99919 | 8999.9273
SR Morula TF 1 | 2025-11-01 | 8999.1 | 2025-08-20 | 0.19986 | 0.9986 | 8986.4745
SR Morula TF 1 | 2025-12-01 | 9241.2 | 2025-08-20 | 0.282 | 0.99802 | 9222.9119
SR Morula TF 1 | 2026-01-01 | 9307.8 | 2025-08-20 | 0.36687 | 0.99743 | 9283.8434
SR Morula TF 1 | 2026-02-01 | 8001.9 | 2025-08-20 | 0.45175 | 0.99683 | 7976.5475
SR Morula TF 1 | 2026-03-01 | 7803.9 | 2025-08-20 | 0.52841 | 0.9963 | 7774.9868
SR Morula TF 1 | 2026-04-01 | 6785.1 | 2025-08-20 | 0.61328 | 0.9957 | 6755.9324
SR Morula TF 1 | 2026-05-01 | 6244.2 | 2025-08-20 | 0.69541 | 0.99513 | 6213.7714
SR Morula TF 1 | 2026-06-01 | 5524.2 | 2025-08-20 | 0.78029 | 0.99453 | 5494.0035
SR Morula TF 1 | 2026-07-01 | 6086.7 | 2025-08-20 | 0.86242 | 0.99396 | 6049.9371
SR Morula TF 1 | 2026-08-01 | 7124 | 2025-08-20 | 0.9473 | 0.99337 | 7076.7515
SR Morula TF 1 | 2026-09-01 | 7864.2 | 2025-08-20 | 1.0322 | 0.99278 | 7807.3861
SR Morula TF 1 | 2026-10-01 | 9007.2 | 2025-08-20 | 1.1143 | 0.9922 | 8936.9708
SR Morula TF 1 | 2026-11-01 | 8999.1 | 2025-08-20 | 1.1992 | 0.99161 | 8923.6121
SR Morula TF 1 | 2026-12-01 | 9241.2 | 2025-08-20 | 1.2813 | 0.99104 | 9158.3956
SR Morula TF 1 - Shoprite | 2024-01-01 | 28699.56 | 2025-08-20 | 0 | 1 | 28699.56
SR Morula TF 1 - Shoprite | 2024-02-01 | 24909.3 | 2025-08-20 | 0 | 1 | 24909.3
SR Morula TF 1 - Shoprite | 2024-03-01 | 24570 | 2025-08-20 | 0 | 1 | 24570
SR Morula TF 1 - Shoprite | 2024-04-01 | 21388.5 | 2025-08-20 | 0 | 1 | 21388.5
SR Morula TF 1 - Shoprite | 2024-05-01 | 19723.5 | 2025-08-20 | 0 | 1 | 19723.5
SR Morula TF 1 - Shoprite | 2024-06-01 | 17431.2 | 2025-08-20 | 0 | 1 | 17431.2
SR Morula TF 1 - Shoprite | 2024-07-01 | 19181.7 | 2025-08-20 | 0 | 1 | 19181.7
SR Morula TF 1 - Shoprite | 2024-08-01 | 7231.3548 | 2025-08-20 | 0 | 1 | 7231.3548
SR Morula TF 1 - Shoprite | 2024-09-01 | 24780.6 | 2025-08-20 | 0 | 1 | 24780.6
SR Morula TF 1 - Shoprite | 2024-10-01 | 28127.7 | 2025-08-20 | 0 | 1 | 28127.7
SR Morula TF 1 - Shoprite | 2024-11-01 | 28061.1 | 2025-08-20 | 0 | 1 | 28061.1
SR Morula TF 1 - Shoprite | 2024-12-01 | 28703.7 | 2025-08-20 | 0 | 1 | 28703.7
SR Morula TF 1 - Shoprite | 2025-01-01 | 28699.56 | 2025-08-20 | 0 | 1 | 28699.56
SR Morula TF 1 - Shoprite | 2025-02-01 | 24909.3 | 2025-08-20 | 0 | 1 | 24909.3
SR Morula TF 1 - Shoprite | 2025-03-01 | 24570 | 2025-08-20 | 0 | 1 | 24570
SR Morula TF 1 - Shoprite | 2025-04-01 | 21388.5 | 2025-08-20 | 0 | 1 | 21388.5
SR Morula TF 1 - Shoprite | 2025-05-01 | 19723.5 | 2025-08-20 | 0 | 1 | 19723.5
SR Morula TF 1 - Shoprite | 2025-06-01 | 17431.2 | 2025-08-20 | 0 | 1 | 17431.2
SR Morula TF 1 - Shoprite | 2025-07-01 | 19181.7 | 2025-08-20 | 0 | 1 | 19181.7
SR Morula TF 1 - Shoprite | 2025-08-01 | 7231.3548 | 2025-08-20 | 0 | 1 | 7231.3548
SR Morula TF 1 - Shoprite | 2025-09-01 | 24780.6 | 2025-08-20 | 0.032854 | 0.99977 | 24774.8816
SR Morula TF 1 - Shoprite | 2025-10-01 | 28127.7 | 2025-08-20 | 0.11499 | 0.99919 | 28104.9888
SR Morula TF 1 - Shoprite | 2025-11-01 | 28061.1 | 2025-08-20 | 0.19986 | 0.9986 | 28021.7309
SR Morula TF 1 - Shoprite | 2025-12-01 | 28703.7 | 2025-08-20 | 0.282 | 0.99802 | 28646.8962
SR Morula TF 1 - Shoprite | 2026-01-01 | 28699.56 | 2025-08-20 | 0.36687 | 0.99743 | 28625.6926
SR Morula TF 1 - Shoprite | 2026-02-01 | 24909.3 | 2025-08-20 | 0.45175 | 0.99683 | 24830.3797
SR Morula TF 1 - Shoprite | 2026-03-01 | 24570 | 2025-08-20 | 0.52841 | 0.9963 | 24478.9691
SR Morula TF 1 - Shoprite | 2026-04-01 | 21388.5 | 2025-08-20 | 0.61328 | 0.9957 | 21296.5556
SR Morula TF 1 - Shoprite | 2026-05-01 | 19723.5 | 2025-08-20 | 0.69541 | 0.99513 | 19627.3853
SR Morula TF 1 - Shoprite | 2026-06-01 | 17431.2 | 2025-08-20 | 0.78029 | 0.99453 | 17335.9171
SR Morula TF 1 - Shoprite | 2026-07-01 | 19181.7 | 2025-08-20 | 0.86242 | 0.99396 | 19065.8449
SR Morula TF 1 - Shoprite | 2026-08-01 | 22417 | 2025-08-20 | 0.9473 | 0.99337 | 22268.3237
SR Morula TF 1 - Shoprite | 2026-09-01 | 24780.6 | 2025-08-20 | 1.0322 | 0.99278 | 24601.5757
SR Morula TF 1 - Shoprite | 2026-10-01 | 28127.7 | 2025-08-20 | 1.1143 | 0.9922 | 27908.388
SR Morula TF 1 - Shoprite | 2026-11-01 | 28061.1 | 2025-08-20 | 1.1992 | 0.99161 | 27825.7126
SR Morula TF 1 - Shoprite | 2026-12-01 | 28703.7 | 2025-08-20 | 1.2813 | 0.99104 | 28446.5047
SR Morula TF 2 | 2024-01-01 | 9601.92 | 2025-08-20 | 0 | 1 | 9601.92
SR Morula TF 2 | 2024-02-01 | 8296.74 | 2025-08-20 | 0 | 1 | 8296.74
SR Morula TF 2 | 2024-03-01 | 8140.5 | 2025-08-20 | 0 | 1 | 8140.5
SR Morula TF 2 | 2024-04-01 | 7017.3 | 2025-08-20 | 0 | 1 | 7017.3
SR Morula TF 2 | 2024-05-01 | 6430.32 | 2025-08-20 | 0 | 1 | 6430.32
SR Morula TF 2 | 2024-06-01 | 5669.28 | 2025-08-20 | 0 | 1 | 5669.28
SR Morula TF 2 | 2024-07-01 | 6247.44 | 2025-08-20 | 0 | 1 | 6247.44
SR Morula TF 2 | 2024-08-01 | 2367.7839 | 2025-08-20 | 0 | 1 | 2367.7839
SR Morula TF 2 | 2024-09-01 | 8154 | 2025-08-20 | 0 | 1 | 8154
SR Morula TF 2 | 2024-10-01 | 9352.8 | 2025-08-20 | 0 | 1 | 9352.8
SR Morula TF 2 | 2024-11-01 | 9353.7 | 2025-08-20 | 0 | 1 | 9353.7
SR Morula TF 2 | 2024-12-01 | 9582.3 | 2025-08-20 | 0 | 1 | 9582.3
SR Morula TF 2 | 2025-01-01 | 9601.92 | 2025-08-20 | 0 | 1 | 9601.92
SR Morula TF 2 | 2025-02-01 | 8296.74 | 2025-08-20 | 0 | 1 | 8296.74
SR Morula TF 2 | 2025-03-01 | 8140.5 | 2025-08-20 | 0 | 1 | 8140.5
SR Morula TF 2 | 2025-04-01 | 7017.3 | 2025-08-20 | 0 | 1 | 7017.3
SR Morula TF 2 | 2025-05-01 | 6430.32 | 2025-08-20 | 0 | 1 | 6430.32
SR Morula TF 2 | 2025-06-01 | 5669.28 | 2025-08-20 | 0 | 1 | 5669.28
SR Morula TF 2 | 2025-07-01 | 6247.44 | 2025-08-20 | 0 | 1 | 6247.44
SR Morula TF 2 | 2025-08-01 | 2367.7839 | 2025-08-20 | 0 | 1 | 2367.7839
SR Morula TF 2 | 2025-09-01 | 8154 | 2025-08-20 | 0.032854 | 0.99977 | 8152.1184
SR Morula TF 2 | 2025-10-01 | 9352.8 | 2025-08-20 | 0.11499 | 0.99919 | 9345.2482
SR Morula TF 2 | 2025-11-01 | 9353.7 | 2025-08-20 | 0.19986 | 0.9986 | 9340.577
SR Morula TF 2 | 2025-12-01 | 9582.3 | 2025-08-20 | 0.282 | 0.99802 | 9563.3369
SR Morula TF 2 | 2026-01-01 | 9601.92 | 2025-08-20 | 0.36687 | 0.99743 | 9577.2064
SR Morula TF 2 | 2026-02-01 | 8296.74 | 2025-08-20 | 0.45175 | 0.99683 | 8270.4534
SR Morula TF 2 | 2026-03-01 | 8140.5 | 2025-08-20 | 0.52841 | 0.9963 | 8110.3398
SR Morula TF 2 | 2026-04-01 | 7017.3 | 2025-08-20 | 0.61328 | 0.9957 | 6987.1342
SR Morula TF 2 | 2026-05-01 | 6430.32 | 2025-08-20 | 0.69541 | 0.99513 | 6398.9844
SR Morula TF 2 | 2026-06-01 | 5669.28 | 2025-08-20 | 0.78029 | 0.99453 | 5638.2904
SR Morula TF 2 | 2026-07-01 | 6247.44 | 2025-08-20 | 0.86242 | 0.99396 | 6209.7062
SR Morula TF 2 | 2026-08-01 | 7340 | 2025-08-20 | 0.9473 | 0.99337 | 7291.3189
SR Morula TF 2 | 2026-09-01 | 8154 | 2025-08-20 | 1.0322 | 0.99278 | 8095.0925
SR Morula TF 2 | 2026-10-01 | 9352.8 | 2025-08-20 | 1.1143 | 0.9922 | 9279.8761
SR Morula TF 2 | 2026-11-01 | 9353.7 | 2025-08-20 | 1.1992 | 0.99161 | 9275.2375
SR Morula TF 2 | 2026-12-01 | 9582.3 | 2025-08-20 | 1.2813 | 0.99104 | 9496.4392
Sakhumnotho | 2024-01-01 | 5191.479 | null |  | 1 | 5191.479
Sakhumnotho | 2024-02-01 | 4656.5573 | null |  | 1 | 4656.5573
Sakhumnotho | 2024-03-01 | 5018.2719 | null |  | 1 | 5018.2719
Sakhumnotho | 2024-04-01 | 4498.5661 | null |  | 1 | 4498.5661
Sakhumnotho | 2024-05-01 | 4604.0626 | null |  | 1 | 4604.0626
Sakhumnotho | 2024-06-01 | 4265.4254 | null |  | 1 | 4265.4254
Sakhumnotho | 2024-07-01 | 4694.8505 | null |  | 1 | 4694.8505
Sakhumnotho | 2024-08-01 | 5144.2253 | null |  | 1 | 5144.2253
Sakhumnotho | 2024-09-01 | 5295.0313 | null |  | 1 | 5295.0313
Sakhumnotho | 2024-10-01 | 5391.4829 | null |  | 1 | 5391.4829
Sakhumnotho | 2024-11-01 | 5210.6678 | null |  | 1 | 5210.6678
Sakhumnotho | 2024-12-01 | 5439.6664 | null |  | 1 | 5439.6664
Sakhumnotho | 2025-01-01 | 5191.479 | null |  | 1 | 5191.479
Sakhumnotho | 2025-02-01 | 4656.5573 | null |  | 1 | 4656.5573
Sakhumnotho | 2025-03-01 | 5018.2719 | null |  | 1 | 5018.2719
Sakhumnotho | 2025-04-01 | 4498.5661 | null |  | 1 | 4498.5661
Sakhumnotho | 2025-05-01 | 4604.0626 | null |  | 1 | 4604.0626
Sakhumnotho | 2025-06-01 | 4265.4254 | null |  | 1 | 4265.4254
Sakhumnotho | 2025-07-01 | 4694.8505 | null |  | 1 | 4694.8505
Sakhumnotho | 2025-08-01 | 5144.2253 | null |  | 1 | 5144.2253
Sakhumnotho | 2025-09-01 | 5295.0313 | null |  | 1 | 5295.0313
Sakhumnotho | 2025-10-01 | 5391.4829 | null |  | 1 | 5391.4829
Sakhumnotho | 2025-11-01 | 5210.6678 | null |  | 1 | 5210.6678
Sakhumnotho | 2025-12-01 | 5439.6664 | null |  | 1 | 5439.6664
Sakhumnotho | 2026-01-01 | 5191.479 | null |  | 1 | 5191.479
Sakhumnotho | 2026-02-01 | 4656.5573 | null |  | 1 | 4656.5573
Sakhumnotho | 2026-03-01 | 5018.2719 | null |  | 1 | 5018.2719
Sakhumnotho | 2026-04-01 | 4498.5661 | null |  | 1 | 4498.5661
Sakhumnotho | 2026-05-01 | 4604.0626 | null |  | 1 | 4604.0626
Sakhumnotho | 2026-06-01 | 4265.4254 | null |  | 1 | 4265.4254
Sakhumnotho | 2026-07-01 | 4694.8505 | null |  | 1 | 4694.8505
Sakhumnotho | 2026-08-01 | 5144.2253 | null |  | 1 | 5144.2253
Sakhumnotho | 2026-09-01 | 5295.0313 | null |  | 1 | 5295.0313
Sakhumnotho | 2026-10-01 | 5391.4829 | null |  | 1 | 5391.4829
Sakhumnotho | 2026-11-01 | 5210.6678 | null |  | 1 | 5210.6678
Sakhumnotho | 2026-12-01 | 5439.6664 | null |  | 1 | 5439.6664
SaveMore Alldays - Store | 2024-01-01 | 23005.8 | 2023-07-03 | 0.49829 | 0.99651 | 22925.4139
SaveMore Alldays - Store | 2024-02-01 | 19888.2 | 2023-07-03 | 0.58316 | 0.99591 | 19806.8948
SaveMore Alldays - Store | 2024-03-01 | 21952.8 | 2023-07-03 | 0.66256 | 0.99536 | 21850.8641
SaveMore Alldays - Store | 2024-04-01 | 21444.3 | 2023-07-03 | 0.74743 | 0.99476 | 21332.0032
SaveMore Alldays - Store | 2024-05-01 | 20688.3 | 2023-07-03 | 0.82957 | 0.99419 | 20568.0916
SaveMore Alldays - Store | 2024-06-01 | 18646.2 | 2023-07-03 | 0.91444 | 0.9936 | 18526.8081
SaveMore Alldays - Store | 2024-07-01 | 19629.9 | 2023-07-03 | 0.99658 | 0.99302 | 19492.9593
SaveMore Alldays - Store | 2024-08-01 | 22998.6 | 2023-07-03 | 1.0815 | 0.99243 | 22824.5467
SaveMore Alldays - Store | 2024-09-01 | 22670.1 | 2023-07-03 | 1.1663 | 0.99184 | 22485.1231
SaveMore Alldays - Store | 2024-10-01 | 22045.5 | 2023-07-03 | 1.2485 | 0.99127 | 21853.0074
SaveMore Alldays - Store | 2024-11-01 | 22062.6 | 2023-07-03 | 1.3333 | 0.99068 | 21856.923
SaveMore Alldays - Store | 2024-12-01 | 23333.4 | 2023-07-03 | 1.4155 | 0.99011 | 23102.5427
SaveMore Alldays - Store | 2025-01-01 | 23005.8 | 2023-07-03 | 1.5003 | 0.98952 | 22764.6076
SaveMore Alldays - Store | 2025-02-01 | 19888.2 | 2023-07-03 | 1.5852 | 0.98893 | 19667.9629
SaveMore Alldays - Store | 2025-03-01 | 21952.8 | 2023-07-03 | 1.6619 | 0.98839 | 21698.0123
SaveMore Alldays - Store | 2025-04-01 | 21444.3 | 2023-07-03 | 1.7467 | 0.9878 | 21182.7811
SaveMore Alldays - Store | 2025-05-01 | 20688.3 | 2023-07-03 | 1.8289 | 0.98723 | 20424.2131
SaveMore Alldays - Store | 2025-06-01 | 18646.2 | 2023-07-03 | 1.9138 | 0.98665 | 18397.2089
SaveMore Alldays - Store | 2025-07-01 | 19629.9 | 2023-07-03 | 1.9959 | 0.98608 | 19356.6017
SaveMore Alldays - Store | 2025-08-01 | 22998.6 | 2023-07-03 | 2.0808 | 0.98549 | 22664.8839
SaveMore Alldays - Store | 2025-09-01 | 22670.1 | 2023-07-03 | 2.1656 | 0.9849 | 22327.8346
SaveMore Alldays - Store | 2025-10-01 | 22045.5 | 2023-07-03 | 2.2478 | 0.98433 | 21700.1407
SaveMore Alldays - Store | 2025-11-01 | 22062.6 | 2023-07-03 | 2.3326 | 0.98375 | 21704.0289
SaveMore Alldays - Store | 2025-12-01 | 23333.4 | 2023-07-03 | 2.4148 | 0.98318 | 22940.9352
SaveMore Alldays - Store | 2026-01-01 | 23005.8 | 2023-07-03 | 2.4997 | 0.98259 | 22605.364
SaveMore Alldays - Store | 2026-02-01 | 19888.2 | 2023-07-03 | 2.5845 | 0.98201 | 19530.381
SaveMore Alldays - Store | 2026-03-01 | 21952.8 | 2023-07-03 | 2.6612 | 0.98148 | 21546.2298
SaveMore Alldays - Store | 2026-04-01 | 21444.3 | 2023-07-03 | 2.7461 | 0.98089 | 21034.6027
SaveMore Alldays - Store | 2026-05-01 | 20688.3 | 2023-07-03 | 2.8282 | 0.98033 | 20281.3411
SaveMore Alldays - Store | 2026-06-01 | 18646.2 | 2023-07-03 | 2.9131 | 0.97974 | 18268.5162
SaveMore Alldays - Store | 2026-07-01 | 19629.9 | 2023-07-03 | 2.9952 | 0.97918 | 19221.1979
SaveMore Alldays - Store | 2026-08-01 | 22998.6 | 2023-07-03 | 3.0801 | 0.9786 | 22506.3379
SaveMore Alldays - Store | 2026-09-01 | 22670.1 | 2023-07-03 | 3.165 | 0.97801 | 22171.6464
SaveMore Alldays - Store | 2026-10-01 | 22045.5 | 2023-07-03 | 3.2471 | 0.97745 | 21548.3433
SaveMore Alldays - Store | 2026-11-01 | 22062.6 | 2023-07-03 | 3.332 | 0.97687 | 21552.2043
SaveMore Alldays - Store | 2026-12-01 | 23333.4 | 2023-07-03 | 3.4141 | 0.9763 | 22780.4582
Savemore Liquor Alldays | 2024-01-01 | 3308.455 | 2023-07-04 | 0.49555 | 0.99652 | 3296.9581
Savemore Liquor Alldays | 2024-02-01 | 2856.595 | 2023-07-04 | 0.58042 | 0.99593 | 2844.9716
Savemore Liquor Alldays | 2024-03-01 | 3155.625 | 2023-07-04 | 0.65982 | 0.99538 | 3141.0325
Savemore Liquor Alldays | 2024-04-01 | 3081.845 | 2023-07-04 | 0.7447 | 0.99478 | 3065.7654
Savemore Liquor Alldays | 2024-05-01 | 2972.875 | 2023-07-04 | 0.82683 | 0.99421 | 2955.6581
Savemore Liquor Alldays | 2024-06-01 | 2678.69 | 2023-07-04 | 0.9117 | 0.99362 | 2661.5895
Savemore Liquor Alldays | 2024-07-01 | 2819.025 | 2023-07-04 | 0.99384 | 0.99304 | 2799.413
Savemore Liquor Alldays | 2024-08-01 | 3304.375 | 2023-07-04 | 1.0787 | 0.99245 | 3279.4306
Savemore Liquor Alldays | 2024-09-01 | 3255.755 | 2023-07-04 | 1.1636 | 0.99186 | 3229.2517
Savemore Liquor Alldays | 2024-10-01 | 3170.245 | 2023-07-04 | 1.2457 | 0.99129 | 3142.6241
Savemore Liquor Alldays | 2024-11-01 | 3173.135 | 2023-07-04 | 1.3306 | 0.9907 | 3143.6141
Savemore Liquor Alldays | 2024-12-01 | 3354.185 | 2023-07-04 | 1.4127 | 0.99013 | 3321.0631
Savemore Liquor Alldays | 2025-01-01 | 3308.455 | 2023-07-04 | 1.4976 | 0.98954 | 3273.8322
Savemore Liquor Alldays | 2025-02-01 | 2856.595 | 2023-07-04 | 1.5825 | 0.98895 | 2825.0161
Savemore Liquor Alldays | 2025-03-01 | 3155.625 | 2023-07-04 | 1.6591 | 0.98841 | 3119.0603
Savemore Liquor Alldays | 2025-04-01 | 3081.845 | 2023-07-04 | 1.744 | 0.98782 | 3044.3196
Savemore Liquor Alldays | 2025-05-01 | 2972.875 | 2023-07-04 | 1.8261 | 0.98725 | 2934.9826
Savemore Liquor Alldays | 2025-06-01 | 2678.69 | 2023-07-04 | 1.911 | 0.98667 | 2642.9711
Savemore Liquor Alldays | 2025-07-01 | 2819.025 | 2023-07-04 | 1.9932 | 0.9861 | 2779.8304
Savemore Liquor Alldays | 2025-08-01 | 3304.375 | 2023-07-04 | 2.078 | 0.98551 | 3256.4902
Savemore Liquor Alldays | 2025-09-01 | 3255.755 | 2023-07-04 | 2.1629 | 0.98492 | 3206.6624
Savemore Liquor Alldays | 2025-10-01 | 3170.245 | 2023-07-04 | 2.245 | 0.98435 | 3120.6407
Savemore Liquor Alldays | 2025-11-01 | 3173.135 | 2023-07-04 | 2.3299 | 0.98377 | 3121.6238
Savemore Liquor Alldays | 2025-12-01 | 3354.185 | 2023-07-04 | 2.412 | 0.9832 | 3297.8315
Savemore Liquor Alldays | 2026-01-01 | 3308.455 | 2023-07-04 | 2.4969 | 0.98261 | 3250.931
Savemore Liquor Alldays | 2026-02-01 | 2856.595 | 2023-07-04 | 2.5818 | 0.98203 | 2805.2545
Savemore Liquor Alldays | 2026-03-01 | 3155.625 | 2023-07-04 | 2.6585 | 0.9815 | 3097.2418
Savemore Liquor Alldays | 2026-04-01 | 3081.845 | 2023-07-04 | 2.7433 | 0.98091 | 3023.0239
Savemore Liquor Alldays | 2026-05-01 | 2972.875 | 2023-07-04 | 2.8255 | 0.98035 | 2914.4517
Savemore Liquor Alldays | 2026-06-01 | 2678.69 | 2023-07-04 | 2.9103 | 0.97976 | 2624.4829
Savemore Liquor Alldays | 2026-07-01 | 2819.025 | 2023-07-04 | 2.9925 | 0.9792 | 2760.3849
Savemore Liquor Alldays | 2026-08-01 | 3304.375 | 2023-07-04 | 3.0773 | 0.97861 | 3233.7103
Savemore Liquor Alldays | 2026-09-01 | 3255.755 | 2023-07-04 | 3.1622 | 0.97803 | 3184.2311
Savemore Liquor Alldays | 2026-10-01 | 3170.245 | 2023-07-04 | 3.2444 | 0.97747 | 3098.8112
Savemore Liquor Alldays | 2026-11-01 | 3173.135 | 2023-07-04 | 3.3292 | 0.97688 | 3099.7874
Savemore Liquor Alldays | 2026-12-01 | 3354.185 | 2023-07-04 | 3.4114 | 0.97632 | 3274.7624
Saverite Durban | 2024-01-01 | 12489.555 | 2023-07-04 | 0.49555 | 0.99652 | 12446.1538
Saverite Durban | 2024-02-01 | 10877.69 | 2023-07-04 | 0.58042 | 0.99593 | 10833.4291
Saverite Durban | 2024-03-01 | 10897.355 | 2023-07-04 | 0.65982 | 0.99538 | 10846.9627
Saverite Durban | 2024-04-01 | 8757.955 | 2023-07-04 | 0.7447 | 0.99478 | 8712.26
Saverite Durban | 2024-05-01 | 7449.425 | 2023-07-04 | 0.82683 | 0.99421 | 7406.2829
Saverite Durban | 2024-06-01 | 6752.695 | 2023-07-04 | 0.9117 | 0.99362 | 6709.5864
Saverite Durban | 2024-07-01 | 7274.245 | 2023-07-04 | 0.99384 | 0.99304 | 7223.6379
Saverite Durban | 2024-08-01 | 8568.715 | 2023-07-04 | 1.0787 | 0.99245 | 8504.0306
Saverite Durban | 2024-09-01 | 9196 | 2023-07-04 | 1.1636 | 0.99186 | 9121.1406
Saverite Durban | 2024-10-01 | 10753.525 | 2023-07-04 | 1.2457 | 0.99129 | 10659.8345
Saverite Durban | 2024-11-01 | 11159.27 | 2023-07-04 | 1.3306 | 0.9907 | 11055.4511
Saverite Durban | 2024-12-01 | 12687.82 | 2023-07-04 | 1.4127 | 0.99013 | 12562.5302
Saverite Durban | 2025-01-01 | 12489.555 | 2023-07-04 | 1.4976 | 0.98954 | 12358.8524
Saverite Durban | 2025-02-01 | 10877.69 | 2023-07-04 | 1.5825 | 0.98895 | 10757.44
Saverite Durban | 2025-03-01 | 10897.355 | 2023-07-04 | 1.6591 | 0.98841 | 10771.0857
Saverite Durban | 2025-04-01 | 8757.955 | 2023-07-04 | 1.744 | 0.98782 | 8651.3158
Saverite Durban | 2025-05-01 | 7449.425 | 2023-07-04 | 1.8261 | 0.98725 | 7354.4743
Saverite Durban | 2025-06-01 | 6752.695 | 2023-07-04 | 1.911 | 0.98667 | 6662.6513
Saverite Durban | 2025-07-01 | 7274.245 | 2023-07-04 | 1.9932 | 0.9861 | 7173.1069
Saverite Durban | 2025-08-01 | 8568.715 | 2023-07-04 | 2.078 | 0.98551 | 8444.5429
Saverite Durban | 2025-09-01 | 9196 | 2023-07-04 | 2.1629 | 0.98492 | 9057.3361
Saverite Durban | 2025-10-01 | 10753.525 | 2023-07-04 | 2.245 | 0.98435 | 10585.2665
Saverite Durban | 2025-11-01 | 11159.27 | 2023-07-04 | 2.3299 | 0.98377 | 10978.1158
Saverite Durban | 2025-12-01 | 12687.82 | 2023-07-04 | 2.412 | 0.9832 | 12474.6524
Saverite Durban | 2026-01-01 | 12489.555 | 2023-07-04 | 2.4969 | 0.98261 | 12272.3995
Saverite Durban | 2026-02-01 | 10877.69 | 2023-07-04 | 2.5818 | 0.98203 | 10682.1893
Saverite Durban | 2026-03-01 | 10897.355 | 2023-07-04 | 2.6585 | 0.9815 | 10695.7396
Saverite Durban | 2026-04-01 | 8757.955 | 2023-07-04 | 2.7433 | 0.98091 | 8590.7979
Saverite Durban | 2026-05-01 | 7449.425 | 2023-07-04 | 2.8255 | 0.98035 | 7303.0281
Saverite Durban | 2026-06-01 | 6752.695 | 2023-07-04 | 2.9103 | 0.97976 | 6616.0446
Saverite Durban | 2026-07-01 | 7274.245 | 2023-07-04 | 2.9925 | 0.9792 | 7122.9294
Saverite Durban | 2026-08-01 | 8568.715 | 2023-07-04 | 3.0773 | 0.97861 | 8385.4715
Saverite Durban | 2026-09-01 | 9196 | 2023-07-04 | 3.1622 | 0.97803 | 8993.978
Saverite Durban | 2026-10-01 | 10753.525 | 2023-07-04 | 3.2444 | 0.97747 | 10511.2202
Saverite Durban | 2026-11-01 | 11159.27 | 2023-07-04 | 3.3292 | 0.97688 | 10901.3214
Saverite Durban | 2026-12-01 | 12687.82 | 2023-07-04 | 3.4114 | 0.97632 | 12387.3894
Saverite PMB | 2024-01-01 | 13218.015 | 2020-11-24 | 3.102 | 0.97845 | 12933.1065
Saverite PMB | 2024-02-01 | 10966.135 | 2020-11-24 | 3.1869 | 0.97786 | 10723.3696
Saverite PMB | 2024-03-01 | 11441.135 | 2020-11-24 | 3.2663 | 0.97732 | 11181.616
Saverite PMB | 2024-04-01 | 10004.07 | 2020-11-24 | 3.3511 | 0.97673 | 9771.3205
Saverite PMB | 2024-05-01 | 8979.59 | 2020-11-24 | 3.4333 | 0.97617 | 8765.6166
Saverite PMB | 2024-06-01 | 7800.26 | 2020-11-24 | 3.5181 | 0.97559 | 7609.8503
Saverite PMB | 2024-07-01 | 8635.69 | 2020-11-24 | 3.6003 | 0.97503 | 8420.0274
Saverite PMB | 2024-08-01 | 9829.935 | 2020-11-24 | 3.6851 | 0.97445 | 9578.7354
Saverite PMB | 2024-09-01 | 10568.94 | 2020-11-24 | 3.77 | 0.97386 | 10292.7171
Saverite PMB | 2024-10-01 | 11606.34 | 2020-11-24 | 3.8522 | 0.9733 | 11296.4847
Saverite PMB | 2024-11-01 | 12483.285 | 2020-11-24 | 3.937 | 0.97272 | 12142.7761
Saverite PMB | 2024-12-01 | 13393.575 | 2020-11-24 | 4.0192 | 0.97216 | 13020.7212
Saverite PMB | 2025-01-01 | 13218.015 | 2020-11-24 | 4.104 | 0.97158 | 12842.3895
Saverite PMB | 2025-02-01 | 10966.135 | 2020-11-24 | 4.1889 | 0.971 | 10648.1524
Saverite PMB | 2025-03-01 | 11441.135 | 2020-11-24 | 4.2656 | 0.97048 | 11103.3981
Saverite PMB | 2025-04-01 | 10004.07 | 2020-11-24 | 4.3504 | 0.9699 | 9702.9679
Saverite PMB | 2025-05-01 | 8979.59 | 2020-11-24 | 4.4326 | 0.96934 | 8704.2991
Saverite PMB | 2025-06-01 | 7800.26 | 2020-11-24 | 4.5175 | 0.96876 | 7556.6177
Saverite PMB | 2025-07-01 | 8635.69 | 2020-11-24 | 4.5996 | 0.96821 | 8361.1274
Saverite PMB | 2025-08-01 | 9829.935 | 2020-11-24 | 4.6845 | 0.96763 | 9511.73
Saverite PMB | 2025-09-01 | 10568.94 | 2020-11-24 | 4.7693 | 0.96705 | 10220.7172
Saverite PMB | 2025-10-01 | 11606.34 | 2020-11-24 | 4.8515 | 0.96649 | 11217.4632
Saverite PMB | 2025-11-01 | 12483.285 | 2020-11-24 | 4.9363 | 0.96592 | 12057.8346
Saverite PMB | 2025-12-01 | 13393.575 | 2020-11-24 | 5.0185 | 0.96536 | 12929.6383
Saverite PMB | 2026-01-01 | 13218.015 | 2020-11-24 | 5.1034 | 0.96479 | 12752.5541
Saverite PMB | 2026-02-01 | 10966.135 | 2020-11-24 | 5.1882 | 0.96421 | 10573.6662
Saverite PMB | 2026-03-01 | 11441.135 | 2020-11-24 | 5.2649 | 0.96369 | 11025.7273
Saverite PMB | 2026-04-01 | 10004.07 | 2020-11-24 | 5.3498 | 0.96312 | 9635.0935
Saverite PMB | 2026-05-01 | 8979.59 | 2020-11-24 | 5.4319 | 0.96256 | 8643.4106
Saverite PMB | 2026-06-01 | 7800.26 | 2020-11-24 | 5.5168 | 0.96199 | 7503.7574
Saverite PMB | 2026-07-01 | 8635.69 | 2020-11-24 | 5.5989 | 0.96143 | 8302.6394
Saverite PMB | 2026-08-01 | 9829.935 | 2020-11-24 | 5.6838 | 0.96086 | 9445.1933
Saverite PMB | 2026-09-01 | 10568.94 | 2020-11-24 | 5.7687 | 0.96029 | 10149.221
Saverite PMB | 2026-10-01 | 11606.34 | 2020-11-24 | 5.8508 | 0.95973 | 11138.9945
Saverite PMB | 2026-11-01 | 12483.285 | 2020-11-24 | 5.9357 | 0.95916 | 11973.4874
Saverite PMB | 2026-12-01 | 13393.575 | 2020-11-24 | 6.0178 | 0.95861 | 12839.1926
Secunda Plaza Shops | 2024-01-01 | 4359.6 | 2022-07-28 | 1.4292 | 0.99001 | 4316.0517
Secunda Plaza Shops | 2024-02-01 | 3825.9 | 2022-07-28 | 1.514 | 0.98942 | 3785.4253
Secunda Plaza Shops | 2024-03-01 | 4077 | 2022-07-28 | 1.5934 | 0.98887 | 4031.6197
Secunda Plaza Shops | 2024-04-01 | 3573.9 | 2022-07-28 | 1.6783 | 0.98828 | 3532.0132
Secunda Plaza Shops | 2024-05-01 | 3623.4 | 2022-07-28 | 1.7604 | 0.98771 | 3578.8675
Secunda Plaza Shops | 2024-06-01 | 3360.6 | 2022-07-28 | 1.8453 | 0.98712 | 3317.319
Secunda Plaza Shops | 2024-07-01 | 3665.7 | 2022-07-28 | 1.9274 | 0.98655 | 3616.4025
Secunda Plaza Shops | 2024-08-01 | 4104 | 2022-07-28 | 2.0123 | 0.98596 | 4046.3949
Secunda Plaza Shops | 2024-09-01 | 4274.1 | 2022-07-28 | 2.0972 | 0.98538 | 4211.5956
Secunda Plaza Shops | 2024-10-01 | 4289.4 | 2022-07-28 | 2.1793 | 0.98481 | 4224.2339
Secunda Plaza Shops | 2024-11-01 | 4249.8 | 2022-07-28 | 2.2642 | 0.98422 | 4182.741
Secunda Plaza Shops | 2024-12-01 | 4446 | 2022-07-28 | 2.3463 | 0.98365 | 4373.3211
Secunda Plaza Shops | 2025-01-01 | 4359.6 | 2022-07-28 | 2.4312 | 0.98307 | 4285.7775
Secunda Plaza Shops | 2025-02-01 | 3825.9 | 2022-07-28 | 2.5161 | 0.98248 | 3758.8731
Secunda Plaza Shops | 2025-03-01 | 4077 | 2022-07-28 | 2.5927 | 0.98195 | 4003.4176
Secunda Plaza Shops | 2025-04-01 | 3573.9 | 2022-07-28 | 2.6776 | 0.98137 | 3507.3059
Secunda Plaza Shops | 2025-05-01 | 3623.4 | 2022-07-28 | 2.7598 | 0.9808 | 3553.8325
Secunda Plaza Shops | 2025-06-01 | 3360.6 | 2022-07-28 | 2.8446 | 0.98022 | 3294.1136
Secunda Plaza Shops | 2025-07-01 | 3665.7 | 2022-07-28 | 2.9268 | 0.97965 | 3591.1049
Secunda Plaza Shops | 2025-08-01 | 4104 | 2022-07-28 | 3.0116 | 0.97907 | 4018.0894
Secunda Plaza Shops | 2025-09-01 | 4274.1 | 2022-07-28 | 3.0965 | 0.97848 | 4182.1345
Secunda Plaza Shops | 2025-10-01 | 4289.4 | 2022-07-28 | 3.1786 | 0.97792 | 4194.6844
Secunda Plaza Shops | 2025-11-01 | 4249.8 | 2022-07-28 | 3.2635 | 0.97734 | 4153.4818
Secunda Plaza Shops | 2025-12-01 | 4446 | 2022-07-28 | 3.3457 | 0.97677 | 4342.7287
Secunda Plaza Shops | 2026-01-01 | 4359.6 | 2022-07-28 | 3.4305 | 0.97619 | 4255.7975
Secunda Plaza Shops | 2026-02-01 | 3825.9 | 2022-07-28 | 3.5154 | 0.97561 | 3732.5789
Secunda Plaza Shops | 2026-03-01 | 4077 | 2022-07-28 | 3.5921 | 0.97508 | 3975.4128
Secunda Plaza Shops | 2026-04-01 | 3573.9 | 2022-07-28 | 3.6769 | 0.9745 | 3482.7715
Secunda Plaza Shops | 2026-05-01 | 3623.4 | 2022-07-28 | 3.7591 | 0.97394 | 3528.9727
Secunda Plaza Shops | 2026-06-01 | 3360.6 | 2022-07-28 | 3.8439 | 0.97336 | 3271.0705
Secunda Plaza Shops | 2026-07-01 | 3665.7 | 2022-07-28 | 3.9261 | 0.9728 | 3565.9843
Secunda Plaza Shops | 2026-08-01 | 4104 | 2022-07-28 | 4.011 | 0.97222 | 3989.982
Secunda Plaza Shops | 2026-09-01 | 4274.1 | 2022-07-28 | 4.0958 | 0.97164 | 4152.8796
Secunda Plaza Shops | 2026-10-01 | 4289.4 | 2022-07-28 | 4.178 | 0.97108 | 4165.3416
Secunda Plaza Shops | 2026-11-01 | 4249.8 | 2022-07-28 | 4.2628 | 0.9705 | 4124.4272
Secunda Plaza Shops | 2026-12-01 | 4446 | 2022-07-28 | 4.345 | 0.96994 | 4312.3503
Secunda Plaza choppies | 2024-01-01 | 23065.02 | 2022-07-28 | 1.4292 | 0.99001 | 22834.6221
Secunda Plaza choppies | 2024-02-01 | 20354.85 | 2022-07-28 | 1.514 | 0.98942 | 20139.5134
Secunda Plaza choppies | 2024-03-01 | 21716.37 | 2022-07-28 | 1.5934 | 0.98887 | 21474.6491
Secunda Plaza choppies | 2024-04-01 | 18847.89 | 2022-07-28 | 1.6783 | 0.98828 | 18626.9888
Secunda Plaza choppies | 2024-05-01 | 18700.92 | 2022-07-28 | 1.7604 | 0.98771 | 18471.081
Secunda Plaza choppies | 2024-06-01 | 17164.44 | 2022-07-28 | 1.8453 | 0.98712 | 16943.38
Secunda Plaza choppies | 2024-07-01 | 18821.97 | 2022-07-28 | 1.9274 | 0.98655 | 18568.846
Secunda Plaza choppies | 2024-08-01 | 21497.67 | 2022-07-28 | 2.0123 | 0.98596 | 21195.9215
Secunda Plaza choppies | 2024-09-01 | 22688.37 | 2022-07-28 | 2.0972 | 0.98538 | 22356.5754
Secunda Plaza choppies | 2024-10-01 | 22841.55 | 2022-07-28 | 2.1793 | 0.98481 | 22494.5329
Secunda Plaza choppies | 2024-11-01 | 22507.92 | 2022-07-28 | 2.2642 | 0.98422 | 22152.76
Secunda Plaza choppies | 2024-12-01 | 23494.59 | 2022-07-28 | 2.3463 | 0.98365 | 23110.5231
Secunda Plaza choppies | 2025-01-01 | 23065.02 | 2022-07-28 | 2.4312 | 0.98307 | 22674.4527
Secunda Plaza choppies | 2025-02-01 | 20354.85 | 2022-07-28 | 2.5161 | 0.98248 | 19998.2483
Secunda Plaza choppies | 2025-03-01 | 21716.37 | 2022-07-28 | 2.5927 | 0.98195 | 21324.4291
Secunda Plaza choppies | 2025-04-01 | 18847.89 | 2022-07-28 | 2.6776 | 0.98137 | 18496.6889
Secunda Plaza choppies | 2025-05-01 | 18700.92 | 2022-07-28 | 2.7598 | 0.9808 | 18341.8716
Secunda Plaza choppies | 2025-06-01 | 17164.44 | 2022-07-28 | 2.8446 | 0.98022 | 16824.8573
Secunda Plaza choppies | 2025-07-01 | 18821.97 | 2022-07-28 | 2.9268 | 0.97965 | 18438.9528
Secunda Plaza choppies | 2025-08-01 | 21497.67 | 2022-07-28 | 3.0116 | 0.97907 | 21047.6513
Secunda Plaza choppies | 2025-09-01 | 22688.37 | 2022-07-28 | 3.0965 | 0.97848 | 22200.1861
Secunda Plaza choppies | 2025-10-01 | 22841.55 | 2022-07-28 | 3.1786 | 0.97792 | 22337.1786
Secunda Plaza choppies | 2025-11-01 | 22507.92 | 2022-07-28 | 3.2635 | 0.97734 | 21997.7965
Secunda Plaza choppies | 2025-12-01 | 23494.59 | 2022-07-28 | 3.3457 | 0.97677 | 22948.8598
Secunda Plaza choppies | 2026-01-01 | 23065.02 | 2022-07-28 | 3.4305 | 0.97619 | 22515.8398
Secunda Plaza choppies | 2026-02-01 | 20354.85 | 2022-07-28 | 3.5154 | 0.97561 | 19858.3561
Secunda Plaza choppies | 2026-03-01 | 21716.37 | 2022-07-28 | 3.5921 | 0.97508 | 21175.2599
Secunda Plaza choppies | 2026-04-01 | 18847.89 | 2022-07-28 | 3.6769 | 0.9745 | 18367.3003
Secunda Plaza choppies | 2026-05-01 | 18700.92 | 2022-07-28 | 3.7591 | 0.97394 | 18213.5661
Secunda Plaza choppies | 2026-06-01 | 17164.44 | 2022-07-28 | 3.8439 | 0.97336 | 16707.1636
Secunda Plaza choppies | 2026-07-01 | 18821.97 | 2022-07-28 | 3.9261 | 0.9728 | 18309.9681
Secunda Plaza choppies | 2026-08-01 | 21497.67 | 2022-07-28 | 4.011 | 0.97222 | 20900.4182
Secunda Plaza choppies | 2026-09-01 | 22688.37 | 2022-07-28 | 4.0958 | 0.97164 | 22044.8908
Secunda Plaza choppies | 2026-10-01 | 22841.55 | 2022-07-28 | 4.178 | 0.97108 | 22180.925
Secunda Plaza choppies | 2026-11-01 | 22507.92 | 2022-07-28 | 4.2628 | 0.9705 | 21843.9169
Secunda Plaza choppies | 2026-12-01 | 23494.59 | 2022-07-28 | 4.345 | 0.96994 | 22788.3273
Shoprite Dube | 2024-01-01 | 23724 | 2025-01-09 | 0 | 1 | 23724
Shoprite Dube | 2024-02-01 | 20448 | 2025-01-09 | 0 | 1 | 20448
Shoprite Dube | 2024-03-01 | 19986.3 | 2025-01-09 | 0 | 1 | 19986.3
Shoprite Dube | 2024-04-01 | 17181.9 | 2025-01-09 | 0 | 1 | 17181.9
Shoprite Dube | 2024-05-01 | 15369.3 | 2025-01-09 | 0 | 1 | 15369.3
Shoprite Dube | 2024-06-01 | 13381.2 | 2025-01-09 | 0 | 1 | 13381.2
Shoprite Dube | 2024-07-01 | 15023.7 | 2025-01-09 | 0 | 1 | 15023.7
Shoprite Dube | 2024-08-01 | 18071.1 | 2025-01-09 | 0 | 1 | 18071.1
Shoprite Dube | 2024-09-01 | 20545.2 | 2025-01-09 | 0 | 1 | 20545.2
Shoprite Dube | 2024-10-01 | 23411.7 | 2025-01-09 | 0 | 1 | 23411.7
Shoprite Dube | 2024-11-01 | 23583.6 | 2025-01-09 | 0 | 1 | 23583.6
Shoprite Dube | 2024-12-01 | 24027.3 | 2025-01-09 | 0 | 1 | 24027.3
Shoprite Dube | 2025-01-01 | 23724 | 2025-01-09 | 0 | 1 | 23724
Shoprite Dube | 2025-02-01 | 20448 | 2025-01-09 | 0.062971 | 0.99956 | 20438.957
Shoprite Dube | 2025-03-01 | 19986.3 | 2025-01-09 | 0.13963 | 0.99902 | 19966.7061
Shoprite Dube | 2025-04-01 | 17181.9 | 2025-01-09 | 0.2245 | 0.99842 | 17154.8246
Shoprite Dube | 2025-05-01 | 15369.3 | 2025-01-09 | 0.30664 | 0.99785 | 15336.2298
Shoprite Dube | 2025-06-01 | 13381.2 | 2025-01-09 | 0.39151 | 0.99725 | 13344.4492
Shoprite Dube | 2025-07-01 | 15023.7 | 2025-01-09 | 0.47365 | 0.99668 | 14973.7963
Shoprite Dube | 2025-08-01 | 18071.1 | 2025-01-09 | 0.55852 | 0.99608 | 18000.3388
Shoprite Dube | 2025-09-01 | 20545.2 | 2025-01-09 | 0.64339 | 0.99549 | 20452.5534
Shoprite Dube | 2025-10-01 | 23411.7 | 2025-01-09 | 0.72553 | 0.99492 | 23292.6841
Shoprite Dube | 2025-11-01 | 23583.6 | 2025-01-09 | 0.8104 | 0.99432 | 23449.7253
Shoprite Dube | 2025-12-01 | 24027.3 | 2025-01-09 | 0.89254 | 0.99375 | 23877.1262
Shoprite Dube | 2026-01-01 | 23724 | 2025-01-09 | 0.97741 | 0.99316 | 23561.6702
Shoprite Dube | 2026-02-01 | 20448 | 2025-01-09 | 1.0623 | 0.99257 | 20295.9818
Shoprite Dube | 2026-03-01 | 19986.3 | 2025-01-09 | 1.1389 | 0.99203 | 19827.0344
Shoprite Dube | 2026-04-01 | 17181.9 | 2025-01-09 | 1.2238 | 0.99144 | 17034.8227
Shoprite Dube | 2026-05-01 | 15369.3 | 2025-01-09 | 1.306 | 0.99087 | 15228.9494
Shoprite Dube | 2026-06-01 | 13381.2 | 2025-01-09 | 1.3908 | 0.99028 | 13251.1018
Shoprite Dube | 2026-07-01 | 15023.7 | 2025-01-09 | 1.473 | 0.98971 | 14869.0512
Shoprite Dube | 2026-08-01 | 18071.1 | 2025-01-09 | 1.5578 | 0.98912 | 17874.4223
Shoprite Dube | 2026-09-01 | 20545.2 | 2025-01-09 | 1.6427 | 0.98853 | 20309.4832
Shoprite Dube | 2026-10-01 | 23411.7 | 2025-01-09 | 1.7248 | 0.98796 | 23129.7465
Shoprite Dube | 2026-11-01 | 23583.6 | 2025-01-09 | 1.8097 | 0.98737 | 23285.6892
Shoprite Dube | 2026-12-01 | 24027.3 | 2025-01-09 | 1.8919 | 0.9868 | 23710.1003
Shoprite Ekhaya | 2024-01-01 | 28380.6 | 2026-02-15 | 0 | 1 | 28380.6
Shoprite Ekhaya | 2024-02-01 | 24379.2 | 2026-02-15 | 0 | 1 | 24379.2
Shoprite Ekhaya | 2024-03-01 | 23351.4 | 2026-02-15 | 0 | 1 | 23351.4
Shoprite Ekhaya | 2024-04-01 | 19887.3 | 2026-02-15 | 0 | 1 | 19887.3
Shoprite Ekhaya | 2024-05-01 | 17745.3 | 2026-02-15 | 0 | 1 | 17745.3
Shoprite Ekhaya | 2024-06-01 | 15502.5 | 2026-02-15 | 0 | 1 | 15502.5
Shoprite Ekhaya | 2024-07-01 | 17358.3 | 2026-02-15 | 0 | 1 | 17358.3
Shoprite Ekhaya | 2024-08-01 | 20842.2 | 2026-02-15 | 0 | 1 | 20842.2
Shoprite Ekhaya | 2024-09-01 | 23841 | 2026-02-15 | 0 | 1 | 23841
Shoprite Ekhaya | 2024-10-01 | 27285.3 | 2026-02-15 | 0 | 1 | 27285.3
Shoprite Ekhaya | 2024-11-01 | 27841.5 | 2026-02-15 | 0 | 1 | 27841.5
Shoprite Ekhaya | 2024-12-01 | 28779.3 | 2026-02-15 | 0 | 1 | 28779.3
Shoprite Ekhaya | 2025-01-01 | 28380.6 | 2026-02-15 | 0 | 1 | 28380.6
Shoprite Ekhaya | 2025-02-01 | 24379.2 | 2026-02-15 | 0 | 1 | 24379.2
Shoprite Ekhaya | 2025-03-01 | 23351.4 | 2026-02-15 | 0 | 1 | 23351.4
Shoprite Ekhaya | 2025-04-01 | 19887.3 | 2026-02-15 | 0 | 1 | 19887.3
Shoprite Ekhaya | 2025-05-01 | 17745.3 | 2026-02-15 | 0 | 1 | 17745.3
Shoprite Ekhaya | 2025-06-01 | 15502.5 | 2026-02-15 | 0 | 1 | 15502.5
Shoprite Ekhaya | 2025-07-01 | 17358.3 | 2026-02-15 | 0 | 1 | 17358.3
Shoprite Ekhaya | 2025-08-01 | 20842.2 | 2026-02-15 | 0 | 1 | 20842.2
Shoprite Ekhaya | 2025-09-01 | 23841 | 2026-02-15 | 0 | 1 | 23841
Shoprite Ekhaya | 2025-10-01 | 27285.3 | 2026-02-15 | 0 | 1 | 27285.3
Shoprite Ekhaya | 2025-11-01 | 27841.5 | 2026-02-15 | 0 | 1 | 27841.5
Shoprite Ekhaya | 2025-12-01 | 28779.3 | 2026-02-15 | 0 | 1 | 28779.3
Shoprite Ekhaya | 2026-01-01 | 28380.6 | 2026-02-15 | 0 | 1 | 28380.6
Shoprite Ekhaya | 2026-02-01 | 24379.2 | 2026-02-15 | 0 | 1 | 24379.2
Shoprite Ekhaya | 2026-03-01 | 23351.4 | 2026-02-15 | 0.03833 | 0.99973 | 23345.1134
Shoprite Ekhaya | 2026-04-01 | 19887.3 | 2026-02-15 | 0.1232 | 0.99913 | 19870.0959
Shoprite Ekhaya | 2026-05-01 | 17745.3 | 2026-02-15 | 0.20534 | 0.99856 | 17719.7222
Shoprite Ekhaya | 2026-06-01 | 15502.5 | 2026-02-15 | 0.29021 | 0.99796 | 15470.9283
Shoprite Ekhaya | 2026-07-01 | 17358.3 | 2026-02-15 | 0.37235 | 0.99739 | 17312.957
Shoprite Ekhaya | 2026-08-01 | 20842.2 | 2026-02-15 | 0.45722 | 0.99679 | 20775.3664
Shoprite Ekhaya | 2026-09-01 | 23841 | 2026-02-15 | 0.54209 | 0.9962 | 23750.386
Shoprite Ekhaya | 2026-10-01 | 27285.3 | 2026-02-15 | 0.62423 | 0.99562 | 27165.9166
Shoprite Ekhaya | 2026-11-01 | 27841.5 | 2026-02-15 | 0.7091 | 0.99503 | 27703.1614
Shoprite Ekhaya | 2026-12-01 | 28779.3 | 2026-02-15 | 0.79124 | 0.99446 | 28619.7841
Shoprite Hillbrow | 2024-01-01 | 20564.65 | 2024-10-25 | 0 | 1 | 20564.65
Shoprite Hillbrow | 2024-02-01 | 17491.4 | 2024-10-25 | 0 | 1 | 17491.4
Shoprite Hillbrow | 2024-03-01 | 18246.65 | 2024-10-25 | 0 | 1 | 18246.65
Shoprite Hillbrow | 2024-04-01 | 15297.85 | 2024-10-25 | 0 | 1 | 15297.85
Shoprite Hillbrow | 2024-05-01 | 14953 | 2024-10-25 | 0 | 1 | 14953
Shoprite Hillbrow | 2024-06-01 | 13275.3 | 2024-10-25 | 0 | 1 | 13275.3
Shoprite Hillbrow | 2024-07-01 | 14678.45 | 2024-10-25 | 0 | 1 | 14678.45
Shoprite Hillbrow | 2024-08-01 | 17062.95 | 2024-10-25 | 0 | 1 | 17062.95
Shoprite Hillbrow | 2024-09-01 | 18937.3 | 2024-10-25 | 0 | 1 | 18937.3
Shoprite Hillbrow | 2024-10-01 | 20481.05 | 2024-10-25 | 0 | 1 | 20481.05
Shoprite Hillbrow | 2024-11-01 | 20366.1 | 2024-10-25 | 0.019165 | 0.99987 | 20363.3584
Shoprite Hillbrow | 2024-12-01 | 21890.85 | 2024-10-25 | 0.1013 | 0.99929 | 21875.2781
Shoprite Hillbrow | 2025-01-01 | 20564.65 | 2024-10-25 | 0.18617 | 0.99869 | 20537.7731
Shoprite Hillbrow | 2025-02-01 | 17491.4 | 2024-10-25 | 0.27105 | 0.9981 | 17458.128
Shoprite Hillbrow | 2025-03-01 | 18246.65 | 2024-10-25 | 0.34771 | 0.99756 | 18202.1368
Shoprite Hillbrow | 2025-04-01 | 15297.85 | 2024-10-25 | 0.43258 | 0.99697 | 15251.4348
Shoprite Hillbrow | 2025-05-01 | 14953 | 2024-10-25 | 0.51472 | 0.99639 | 14899.0323
Shoprite Hillbrow | 2025-06-01 | 13275.3 | 2024-10-25 | 0.59959 | 0.9958 | 13219.5036
Shoprite Hillbrow | 2025-07-01 | 14678.45 | 2024-10-25 | 0.68172 | 0.99522 | 14608.3251
Shoprite Hillbrow | 2025-08-01 | 17062.95 | 2024-10-25 | 0.7666 | 0.99463 | 16971.312
Shoprite Hillbrow | 2025-09-01 | 18937.3 | 2024-10-25 | 0.85147 | 0.99404 | 18824.3692
Shoprite Hillbrow | 2025-10-01 | 20481.05 | 2024-10-25 | 0.93361 | 0.99346 | 20347.17
Shoprite Hillbrow | 2025-11-01 | 20366.1 | 2024-10-25 | 1.0185 | 0.99287 | 20220.9121
Shoprite Hillbrow | 2025-12-01 | 21890.85 | 2024-10-25 | 1.1006 | 0.9923 | 21722.2556
Shoprite Hillbrow | 2026-01-01 | 20564.65 | 2024-10-25 | 1.1855 | 0.99171 | 20394.1068
Shoprite Hillbrow | 2026-02-01 | 17491.4 | 2024-10-25 | 1.2704 | 0.99112 | 17336.0045
Shoprite Hillbrow | 2026-03-01 | 18246.65 | 2024-10-25 | 1.347 | 0.99058 | 18074.8087
Shoprite Hillbrow | 2026-04-01 | 15297.85 | 2024-10-25 | 1.4319 | 0.98999 | 15144.7476
Shoprite Hillbrow | 2026-05-01 | 14953 | 2024-10-25 | 1.514 | 0.98942 | 14794.8102
Shoprite Hillbrow | 2026-06-01 | 13275.3 | 2024-10-25 | 1.5989 | 0.98883 | 13127.0302
Shoprite Hillbrow | 2026-07-01 | 14678.45 | 2024-10-25 | 1.681 | 0.98826 | 14506.1366
Shoprite Hillbrow | 2026-08-01 | 17062.95 | 2024-10-25 | 1.7659 | 0.98767 | 16852.5938
Shoprite Hillbrow | 2026-09-01 | 18937.3 | 2024-10-25 | 1.8508 | 0.98708 | 18692.6884
Shoprite Hillbrow | 2026-10-01 | 20481.05 | 2024-10-25 | 1.9329 | 0.98651 | 20204.837
Shoprite Hillbrow | 2026-11-01 | 20366.1 | 2024-10-25 | 2.0178 | 0.98593 | 20079.4622
Shoprite Hillbrow | 2026-12-01 | 21890.85 | 2024-10-25 | 2.0999 | 0.98536 | 21570.3035
Shoprite Ladybrand | 2024-01-01 | 37513.6 | 2024-09-23 | 0 | 1 | 37513.6
Shoprite Ladybrand | 2024-02-01 | 31212.25 | 2024-09-23 | 0 | 1 | 31212.25
Shoprite Ladybrand | 2024-03-01 | 29700.135 | 2024-09-23 | 0 | 1 | 29700.135
Shoprite Ladybrand | 2024-04-01 | 24898.55 | 2024-09-23 | 0 | 1 | 24898.55
Shoprite Ladybrand | 2024-05-01 | 21981.1 | 2024-09-23 | 0 | 1 | 21981.1
Shoprite Ladybrand | 2024-06-01 | 18982.9 | 2024-09-23 | 0 | 1 | 18982.9
Shoprite Ladybrand | 2024-07-01 | 21551.7 | 2024-09-23 | 0 | 1 | 21551.7
Shoprite Ladybrand | 2024-08-01 | 26041.4 | 2024-09-23 | 0 | 1 | 26041.4
Shoprite Ladybrand | 2024-09-01 | 29888.9 | 2024-09-23 | 0 | 1 | 29888.9
Shoprite Ladybrand | 2024-10-01 | 34705.4 | 2024-09-23 | 0.021903 | 0.99985 | 34700.0607
Shoprite Ladybrand | 2024-11-01 | 36881.85 | 2024-09-23 | 0.10678 | 0.99925 | 36854.1967
Shoprite Ladybrand | 2024-12-01 | 40110.9 | 2024-09-23 | 0.18891 | 0.99867 | 40057.7069
Shoprite Ladybrand | 2025-01-01 | 37513.6 | 2024-09-23 | 0.27379 | 0.99808 | 37441.5219
Shoprite Ladybrand | 2025-02-01 | 31212.25 | 2024-09-23 | 0.35866 | 0.99748 | 31133.7117
Shoprite Ladybrand | 2025-03-01 | 29700.135 | 2024-09-23 | 0.43532 | 0.99695 | 29609.4524
Shoprite Ladybrand | 2025-04-01 | 24898.55 | 2024-09-23 | 0.52019 | 0.99635 | 24807.7331
Shoprite Ladybrand | 2025-05-01 | 21981.1 | 2024-09-23 | 0.60233 | 0.99578 | 21888.2919
Shoprite Ladybrand | 2025-06-01 | 18982.9 | 2024-09-23 | 0.6872 | 0.99518 | 18891.4843
Shoprite Ladybrand | 2025-07-01 | 21551.7 | 2024-09-23 | 0.76934 | 0.99461 | 21435.5425
Shoprite Ladybrand | 2025-08-01 | 26041.4 | 2024-09-23 | 0.85421 | 0.99402 | 25885.6067
Shoprite Ladybrand | 2025-09-01 | 29888.9 | 2024-09-23 | 0.93908 | 0.99343 | 29692.3809
Shoprite Ladybrand | 2025-10-01 | 34705.4 | 2024-09-23 | 1.0212 | 0.99285 | 34457.3259
Shoprite Ladybrand | 2025-11-01 | 36881.85 | 2024-09-23 | 1.1061 | 0.99226 | 36596.3933
Shoprite Ladybrand | 2025-12-01 | 40110.9 | 2024-09-23 | 1.1882 | 0.99169 | 39777.4942
Shoprite Ladybrand | 2026-01-01 | 37513.6 | 2024-09-23 | 1.2731 | 0.9911 | 37179.61
Shoprite Ladybrand | 2026-02-01 | 31212.25 | 2024-09-23 | 1.358 | 0.99051 | 30915.9243
Shoprite Ladybrand | 2026-03-01 | 29700.135 | 2024-09-23 | 1.4346 | 0.98997 | 29402.3276
Shoprite Ladybrand | 2026-04-01 | 24898.55 | 2024-09-23 | 1.5195 | 0.98938 | 24634.1974
Shoprite Ladybrand | 2026-05-01 | 21981.1 | 2024-09-23 | 1.6016 | 0.98881 | 21735.1783
Shoprite Ladybrand | 2026-06-01 | 18982.9 | 2024-09-23 | 1.6865 | 0.98822 | 18759.3341
Shoprite Ladybrand | 2026-07-01 | 21551.7 | 2024-09-23 | 1.7687 | 0.98765 | 21285.5961
Shoprite Ladybrand | 2026-08-01 | 26041.4 | 2024-09-23 | 1.8535 | 0.98706 | 25704.531
Shoprite Ladybrand | 2026-09-01 | 29888.9 | 2024-09-23 | 1.9384 | 0.98648 | 29484.676
Shoprite Ladybrand | 2026-10-01 | 34705.4 | 2024-09-23 | 2.0205 | 0.98591 | 34216.2892
Shoprite Ladybrand | 2026-11-01 | 36881.85 | 2024-09-23 | 2.1054 | 0.98532 | 36340.3933
Shoprite Ladybrand | 2026-12-01 | 40110.9 | 2024-09-23 | 2.1875 | 0.98475 | 39499.2416
Shoprite Mini Ganyesa | 2024-01-01 | 34074.9 | 2024-08-27 | 0 | 1 | 34074.9
Shoprite Mini Ganyesa | 2024-02-01 | 28396.8 | 2024-08-27 | 0 | 1 | 28396.8
Shoprite Mini Ganyesa | 2024-03-01 | 28665.9 | 2024-08-27 | 0 | 1 | 28665.9
Shoprite Mini Ganyesa | 2024-04-01 | 24411.6 | 2024-08-27 | 0 | 1 | 24411.6
Shoprite Mini Ganyesa | 2024-05-01 | 22266.9 | 2024-08-27 | 0 | 1 | 22266.9
Shoprite Mini Ganyesa | 2024-06-01 | 19791.9 | 2024-08-27 | 0 | 1 | 19791.9
Shoprite Mini Ganyesa | 2024-07-01 | 21774.6 | 2024-08-27 | 0 | 1 | 21774.6
Shoprite Mini Ganyesa | 2024-08-01 | 25973.1 | 2024-08-27 | 0 | 1 | 25973.1
Shoprite Mini Ganyesa | 2024-09-01 | 28984.5 | 2024-08-27 | 0.013689 | 0.9999 | 28981.7129
Shoprite Mini Ganyesa | 2024-10-01 | 33058.8 | 2024-08-27 | 0.095825 | 0.99933 | 33036.5545
Shoprite Mini Ganyesa | 2024-11-01 | 34366.5 | 2024-08-27 | 0.1807 | 0.99873 | 34322.9051
Shoprite Mini Ganyesa | 2024-12-01 | 36320.4 | 2024-08-27 | 0.26283 | 0.99816 | 36253.4033
Shoprite Mini Ganyesa | 2025-01-01 | 34074.9 | 2024-08-27 | 0.34771 | 0.99756 | 33991.7733
Shoprite Mini Ganyesa | 2025-02-01 | 28396.8 | 2024-08-27 | 0.43258 | 0.99697 | 28310.6413
Shoprite Mini Ganyesa | 2025-03-01 | 28665.9 | 2024-08-27 | 0.50924 | 0.99643 | 28563.5391
Shoprite Mini Ganyesa | 2025-04-01 | 24411.6 | 2024-08-27 | 0.59411 | 0.99584 | 24309.9325
Shoprite Mini Ganyesa | 2025-05-01 | 22266.9 | 2024-08-27 | 0.67625 | 0.99526 | 22161.3744
Shoprite Mini Ganyesa | 2025-06-01 | 19791.9 | 2024-08-27 | 0.76112 | 0.99467 | 19686.3632
Shoprite Mini Ganyesa | 2025-07-01 | 21774.6 | 2024-08-27 | 0.84326 | 0.99409 | 21645.9981
Shoprite Mini Ganyesa | 2025-08-01 | 25973.1 | 2024-08-27 | 0.92813 | 0.9935 | 25804.3123
Shoprite Mini Ganyesa | 2025-09-01 | 28984.5 | 2024-08-27 | 1.013 | 0.99291 | 28778.9793
Shoprite Mini Ganyesa | 2025-10-01 | 33058.8 | 2024-08-27 | 1.0951 | 0.99234 | 32805.4564
Shoprite Mini Ganyesa | 2025-11-01 | 34366.5 | 2024-08-27 | 1.18 | 0.99175 | 34082.8086
Shoprite Mini Ganyesa | 2025-12-01 | 36320.4 | 2024-08-27 | 1.2621 | 0.99117 | 35999.8026
Shoprite Mini Ganyesa | 2026-01-01 | 34074.9 | 2024-08-27 | 1.347 | 0.99058 | 33753.9932
Shoprite Mini Ganyesa | 2026-02-01 | 28396.8 | 2024-08-27 | 1.4319 | 0.98999 | 28112.602
Shoprite Mini Ganyesa | 2026-03-01 | 28665.9 | 2024-08-27 | 1.5086 | 0.98946 | 28363.7307
Shoprite Mini Ganyesa | 2026-04-01 | 24411.6 | 2024-08-27 | 1.5934 | 0.98887 | 24139.879
Shoprite Mini Ganyesa | 2026-05-01 | 22266.9 | 2024-08-27 | 1.6756 | 0.9883 | 22006.3506
Shoprite Mini Ganyesa | 2026-06-01 | 19791.9 | 2024-08-27 | 1.7604 | 0.98771 | 19548.6526
Shoprite Mini Ganyesa | 2026-07-01 | 21774.6 | 2024-08-27 | 1.8426 | 0.98714 | 21494.5794
Shoprite Mini Ganyesa | 2026-08-01 | 25973.1 | 2024-08-27 | 1.9274 | 0.98655 | 25623.8053
Shoprite Mini Ganyesa | 2026-09-01 | 28984.5 | 2024-08-27 | 2.0123 | 0.98596 | 28577.6639
Shoprite Mini Ganyesa | 2026-10-01 | 33058.8 | 2024-08-27 | 2.0945 | 0.98539 | 32575.9748
Shoprite Mini Ganyesa | 2026-11-01 | 34366.5 | 2024-08-27 | 2.1793 | 0.98481 | 33844.3917
Shoprite Mini Ganyesa | 2026-12-01 | 36320.4 | 2024-08-27 | 2.2615 | 0.98424 | 35747.9758
Shoprite Naledi | 2024-01-01 | 20588.4 | 2024-09-05 | 0 | 1 | 20588.4
Shoprite Naledi | 2024-02-01 | 17538.3 | 2024-09-05 | 0 | 1 | 17538.3
Shoprite Naledi | 2024-03-01 | 17897.4 | 2024-09-05 | 0 | 1 | 17897.4
Shoprite Naledi | 2024-04-01 | 14674.5 | 2024-09-05 | 0 | 1 | 14674.5
Shoprite Naledi | 2024-05-01 | 13272.3 | 2024-09-05 | 0 | 1 | 13272.3
Shoprite Naledi | 2024-06-01 | 11571.3 | 2024-09-05 | 0 | 1 | 11571.3
Shoprite Naledi | 2024-07-01 | 12990.6 | 2024-09-05 | 0 | 1 | 12990.6
Shoprite Naledi | 2024-08-01 | 15871.5 | 2024-09-05 | 0 | 1 | 15871.5
Shoprite Naledi | 2024-09-01 | 18317.7 | 2024-09-05 | 0 | 1 | 18317.7
Shoprite Naledi | 2024-10-01 | 20121.3 | 2024-09-05 | 0.071184 | 0.9995 | 20111.241
Shoprite Naledi | 2024-11-01 | 20573.1 | 2024-09-05 | 0.15606 | 0.9989 | 20550.5592
Shoprite Naledi | 2024-12-01 | 21930.3 | 2024-09-05 | 0.23819 | 0.99833 | 21893.6366
Shoprite Naledi | 2025-01-01 | 20588.4 | 2024-09-05 | 0.32307 | 0.99773 | 20541.7293
Shoprite Naledi | 2025-02-01 | 17538.3 | 2024-09-05 | 0.40794 | 0.99714 | 17488.1138
Shoprite Naledi | 2025-03-01 | 17897.4 | 2024-09-05 | 0.4846 | 0.9966 | 17836.5786
Shoprite Naledi | 2025-04-01 | 14674.5 | 2024-09-05 | 0.56947 | 0.99601 | 14615.9144
Shoprite Naledi | 2025-05-01 | 13272.3 | 2024-09-05 | 0.65161 | 0.99543 | 13211.6875
Shoprite Naledi | 2025-06-01 | 11571.3 | 2024-09-05 | 0.73648 | 0.99484 | 11511.5904
Shoprite Naledi | 2025-07-01 | 12990.6 | 2024-09-05 | 0.81862 | 0.99427 | 12916.1123
Shoprite Naledi | 2025-08-01 | 15871.5 | 2024-09-05 | 0.90349 | 0.99367 | 15771.0877
Shoprite Naledi | 2025-09-01 | 18317.7 | 2024-09-05 | 0.98836 | 0.99308 | 18190.9629
Shoprite Naledi | 2025-10-01 | 20121.3 | 2024-09-05 | 1.0705 | 0.99251 | 19970.5584
Shoprite Naledi | 2025-11-01 | 20573.1 | 2024-09-05 | 1.1554 | 0.99192 | 20406.8034
Shoprite Naledi | 2025-12-01 | 21930.3 | 2024-09-05 | 1.2375 | 0.99134 | 21740.4857
Shoprite Naledi | 2026-01-01 | 20588.4 | 2024-09-05 | 1.3224 | 0.99075 | 20398.0353
Shoprite Naledi | 2026-02-01 | 17538.3 | 2024-09-05 | 1.4073 | 0.99016 | 17365.7805
Shoprite Naledi | 2026-03-01 | 17897.4 | 2024-09-05 | 1.4839 | 0.98963 | 17711.8077
Shoprite Naledi | 2026-04-01 | 14674.5 | 2024-09-05 | 1.5688 | 0.98904 | 14513.6728
Shoprite Naledi | 2026-05-01 | 13272.3 | 2024-09-05 | 1.6509 | 0.98847 | 13119.2688
Shoprite Naledi | 2026-06-01 | 11571.3 | 2024-09-05 | 1.7358 | 0.98788 | 11431.0643
Shoprite Naledi | 2026-07-01 | 12990.6 | 2024-09-05 | 1.8179 | 0.98731 | 12825.7612
Shoprite Naledi | 2026-08-01 | 15871.5 | 2024-09-05 | 1.9028 | 0.98672 | 15660.7654
Shoprite Naledi | 2026-09-01 | 18317.7 | 2024-09-05 | 1.9877 | 0.98613 | 18063.713
Shoprite Naledi | 2026-10-01 | 20121.3 | 2024-09-05 | 2.0698 | 0.98557 | 19830.8598
Shoprite Naledi | 2026-11-01 | 20573.1 | 2024-09-05 | 2.1547 | 0.98498 | 20264.0532
Shoprite Naledi | 2026-12-01 | 21930.3 | 2024-09-05 | 2.2368 | 0.98441 | 21588.4061
Shoprite Newlands | 2024-01-01 | 30721.5 | 2025-12-01 | 0 | 1 | 30721.5
Shoprite Newlands | 2024-02-01 | 24282.9 | 2025-12-01 | 0 | 1 | 24282.9
Shoprite Newlands | 2024-03-01 | 24146.1 | 2025-12-01 | 0 | 1 | 24146.1
Shoprite Newlands | 2024-04-01 | 18389.7 | 2025-12-01 | 0 | 1 | 18389.7
Shoprite Newlands | 2024-05-01 | 18961.2 | 2025-12-01 | 0 | 1 | 18961.2
Shoprite Newlands | 2024-06-01 | 15280.2 | 2025-12-01 | 0 | 1 | 15280.2
Shoprite Newlands | 2024-07-01 | 17361.9 | 2025-12-01 | 0 | 1 | 17361.9
Shoprite Newlands | 2024-08-01 | 19303.2 | 2025-12-01 | 0 | 1 | 19303.2
Shoprite Newlands | 2024-09-01 | 18141.3 | 2025-12-01 | 0 | 1 | 18141.3
Shoprite Newlands | 2024-10-01 | 22548.6 | 2025-12-01 | 0 | 1 | 22548.6
Shoprite Newlands | 2024-11-01 | 22923.9 | 2025-12-01 | 0 | 1 | 22923.9
Shoprite Newlands | 2024-12-01 | 28392.3 | 2025-12-01 | 0 | 1 | 28392.3
Shoprite Newlands | 2025-01-01 | 30721.5 | 2025-12-01 | 0 | 1 | 30721.5
Shoprite Newlands | 2025-02-01 | 24282.9 | 2025-12-01 | 0 | 1 | 24282.9
Shoprite Newlands | 2025-03-01 | 24146.1 | 2025-12-01 | 0 | 1 | 24146.1
Shoprite Newlands | 2025-04-01 | 18389.7 | 2025-12-01 | 0 | 1 | 18389.7
Shoprite Newlands | 2025-05-01 | 18961.2 | 2025-12-01 | 0 | 1 | 18961.2
Shoprite Newlands | 2025-06-01 | 15280.2 | 2025-12-01 | 0 | 1 | 15280.2
Shoprite Newlands | 2025-07-01 | 17361.9 | 2025-12-01 | 0 | 1 | 17361.9
Shoprite Newlands | 2025-08-01 | 19303.2 | 2025-12-01 | 0 | 1 | 19303.2
Shoprite Newlands | 2025-09-01 | 18141.3 | 2025-12-01 | 0 | 1 | 18141.3
Shoprite Newlands | 2025-10-01 | 22548.6 | 2025-12-01 | 0 | 1 | 22548.6
Shoprite Newlands | 2025-11-01 | 22923.9 | 2025-12-01 | 0 | 1 | 22923.9
Shoprite Newlands | 2025-12-01 | 28392.3 | 2025-12-01 | 0 | 1 | 28392.3
Shoprite Newlands | 2026-01-01 | 30721.5 | 2025-12-01 | 0.084873 | 0.9994 | 30703.1892
Shoprite Newlands | 2026-02-01 | 24282.9 | 2025-12-01 | 0.16975 | 0.99881 | 24253.9622
Shoprite Newlands | 2026-03-01 | 24146.1 | 2025-12-01 | 0.24641 | 0.99827 | 24104.3414
Shoprite Newlands | 2026-04-01 | 18389.7 | 2025-12-01 | 0.33128 | 0.99768 | 18346.9548
Shoprite Newlands | 2026-05-01 | 18961.2 | 2025-12-01 | 0.41342 | 0.9971 | 18906.215
Shoprite Newlands | 2026-06-01 | 15280.2 | 2025-12-01 | 0.49829 | 0.99651 | 15226.8084
Shoprite Newlands | 2026-07-01 | 17361.9 | 2025-12-01 | 0.58042 | 0.99593 | 17291.2552
Shoprite Newlands | 2026-08-01 | 19303.2 | 2025-12-01 | 0.6653 | 0.99534 | 19213.1977
Shoprite Newlands | 2026-09-01 | 18141.3 | 2025-12-01 | 0.75017 | 0.99474 | 18045.9529
Shoprite Newlands | 2026-10-01 | 22548.6 | 2025-12-01 | 0.83231 | 0.99417 | 22417.1512
Shoprite Newlands | 2026-11-01 | 22923.9 | 2025-12-01 | 0.91718 | 0.99358 | 22776.6798
Shoprite Newlands | 2026-12-01 | 28392.3 | 2025-12-01 | 0.99932 | 0.993 | 28193.6895
Shoprite Thokoza | 2024-01-01 | 18584.1 | 2025-04-01 | 0 | 1 | 18584.1
Shoprite Thokoza | 2024-02-01 | 16101.9 | 2025-04-01 | 0 | 1 | 16101.9
Shoprite Thokoza | 2024-03-01 | 15901.2 | 2025-04-01 | 0 | 1 | 15901.2
Shoprite Thokoza | 2024-04-01 | 13660.2 | 2025-04-01 | 0 | 1 | 13660.2
Shoprite Thokoza | 2024-05-01 | 12620.7 | 2025-04-01 | 0 | 1 | 12620.7
Shoprite Thokoza | 2024-06-01 | 11094.3 | 2025-04-01 | 0 | 1 | 11094.3
Shoprite Thokoza | 2024-07-01 | 12367.8 | 2025-04-01 | 0 | 1 | 12367.8
Shoprite Thokoza | 2024-08-01 | 14484.6 | 2025-04-01 | 0 | 1 | 14484.6
Shoprite Thokoza | 2024-09-01 | 16189.2 | 2025-04-01 | 0 | 1 | 16189.2
Shoprite Thokoza | 2024-10-01 | 18663.3 | 2025-04-01 | 0 | 1 | 18663.3
Shoprite Thokoza | 2024-11-01 | 18589.5 | 2025-04-01 | 0 | 1 | 18589.5
Shoprite Thokoza | 2024-12-01 | 19022.4 | 2025-04-01 | 0 | 1 | 19022.4
Shoprite Thokoza | 2025-01-01 | 18584.1 | 2025-04-01 | 0 | 1 | 18584.1
Shoprite Thokoza | 2025-02-01 | 16101.9 | 2025-04-01 | 0 | 1 | 16101.9
Shoprite Thokoza | 2025-03-01 | 15901.2 | 2025-04-01 | 0 | 1 | 15901.2
Shoprite Thokoza | 2025-04-01 | 13660.2 | 2025-04-01 | 0 | 1 | 13660.2
Shoprite Thokoza | 2025-05-01 | 12620.7 | 2025-04-01 | 0.082136 | 0.99942 | 12613.4203
Shoprite Thokoza | 2025-06-01 | 11094.3 | 2025-04-01 | 0.16701 | 0.99883 | 11081.2921
Shoprite Thokoza | 2025-07-01 | 12367.8 | 2025-04-01 | 0.24914 | 0.99825 | 12346.1735
Shoprite Thokoza | 2025-08-01 | 14484.6 | 2025-04-01 | 0.33402 | 0.99766 | 14450.654
Shoprite Thokoza | 2025-09-01 | 16189.2 | 2025-04-01 | 0.41889 | 0.99706 | 16141.6325
Shoprite Thokoza | 2025-10-01 | 18663.3 | 2025-04-01 | 0.50103 | 0.99649 | 18597.7296
Shoprite Thokoza | 2025-11-01 | 18589.5 | 2025-04-01 | 0.5859 | 0.99589 | 18513.148
Shoprite Thokoza | 2025-12-01 | 19022.4 | 2025-04-01 | 0.66804 | 0.99532 | 18933.3428
Shoprite Thokoza | 2026-01-01 | 18584.1 | 2025-04-01 | 0.75291 | 0.99473 | 18486.0701
Shoprite Thokoza | 2026-02-01 | 16101.9 | 2025-04-01 | 0.83778 | 0.99413 | 16007.417
Shoprite Thokoza | 2026-03-01 | 15901.2 | 2025-04-01 | 0.91444 | 0.9936 | 15799.3843
Shoprite Thokoza | 2026-04-01 | 13660.2 | 2025-04-01 | 0.99932 | 0.993 | 13564.6438
Shoprite Thokoza | 2026-05-01 | 12620.7 | 2025-04-01 | 1.0815 | 0.99243 | 12525.1866
Shoprite Thokoza | 2026-06-01 | 11094.3 | 2025-04-01 | 1.1663 | 0.99184 | 11003.776
Shoprite Thokoza | 2026-07-01 | 12367.8 | 2025-04-01 | 1.2485 | 0.99127 | 12259.8092
Shoprite Thokoza | 2026-08-01 | 14484.6 | 2025-04-01 | 1.3333 | 0.99068 | 14349.5684
Shoprite Thokoza | 2026-09-01 | 16189.2 | 2025-04-01 | 1.4182 | 0.99009 | 16028.7181
Shoprite Thokoza | 2026-10-01 | 18663.3 | 2025-04-01 | 1.5003 | 0.98952 | 18467.6343
Shoprite Thokoza | 2026-11-01 | 18589.5 | 2025-04-01 | 1.5852 | 0.98893 | 18383.6444
Shoprite Thokoza | 2026-12-01 | 19022.4 | 2025-04-01 | 1.6674 | 0.98836 | 18800.8998
Spring Glade | 2024-01-01 | 16638.665 | 2021-12-02 | 2.0808 | 0.98549 | 16397.2333
Spring Glade | 2024-02-01 | 14215.06 | 2021-12-02 | 2.1656 | 0.9849 | 14000.4459
Spring Glade | 2024-03-01 | 15137.31 | 2021-12-02 | 2.245 | 0.98435 | 14900.4592
Spring Glade | 2024-04-01 | 13176.87 | 2021-12-02 | 2.3299 | 0.98377 | 12962.963
Spring Glade | 2024-05-01 | 12813.75 | 2021-12-02 | 2.412 | 0.9832 | 12598.4667
Spring Glade | 2024-06-01 | 11578.87 | 2021-12-02 | 2.4969 | 0.98261 | 11377.5485
Spring Glade | 2024-07-01 | 12892.545 | 2021-12-02 | 2.5791 | 0.98205 | 12661.0755
Spring Glade | 2024-08-01 | 14836.92 | 2021-12-02 | 2.6639 | 0.98146 | 14561.8573
Spring Glade | 2024-09-01 | 15996.15 | 2021-12-02 | 2.7488 | 0.98088 | 15690.2389
Spring Glade | 2024-10-01 | 16796.17 | 2021-12-02 | 2.8309 | 0.98031 | 16465.4564
Spring Glade | 2024-11-01 | 16463.225 | 2021-12-02 | 2.9158 | 0.97973 | 16129.4478
Spring Glade | 2024-12-01 | 17398.905 | 2021-12-02 | 2.9979 | 0.97916 | 17036.3254
Spring Glade | 2025-01-01 | 16638.665 | 2021-12-02 | 3.0828 | 0.97858 | 16282.2178
Spring Glade | 2025-02-01 | 14215.06 | 2021-12-02 | 3.1677 | 0.97799 | 13902.2422
Spring Glade | 2025-03-01 | 15137.31 | 2021-12-02 | 3.2444 | 0.97747 | 14796.2271
Spring Glade | 2025-04-01 | 13176.87 | 2021-12-02 | 3.3292 | 0.97688 | 12872.2842
Spring Glade | 2025-05-01 | 12813.75 | 2021-12-02 | 3.4114 | 0.97632 | 12510.3376
Spring Glade | 2025-06-01 | 11578.87 | 2021-12-02 | 3.4962 | 0.97574 | 11297.96
Spring Glade | 2025-07-01 | 12892.545 | 2021-12-02 | 3.5784 | 0.97518 | 12572.5084
Spring Glade | 2025-08-01 | 14836.92 | 2021-12-02 | 3.6632 | 0.9746 | 14459.9938
Spring Glade | 2025-09-01 | 15996.15 | 2021-12-02 | 3.7481 | 0.97401 | 15580.4821
Spring Glade | 2025-10-01 | 16796.17 | 2021-12-02 | 3.8303 | 0.97345 | 16350.2769
Spring Glade | 2025-11-01 | 16463.225 | 2021-12-02 | 3.9151 | 0.97287 | 16016.6186
Spring Glade | 2025-12-01 | 17398.905 | 2021-12-02 | 3.9973 | 0.97231 | 16917.1525
Spring Glade | 2026-01-01 | 16638.665 | 2021-12-02 | 4.0821 | 0.97173 | 16168.32
Spring Glade | 2026-02-01 | 14215.06 | 2021-12-02 | 4.167 | 0.97115 | 13804.9929
Spring Glade | 2026-03-01 | 15137.31 | 2021-12-02 | 4.2437 | 0.97063 | 14692.7242
Spring Glade | 2026-04-01 | 13176.87 | 2021-12-02 | 4.3285 | 0.97005 | 12782.2396
Spring Glade | 2026-05-01 | 12813.75 | 2021-12-02 | 4.4107 | 0.96949 | 12422.8249
Spring Glade | 2026-06-01 | 11578.87 | 2021-12-02 | 4.4956 | 0.96891 | 11218.9282
Spring Glade | 2026-07-01 | 12892.545 | 2021-12-02 | 4.5777 | 0.96836 | 12484.5609
Spring Glade | 2026-08-01 | 14836.92 | 2021-12-02 | 4.6626 | 0.96778 | 14358.8429
Spring Glade | 2026-09-01 | 15996.15 | 2021-12-02 | 4.7474 | 0.9672 | 15471.4931
Spring Glade | 2026-10-01 | 16796.17 | 2021-12-02 | 4.8296 | 0.96664 | 16235.903
Spring Glade | 2026-11-01 | 16463.225 | 2021-12-02 | 4.9144 | 0.96607 | 15904.5788
Spring Glade | 2026-12-01 | 17398.905 | 2021-12-02 | 4.9966 | 0.96551 | 16798.8132
TPF Foods | 2024-01-01 | 3784.425 | 2021-06-04 | 2.5763 | 0.98207 | 3716.5519
TPF Foods | 2024-02-01 | 3270.15 | 2021-06-04 | 2.6612 | 0.98148 | 3209.5862
TPF Foods | 2024-03-01 | 3533.325 | 2021-06-04 | 2.7406 | 0.98093 | 3465.9535
TPF Foods | 2024-04-01 | 3063.075 | 2021-06-04 | 2.8255 | 0.98035 | 3002.8791
TPF Foods | 2024-05-01 | 3093.825 | 2021-06-04 | 2.9076 | 0.97978 | 3031.2753
TPF Foods | 2024-06-01 | 2834.025 | 2021-06-04 | 2.9925 | 0.9792 | 2775.0729
TPF Foods | 2024-07-01 | 3103.35 | 2021-06-04 | 3.0746 | 0.97863 | 3037.0427
TPF Foods | 2024-08-01 | 3491.55 | 2021-06-04 | 3.1595 | 0.97805 | 3414.9117
TPF Foods | 2024-09-01 | 3723.45 | 2021-06-04 | 3.2444 | 0.97747 | 3639.551
TPF Foods | 2024-10-01 | 3899.4 | 2021-06-04 | 3.3265 | 0.9769 | 3809.3379
TPF Foods | 2024-11-01 | 3732.75 | 2021-06-04 | 3.4114 | 0.97632 | 3644.3635
TPF Foods | 2024-12-01 | 4016.175 | 2021-06-04 | 3.4935 | 0.97576 | 3918.8157
TPF Foods | 2025-01-01 | 3784.425 | 2021-06-04 | 3.5784 | 0.97518 | 3690.4828
TPF Foods | 2025-02-01 | 3270.15 | 2021-06-04 | 3.6632 | 0.9746 | 3187.0731
TPF Foods | 2025-03-01 | 3533.325 | 2021-06-04 | 3.7399 | 0.97407 | 3441.7084
TPF Foods | 2025-04-01 | 3063.075 | 2021-06-04 | 3.8248 | 0.97349 | 2981.8733
TPF Foods | 2025-05-01 | 3093.825 | 2021-06-04 | 3.9069 | 0.97293 | 3010.0709
TPF Foods | 2025-06-01 | 2834.025 | 2021-06-04 | 3.9918 | 0.97235 | 2755.6606
TPF Foods | 2025-07-01 | 3103.35 | 2021-06-04 | 4.0739 | 0.97179 | 3015.7979
TPF Foods | 2025-08-01 | 3491.55 | 2021-06-04 | 4.1588 | 0.97121 | 3391.0236
TPF Foods | 2025-09-01 | 3723.45 | 2021-06-04 | 4.2437 | 0.97063 | 3614.0915
TPF Foods | 2025-10-01 | 3899.4 | 2021-06-04 | 4.3258 | 0.97007 | 3782.6907
TPF Foods | 2025-11-01 | 3732.75 | 2021-06-04 | 4.4107 | 0.96949 | 3618.8703
TPF Foods | 2025-12-01 | 4016.175 | 2021-06-04 | 4.4928 | 0.96893 | 3891.4027
TPF Foods | 2026-01-01 | 3784.425 | 2021-06-04 | 4.5777 | 0.96836 | 3664.667
TPF Foods | 2026-02-01 | 3270.15 | 2021-06-04 | 4.6626 | 0.96778 | 3164.7788
TPF Foods | 2026-03-01 | 3533.325 | 2021-06-04 | 4.7392 | 0.96726 | 3417.6328
TPF Foods | 2026-04-01 | 3063.075 | 2021-06-04 | 4.8241 | 0.96668 | 2961.0144
TPF Foods | 2026-05-01 | 3093.825 | 2021-06-04 | 4.9062 | 0.96612 | 2989.0148
TPF Foods | 2026-06-01 | 2834.025 | 2021-06-04 | 4.9911 | 0.96555 | 2736.3841
TPF Foods | 2026-07-01 | 3103.35 | 2021-06-04 | 5.0732 | 0.96499 | 2994.7017
TPF Foods | 2026-08-01 | 3491.55 | 2021-06-04 | 5.1581 | 0.96441 | 3367.3026
TPF Foods | 2026-09-01 | 3723.45 | 2021-06-04 | 5.243 | 0.96384 | 3588.8101
TPF Foods | 2026-10-01 | 3899.4 | 2021-06-04 | 5.3251 | 0.96328 | 3756.2299
TPF Foods | 2026-11-01 | 3732.75 | 2021-06-04 | 5.41 | 0.96271 | 3593.5555
TPF Foods | 2026-12-01 | 4016.175 | 2021-06-04 | 5.4921 | 0.96215 | 3864.1814
Thakadu Industrial | 2024-01-01 | 0 | 2023-11-17 | 0.1232 | 0.99913 | 0
Thakadu Industrial | 2024-02-01 | 0 | 2023-11-17 | 0.20808 | 0.99854 | 0
Thakadu Industrial | 2024-03-01 | 0 | 2023-11-17 | 0.28747 | 0.99798 | 0
Thakadu Industrial | 2024-04-01 | 0 | 2023-11-17 | 0.37235 | 0.99739 | 0
Thakadu Industrial | 2024-05-01 | 0 | 2023-11-17 | 0.45448 | 0.99681 | 0
Thakadu Industrial | 2024-06-01 | 0 | 2023-11-17 | 0.53936 | 0.99622 | 0
Thakadu Industrial | 2024-07-01 | 0 | 2023-11-17 | 0.62149 | 0.99564 | 0
Thakadu Industrial | 2024-08-01 | 0 | 2023-11-17 | 0.70637 | 0.99505 | 0
Thakadu Industrial | 2024-09-01 | 0 | 2023-11-17 | 0.79124 | 0.99446 | 0
Thakadu Industrial | 2024-10-01 | 0 | 2023-11-17 | 0.87337 | 0.99388 | 0
Thakadu Industrial | 2024-11-01 | 0 | 2023-11-17 | 0.95825 | 0.99329 | 0
Thakadu Industrial | 2024-12-01 | 0 | 2023-11-17 | 1.0404 | 0.99272 | 0
Thakadu Industrial | 2025-01-01 | 0 | 2023-11-17 | 1.1253 | 0.99213 | 0
Thakadu Industrial | 2025-02-01 | 0 | 2023-11-17 | 1.2101 | 0.99154 | 0
Thakadu Industrial | 2025-03-01 | 0 | 2023-11-17 | 1.2868 | 0.991 | 0
Thakadu Industrial | 2025-04-01 | 0 | 2023-11-17 | 1.3717 | 0.99041 | 0
Thakadu Industrial | 2025-05-01 | 0 | 2023-11-17 | 1.4538 | 0.98984 | 0
Thakadu Industrial | 2025-06-01 | 0 | 2023-11-17 | 1.5387 | 0.98925 | 0
Thakadu Industrial | 2025-07-01 | 0 | 2023-11-17 | 1.6208 | 0.98868 | 0
Thakadu Industrial | 2025-08-01 | 0 | 2023-11-17 | 1.7057 | 0.98809 | 0
Thakadu Industrial | 2025-09-01 | 0 | 2023-11-17 | 1.7906 | 0.9875 | 0
Thakadu Industrial | 2025-10-01 | 0 | 2023-11-17 | 1.8727 | 0.98693 | 0
Thakadu Industrial | 2025-11-01 | 0 | 2023-11-17 | 1.9576 | 0.98634 | 0
Thakadu Industrial | 2025-12-01 | 0 | 2023-11-17 | 2.0397 | 0.98577 | 0
Thakadu Industrial | 2026-01-01 | 0 | 2023-11-17 | 2.1246 | 0.98519 | 0
Thakadu Industrial | 2026-02-01 | 0 | 2023-11-17 | 2.2094 | 0.9846 | 0
Thakadu Industrial | 2026-03-01 | 0 | 2023-11-17 | 2.2861 | 0.98407 | 0
Thakadu Industrial | 2026-04-01 | 0 | 2023-11-17 | 2.371 | 0.98348 | 0
Thakadu Industrial | 2026-05-01 | 0 | 2023-11-17 | 2.4531 | 0.98292 | 0
Thakadu Industrial | 2026-06-01 | 0 | 2023-11-17 | 2.538 | 0.98233 | 0
Thakadu Industrial | 2026-07-01 | 0 | 2023-11-17 | 2.6201 | 0.98176 | 0
Thakadu Industrial | 2026-08-01 | 0 | 2023-11-17 | 2.705 | 0.98118 | 0
Thakadu Industrial | 2026-09-01 | 0 | 2023-11-17 | 2.7899 | 0.98059 | 0
Thakadu Industrial | 2026-10-01 | 0 | 2023-11-17 | 2.872 | 0.98003 | 0
Thakadu Industrial | 2026-11-01 | 0 | 2023-11-17 | 2.9569 | 0.97944 | 0
Thakadu Industrial | 2026-12-01 | 0 | 2023-11-17 | 3.039 | 0.97888 | 0
The Alec | 2024-01-01 | 7399.8 | 2023-05-22 | 0.61328 | 0.9957 | 7367.9899
The Alec | 2024-02-01 | 6298.2 | 2023-05-22 | 0.69815 | 0.99511 | 6267.3877
The Alec | 2024-03-01 | 6353.1 | 2023-05-22 | 0.77755 | 0.99455 | 6318.494
The Alec | 2024-04-01 | 5016.6 | 2023-05-22 | 0.86242 | 0.99396 | 4986.3004
The Alec | 2024-05-01 | 4753.8 | 2023-05-22 | 0.94456 | 0.99339 | 4722.3622
The Alec | 2024-06-01 | 4257 | 2023-05-22 | 1.0294 | 0.99279 | 4226.3271
The Alec | 2024-07-01 | 4730.4 | 2023-05-22 | 1.1116 | 0.99222 | 4693.6073
The Alec | 2024-08-01 | 5440.5 | 2023-05-22 | 1.1964 | 0.99163 | 5394.9667
The Alec | 2024-09-01 | 6345.9 | 2023-05-22 | 1.2813 | 0.99104 | 6289.0385
The Alec | 2024-10-01 | 7250.4 | 2023-05-22 | 1.3634 | 0.99047 | 7181.2893
The Alec | 2024-11-01 | 7330.5 | 2023-05-22 | 1.4483 | 0.98988 | 7256.2982
The Alec | 2024-12-01 | 7866 | 2023-05-22 | 1.5305 | 0.98931 | 7781.8865
The Alec | 2025-01-01 | 7399.8 | 2023-05-22 | 1.6153 | 0.98872 | 7316.3084
The Alec | 2025-02-01 | 6298.2 | 2023-05-22 | 1.7002 | 0.98813 | 6223.4262
The Alec | 2025-03-01 | 6353.1 | 2023-05-22 | 1.7769 | 0.9876 | 6274.2948
The Alec | 2025-04-01 | 5016.6 | 2023-05-22 | 1.8617 | 0.98701 | 4951.4201
The Alec | 2025-05-01 | 4753.8 | 2023-05-22 | 1.9439 | 0.98644 | 4689.3282
The Alec | 2025-06-01 | 4257 | 2023-05-22 | 2.0287 | 0.98585 | 4196.763
The Alec | 2025-07-01 | 4730.4 | 2023-05-22 | 2.1109 | 0.98528 | 4660.7745
The Alec | 2025-08-01 | 5440.5 | 2023-05-22 | 2.1958 | 0.98469 | 5357.2277
The Alec | 2025-09-01 | 6345.9 | 2023-05-22 | 2.2806 | 0.98411 | 6245.0453
The Alec | 2025-10-01 | 7250.4 | 2023-05-22 | 2.3628 | 0.98354 | 7131.0545
The Alec | 2025-11-01 | 7330.5 | 2023-05-22 | 2.4476 | 0.98295 | 7205.5388
The Alec | 2025-12-01 | 7866 | 2023-05-22 | 2.5298 | 0.98239 | 7727.4505
The Alec | 2026-01-01 | 7399.8 | 2023-05-22 | 2.6146 | 0.9818 | 7265.1292
The Alec | 2026-02-01 | 6298.2 | 2023-05-22 | 2.6995 | 0.98122 | 6179.8919
The Alec | 2026-03-01 | 6353.1 | 2023-05-22 | 2.7762 | 0.98069 | 6230.4046
The Alec | 2026-04-01 | 5016.6 | 2023-05-22 | 2.8611 | 0.9801 | 4916.7838
The Alec | 2026-05-01 | 4753.8 | 2023-05-22 | 2.9432 | 0.97954 | 4656.5253
The Alec | 2026-06-01 | 4257 | 2023-05-22 | 3.0281 | 0.97895 | 4167.4057
The Alec | 2026-07-01 | 4730.4 | 2023-05-22 | 3.1102 | 0.97839 | 4628.1713
The Alec | 2026-08-01 | 5440.5 | 2023-05-22 | 3.1951 | 0.97781 | 5319.7527
The Alec | 2026-09-01 | 6345.9 | 2023-05-22 | 3.2799 | 0.97722 | 6201.3598
The Alec | 2026-10-01 | 7250.4 | 2023-05-22 | 3.3621 | 0.97666 | 7081.1712
The Alec | 2026-11-01 | 7330.5 | 2023-05-22 | 3.447 | 0.97608 | 7155.1344
The Alec | 2026-12-01 | 7866 | 2023-05-22 | 3.5291 | 0.97551 | 7673.3952
Three Peaks | 2024-01-01 | 4274.1 | 2022-02-25 | 1.848 | 0.9871 | 4218.9729
Three Peaks | 2024-02-01 | 3810.6 | 2022-02-25 | 1.9329 | 0.98651 | 3759.2092
Three Peaks | 2024-03-01 | 3907.275 | 2022-02-25 | 2.0123 | 0.98596 | 3852.4312
Three Peaks | 2024-04-01 | 3268.125 | 2022-02-25 | 2.0972 | 0.98538 | 3220.332
Three Peaks | 2024-05-01 | 2929.95 | 2022-02-25 | 2.1793 | 0.98481 | 2885.4371
Three Peaks | 2024-06-01 | 2664.75 | 2022-02-25 | 2.2642 | 0.98422 | 2622.702
Three Peaks | 2024-07-01 | 2851.125 | 2022-02-25 | 2.3463 | 0.98365 | 2804.5176
Three Peaks | 2024-08-01 | 3237 | 2022-02-25 | 2.4312 | 0.98307 | 3182.1869
Three Peaks | 2024-09-01 | 3327.75 | 2022-02-25 | 2.5161 | 0.98248 | 3269.4503
Three Peaks | 2024-10-01 | 3775.725 | 2022-02-25 | 2.5982 | 0.98191 | 3707.4374
Three Peaks | 2024-11-01 | 3829.575 | 2022-02-25 | 2.6831 | 0.98133 | 3758.0723
Three Peaks | 2024-12-01 | 4315.65 | 2022-02-25 | 2.7652 | 0.98076 | 4232.6289
Three Peaks | 2025-01-01 | 4274.1 | 2022-02-25 | 2.8501 | 0.98018 | 4189.3797
Three Peaks | 2025-02-01 | 3810.6 | 2022-02-25 | 2.935 | 0.97959 | 3732.8409
Three Peaks | 2025-03-01 | 3907.275 | 2022-02-25 | 3.0116 | 0.97907 | 3825.4826
Three Peaks | 2025-04-01 | 3268.125 | 2022-02-25 | 3.0965 | 0.97848 | 3197.805
Three Peaks | 2025-05-01 | 2929.95 | 2022-02-25 | 3.1786 | 0.97792 | 2865.2529
Three Peaks | 2025-06-01 | 2664.75 | 2022-02-25 | 3.2635 | 0.97734 | 2604.3556
Three Peaks | 2025-07-01 | 2851.125 | 2022-02-25 | 3.3457 | 0.97677 | 2784.8993
Three Peaks | 2025-08-01 | 3237 | 2022-02-25 | 3.4305 | 0.97619 | 3159.9267
Three Peaks | 2025-09-01 | 3327.75 | 2022-02-25 | 3.5154 | 0.97561 | 3246.5798
Three Peaks | 2025-10-01 | 3775.725 | 2022-02-25 | 3.5975 | 0.97505 | 3681.5031
Three Peaks | 2025-11-01 | 3829.575 | 2022-02-25 | 3.6824 | 0.97446 | 3731.7837
Three Peaks | 2025-12-01 | 4315.65 | 2022-02-25 | 3.7645 | 0.9739 | 4203.0207
Three Peaks | 2026-01-01 | 4274.1 | 2022-02-25 | 3.8494 | 0.97332 | 4160.074
Three Peaks | 2026-02-01 | 3810.6 | 2022-02-25 | 3.9343 | 0.97274 | 3706.7288
Three Peaks | 2026-03-01 | 3907.275 | 2022-02-25 | 4.011 | 0.97222 | 3798.7224
Three Peaks | 2026-04-01 | 3268.125 | 2022-02-25 | 4.0958 | 0.97164 | 3175.4356
Three Peaks | 2026-05-01 | 2929.95 | 2022-02-25 | 4.178 | 0.97108 | 2845.2098
Three Peaks | 2026-06-01 | 2664.75 | 2022-02-25 | 4.2628 | 0.9705 | 2586.1376
Three Peaks | 2026-07-01 | 2851.125 | 2022-02-25 | 4.345 | 0.96994 | 2765.4183
Three Peaks | 2026-08-01 | 3237 | 2022-02-25 | 4.4298 | 0.96936 | 3137.8223
Three Peaks | 2026-09-01 | 3327.75 | 2022-02-25 | 4.5147 | 0.96878 | 3223.8692
Three Peaks | 2026-10-01 | 3775.725 | 2022-02-25 | 4.5969 | 0.96822 | 3655.7501
Three Peaks | 2026-11-01 | 3829.575 | 2022-02-25 | 4.6817 | 0.96765 | 3705.679
Three Peaks | 2026-12-01 | 4315.65 | 2022-02-25 | 4.7639 | 0.96709 | 4173.6196
Trouw Nutrition | 2024-01-01 | 13441.985 | 2021-11-04 | 2.1574 | 0.98496 | 13239.8064
Trouw Nutrition | 2024-02-01 | 12055.125 | 2021-11-04 | 2.2423 | 0.98437 | 11866.7288
Trouw Nutrition | 2024-03-01 | 12858.46 | 2021-11-04 | 2.3217 | 0.98382 | 12650.4518
Trouw Nutrition | 2024-04-01 | 11531.27 | 2021-11-04 | 2.4066 | 0.98324 | 11337.9697
Trouw Nutrition | 2024-05-01 | 11785.93 | 2021-11-04 | 2.4887 | 0.98267 | 11581.6766
Trouw Nutrition | 2024-06-01 | 11018.635 | 2021-11-04 | 2.5736 | 0.98208 | 10821.2254
Trouw Nutrition | 2024-07-01 | 12024.27 | 2021-11-04 | 2.6557 | 0.98152 | 11802.0321
Trouw Nutrition | 2024-08-01 | 13262.635 | 2021-11-04 | 2.7406 | 0.98093 | 13009.7503
Trouw Nutrition | 2024-09-01 | 13540.33 | 2021-11-04 | 2.8255 | 0.98035 | 13274.2339
Trouw Nutrition | 2024-10-01 | 13925.295 | 2021-11-04 | 2.9076 | 0.97978 | 13643.7592
Trouw Nutrition | 2024-11-01 | 13508.37 | 2021-11-04 | 2.9925 | 0.9792 | 13227.3749
Trouw Nutrition | 2024-12-01 | 14234.525 | 2021-11-04 | 3.0746 | 0.97863 | 13930.385
Trouw Nutrition | 2025-01-01 | 13441.985 | 2021-11-04 | 3.1595 | 0.97805 | 13146.9381
Trouw Nutrition | 2025-02-01 | 12055.125 | 2021-11-04 | 3.2444 | 0.97747 | 11783.4918
Trouw Nutrition | 2025-03-01 | 12858.46 | 2021-11-04 | 3.321 | 0.97694 | 12561.959
Trouw Nutrition | 2025-04-01 | 11531.27 | 2021-11-04 | 3.4059 | 0.97636 | 11258.658
Trouw Nutrition | 2025-05-01 | 11785.93 | 2021-11-04 | 3.488 | 0.9758 | 11500.6601
Trouw Nutrition | 2025-06-01 | 11018.635 | 2021-11-04 | 3.5729 | 0.97521 | 10745.5285
Trouw Nutrition | 2025-07-01 | 12024.27 | 2021-11-04 | 3.655 | 0.97465 | 11719.4742
Trouw Nutrition | 2025-08-01 | 13262.635 | 2021-11-04 | 3.7399 | 0.97407 | 12918.7442
Trouw Nutrition | 2025-09-01 | 13540.33 | 2021-11-04 | 3.8248 | 0.97349 | 13181.3777
Trouw Nutrition | 2025-10-01 | 13925.295 | 2021-11-04 | 3.9069 | 0.97293 | 13548.3181
Trouw Nutrition | 2025-11-01 | 13508.37 | 2021-11-04 | 3.9918 | 0.97235 | 13134.8464
Trouw Nutrition | 2025-12-01 | 14234.525 | 2021-11-04 | 4.0739 | 0.97179 | 13832.9388
Trouw Nutrition | 2026-01-01 | 13441.985 | 2021-11-04 | 4.1588 | 0.97121 | 13054.9723
Trouw Nutrition | 2026-02-01 | 12055.125 | 2021-11-04 | 4.2437 | 0.97063 | 11701.0636
Trouw Nutrition | 2026-03-01 | 12858.46 | 2021-11-04 | 4.3203 | 0.97011 | 12474.0853
Trouw Nutrition | 2026-04-01 | 11531.27 | 2021-11-04 | 4.4052 | 0.96953 | 11179.9012
Trouw Nutrition | 2026-05-01 | 11785.93 | 2021-11-04 | 4.4873 | 0.96897 | 11420.2104
Trouw Nutrition | 2026-06-01 | 11018.635 | 2021-11-04 | 4.5722 | 0.96839 | 10670.3611
Trouw Nutrition | 2026-07-01 | 12024.27 | 2021-11-04 | 4.6543 | 0.96783 | 11637.4939
Trouw Nutrition | 2026-08-01 | 13262.635 | 2021-11-04 | 4.7392 | 0.96726 | 12828.3747
Trouw Nutrition | 2026-09-01 | 13540.33 | 2021-11-04 | 4.8241 | 0.96668 | 13089.1709
Trouw Nutrition | 2026-10-01 | 13925.295 | 2021-11-04 | 4.9062 | 0.96612 | 13453.5445
Trouw Nutrition | 2026-11-01 | 13508.37 | 2021-11-04 | 4.9911 | 0.96555 | 13042.9652
Trouw Nutrition | 2026-12-01 | 14234.525 | 2021-11-04 | 5.0732 | 0.96499 | 13736.1743
U Save Botrivier | 2024-01-01 | 7299.9 | 2025-07-23 | 0 | 1 | 7299.9
U Save Botrivier | 2024-02-01 | 6223.5 | 2025-07-23 | 0 | 1 | 6223.5
U Save Botrivier | 2024-03-01 | 6048.9 | 2025-07-23 | 0 | 1 | 6048.9
U Save Botrivier | 2024-04-01 | 5130.9 | 2025-07-23 | 0 | 1 | 5130.9
U Save Botrivier | 2024-05-01 | 4621.5 | 2025-07-23 | 0 | 1 | 4621.5
U Save Botrivier | 2024-06-01 | 3931.2 | 2025-07-23 | 0 | 1 | 3931.2
U Save Botrivier | 2024-07-01 | 4065.3 | 2025-07-23 | 0 | 1 | 4065.3
U Save Botrivier | 2024-08-01 | 4723.2 | 2025-07-23 | 0 | 1 | 4723.2
U Save Botrivier | 2024-09-01 | 5251.5 | 2025-07-23 | 0 | 1 | 5251.5
U Save Botrivier | 2024-10-01 | 6489.9 | 2025-07-23 | 0 | 1 | 6489.9
U Save Botrivier | 2024-11-01 | 6813.9 | 2025-07-23 | 0 | 1 | 6813.9
U Save Botrivier | 2024-12-01 | 7296.3 | 2025-07-23 | 0 | 1 | 7296.3
U Save Botrivier | 2025-01-01 | 7299.9 | 2025-07-23 | 0 | 1 | 7299.9
U Save Botrivier | 2025-02-01 | 6223.5 | 2025-07-23 | 0 | 1 | 6223.5
U Save Botrivier | 2025-03-01 | 6048.9 | 2025-07-23 | 0 | 1 | 6048.9
U Save Botrivier | 2025-04-01 | 5130.9 | 2025-07-23 | 0 | 1 | 5130.9
U Save Botrivier | 2025-05-01 | 4621.5 | 2025-07-23 | 0 | 1 | 4621.5
U Save Botrivier | 2025-06-01 | 3931.2 | 2025-07-23 | 0 | 1 | 3931.2
U Save Botrivier | 2025-07-01 | 4065.3 | 2025-07-23 | 0 | 1 | 4065.3
U Save Botrivier | 2025-08-01 | 4723.2 | 2025-07-23 | 0.024641 | 0.99983 | 4722.3825
U Save Botrivier | 2025-09-01 | 5251.5 | 2025-07-23 | 0.10951 | 0.99923 | 5247.4616
U Save Botrivier | 2025-10-01 | 6489.9 | 2025-07-23 | 0.19165 | 0.99865 | 6481.1688
U Save Botrivier | 2025-11-01 | 6813.9 | 2025-07-23 | 0.27652 | 0.99806 | 6800.6771
U Save Botrivier | 2025-12-01 | 7296.3 | 2025-07-23 | 0.35866 | 0.99748 | 7277.9406
U Save Botrivier | 2026-01-01 | 7299.9 | 2025-07-23 | 0.44353 | 0.99689 | 7277.1915
U Save Botrivier | 2026-02-01 | 6223.5 | 2025-07-23 | 0.52841 | 0.9963 | 6200.4422
U Save Botrivier | 2026-03-01 | 6048.9 | 2025-07-23 | 0.60507 | 0.99576 | 6023.2446
U Save Botrivier | 2026-04-01 | 5130.9 | 2025-07-23 | 0.68994 | 0.99517 | 5106.093
U Save Botrivier | 2026-05-01 | 4621.5 | 2025-07-23 | 0.77207 | 0.99459 | 4596.503
U Save Botrivier | 2026-06-01 | 3931.2 | 2025-07-23 | 0.85695 | 0.994 | 3907.6063
U Save Botrivier | 2026-07-01 | 4065.3 | 2025-07-23 | 0.93908 | 0.99343 | 4038.5707
U Save Botrivier | 2026-08-01 | 4723.2 | 2025-07-23 | 1.024 | 0.99283 | 4689.3484
U Save Botrivier | 2026-09-01 | 5251.5 | 2025-07-23 | 1.1088 | 0.99224 | 5210.7544
U Save Botrivier | 2026-10-01 | 6489.9 | 2025-07-23 | 1.191 | 0.99167 | 6435.8315
U Save Botrivier | 2026-11-01 | 6813.9 | 2025-07-23 | 1.2758 | 0.99108 | 6753.1048
U Save Botrivier | 2026-12-01 | 7296.3 | 2025-07-23 | 1.358 | 0.99051 | 7227.0297
Watt Place Rotoflo | 2024-01-01 | 28027.8 | 2023-05-13 | 0.63792 | 0.99553 | 27902.4846
Watt Place Rotoflo | 2024-02-01 | 23853.6 | 2023-05-13 | 0.72279 | 0.99494 | 23732.7941
Watt Place Rotoflo | 2024-03-01 | 24144.3 | 2023-05-13 | 0.80219 | 0.99438 | 24008.6276
Watt Place Rotoflo | 2024-04-01 | 20043 | 2023-05-13 | 0.88706 | 0.99379 | 19918.4948
Watt Place Rotoflo | 2024-05-01 | 19021.5 | 2023-05-13 | 0.9692 | 0.99321 | 18892.4367
Watt Place Rotoflo | 2024-06-01 | 17054.1 | 2023-05-13 | 1.0541 | 0.99262 | 16928.2901
Watt Place Rotoflo | 2024-07-01 | 18900 | 2023-05-13 | 1.1362 | 0.99205 | 18749.7515
Watt Place Rotoflo | 2024-08-01 | 22066.2 | 2023-05-13 | 1.2211 | 0.99146 | 21877.7338
Watt Place Rotoflo | 2024-09-01 | 24526.8 | 2023-05-13 | 1.306 | 0.99087 | 24302.8242
Watt Place Rotoflo | 2024-10-01 | 27256.5 | 2023-05-13 | 1.3881 | 0.9903 | 26992.0189
Watt Place Rotoflo | 2024-11-01 | 26973.9 | 2023-05-13 | 1.473 | 0.98971 | 26696.2399
Watt Place Rotoflo | 2024-12-01 | 29028.6 | 2023-05-13 | 1.5551 | 0.98914 | 28713.2181
Watt Place Rotoflo | 2025-01-01 | 28027.8 | 2023-05-13 | 1.64 | 0.98855 | 27706.7675
Watt Place Rotoflo | 2025-02-01 | 23853.6 | 2023-05-13 | 1.7248 | 0.98796 | 23566.3246
Watt Place Rotoflo | 2025-03-01 | 24144.3 | 2023-05-13 | 1.8015 | 0.98742 | 23840.6818
Watt Place Rotoflo | 2025-04-01 | 20043 | 2023-05-13 | 1.8864 | 0.98684 | 19779.1604
Watt Place Rotoflo | 2025-05-01 | 19021.5 | 2023-05-13 | 1.9685 | 0.98627 | 18760.2798
Watt Place Rotoflo | 2025-06-01 | 17054.1 | 2023-05-13 | 2.0534 | 0.98568 | 16809.8728
Watt Place Rotoflo | 2025-07-01 | 18900 | 2023-05-13 | 2.1355 | 0.98511 | 18618.5927
Watt Place Rotoflo | 2025-08-01 | 22066.2 | 2023-05-13 | 2.2204 | 0.98452 | 21724.6941
Watt Place Rotoflo | 2025-09-01 | 24526.8 | 2023-05-13 | 2.3053 | 0.98394 | 24132.8205
Watt Place Rotoflo | 2025-10-01 | 27256.5 | 2023-05-13 | 2.3874 | 0.98337 | 26803.2036
Watt Place Rotoflo | 2025-11-01 | 26973.9 | 2023-05-13 | 2.4723 | 0.98278 | 26509.4937
Watt Place Rotoflo | 2025-12-01 | 29028.6 | 2023-05-13 | 2.5544 | 0.98222 | 28512.3627
Watt Place Rotoflo | 2026-01-01 | 28027.8 | 2023-05-13 | 2.6393 | 0.98163 | 27512.9524
Watt Place Rotoflo | 2026-02-01 | 23853.6 | 2023-05-13 | 2.7242 | 0.98105 | 23401.4729
Watt Place Rotoflo | 2026-03-01 | 24144.3 | 2023-05-13 | 2.8008 | 0.98052 | 23673.9109
Watt Place Rotoflo | 2026-04-01 | 20043 | 2023-05-13 | 2.8857 | 0.97993 | 19640.8007
Watt Place Rotoflo | 2026-05-01 | 19021.5 | 2023-05-13 | 2.9678 | 0.97937 | 18629.0475
Watt Place Rotoflo | 2026-06-01 | 17054.1 | 2023-05-13 | 3.0527 | 0.97878 | 16692.284
Watt Place Rotoflo | 2026-07-01 | 18900 | 2023-05-13 | 3.1348 | 0.97822 | 18488.3515
Watt Place Rotoflo | 2026-08-01 | 22066.2 | 2023-05-13 | 3.2197 | 0.97764 | 21572.725
Watt Place Rotoflo | 2026-09-01 | 24526.8 | 2023-05-13 | 3.3046 | 0.97705 | 23964.006
Watt Place Rotoflo | 2026-10-01 | 27256.5 | 2023-05-13 | 3.3867 | 0.97649 | 26615.7091
Watt Place Rotoflo | 2026-11-01 | 26973.9 | 2023-05-13 | 3.4716 | 0.97591 | 26324.0538
Watt Place Rotoflo | 2026-12-01 | 29028.6 | 2023-05-13 | 3.5537 | 0.97535 | 28312.9122
Zwartop Golf Course | 2024-01-01 |  | 2023-09-19 | 0.28474 | 0.998
Zwartop Golf Course | 2024-02-01 |  | 2023-09-19 | 0.36961 | 0.99741
Zwartop Golf Course | 2024-03-01 |  | 2023-09-19 | 0.44901 | 0.99685
Zwartop Golf Course | 2024-04-01 |  | 2023-09-19 | 0.53388 | 0.99626
Zwartop Golf Course | 2024-05-01 |  | 2023-09-19 | 0.61602 | 0.99568
Zwartop Golf Course | 2024-06-01 |  | 2023-09-19 | 0.70089 | 0.99509
Zwartop Golf Course | 2024-07-01 |  | 2023-09-19 | 0.78303 | 0.99451
Zwartop Golf Course | 2024-08-01 |  | 2023-09-19 | 0.8679 | 0.99392
Zwartop Golf Course | 2024-09-01 |  | 2023-09-19 | 0.95277 | 0.99333
Zwartop Golf Course | 2024-10-01 |  | 2023-09-19 | 1.0349 | 0.99276
Zwartop Golf Course | 2024-11-01 |  | 2023-09-19 | 1.1198 | 0.99216
Zwartop Golf Course | 2024-12-01 |  | 2023-09-19 | 1.2019 | 0.99159
Zwartop Golf Course | 2025-01-01 |  | 2023-09-19 | 1.2868 | 0.991
Zwartop Golf Course | 2025-02-01 |  | 2023-09-19 | 1.3717 | 0.99041
Zwartop Golf Course | 2025-03-01 |  | 2023-09-19 | 1.4483 | 0.98988
Zwartop Golf Course | 2025-04-01 |  | 2023-09-19 | 1.5332 | 0.98929
Zwartop Golf Course | 2025-05-01 |  | 2023-09-19 | 1.6153 | 0.98872
Zwartop Golf Course | 2025-06-01 |  | 2023-09-19 | 1.7002 | 0.98813
Zwartop Golf Course | 2025-07-01 |  | 2023-09-19 | 1.7823 | 0.98756
Zwartop Golf Course | 2025-08-01 |  | 2023-09-19 | 1.8672 | 0.98697
Zwartop Golf Course | 2025-09-01 |  | 2023-09-19 | 1.9521 | 0.98638
Zwartop Golf Course | 2025-10-01 |  | 2023-09-19 | 2.0342 | 0.98581
Zwartop Golf Course | 2025-11-01 |  | 2023-09-19 | 2.1191 | 0.98522
Zwartop Golf Course | 2025-12-01 |  | 2023-09-19 | 2.2012 | 0.98466
Zwartop Golf Course | 2026-01-01 |  | 2023-09-19 | 2.2861 | 0.98407
Zwartop Golf Course | 2026-02-01 |  | 2023-09-19 | 2.371 | 0.98348
Zwartop Golf Course | 2026-03-01 |  | 2023-09-19 | 2.4476 | 0.98295
Zwartop Golf Course | 2026-04-01 |  | 2023-09-19 | 2.5325 | 0.98237
Zwartop Golf Course | 2026-05-01 |  | 2023-09-19 | 2.6146 | 0.9818
Zwartop Golf Course | 2026-06-01 |  | 2023-09-19 | 2.6995 | 0.98122
Zwartop Golf Course | 2026-07-01 |  | 2023-09-19 | 2.7817 | 0.98065
Zwartop Golf Course | 2026-08-01 |  | 2023-09-19 | 2.8665 | 0.98007
Zwartop Golf Course | 2026-09-01 |  | 2023-09-19 | 2.9514 | 0.97948
Zwartop Golf Course | 2026-10-01 |  | 2023-09-19 | 3.0335 | 0.97892
Zwartop Golf Course | 2026-11-01 |  | 2023-09-19 | 3.1184 | 0.97833
Zwartop Golf Course | 2026-12-01 |  | 2023-09-19 | 3.2005 | 0.97777
Engen Kaalfontein | 2024-01-01 | 17370.9 | 2026-05-20 | 0 | 1 | 17370.9
Engen Kaalfontein | 2024-02-01 | 15077.7 | 2026-05-20 | 0 | 1 | 15077.7
Engen Kaalfontein | 2024-03-01 | 14634 | 2026-05-20 | 0 | 1 | 14634
Engen Kaalfontein | 2024-04-01 | 12420 | 2026-05-20 | 0 | 1 | 12420
Engen Kaalfontein | 2024-05-01 | 11402.1 | 2026-05-20 | 0 | 1 | 11402.1
Engen Kaalfontein | 2024-06-01 | 9989.1 | 2026-05-20 | 0 | 1 | 9989.1
Engen Kaalfontein | 2024-07-01 | 10986.3 | 2026-05-20 | 0 | 1 | 10986.3
Engen Kaalfontein | 2024-08-01 | 13108.77 | 2026-05-20 | 0 | 1 | 13108.77
Engen Kaalfontein | 2024-09-01 | 14833.17 | 2026-05-20 | 0 | 1 | 14833.17
Engen Kaalfontein | 2024-10-01 | 17053.2 | 2026-05-20 | 0 | 1 | 17053.2
Engen Kaalfontein | 2024-11-01 | 17239.5 | 2026-05-20 | 0 | 1 | 17239.5
Engen Kaalfontein | 2024-12-01 | 17465.4 | 2026-05-20 | 0 | 1 | 17465.4
Engen Kaalfontein | 2025-01-01 | 17370.9 | 2026-05-20 | 0 | 1 | 17370.9
Engen Kaalfontein | 2025-02-01 | 15077.7 | 2026-05-20 | 0 | 1 | 15077.7
Engen Kaalfontein | 2025-03-01 | 14634 | 2026-05-20 | 0 | 1 | 14634
Engen Kaalfontein | 2025-04-01 | 12420 | 2026-05-20 | 0 | 1 | 12420
Engen Kaalfontein | 2025-05-01 | 11402.1 | 2026-05-20 | 0 | 1 | 11402.1
Engen Kaalfontein | 2025-06-01 | 9989.1 | 2026-05-20 | 0 | 1 | 9989.1
Engen Kaalfontein | 2025-07-01 | 10986.3 | 2026-05-20 | 0 | 1 | 10986.3
Engen Kaalfontein | 2025-08-01 | 13108.77 | 2026-05-20 | 0 | 1 | 13108.77
Engen Kaalfontein | 2025-09-01 | 14833.17 | 2026-05-20 | 0 | 1 | 14833.17
Engen Kaalfontein | 2025-10-01 | 17053.2 | 2026-05-20 | 0 | 1 | 17053.2
Engen Kaalfontein | 2025-11-01 | 17239.5 | 2026-05-20 | 0 | 1 | 17239.5
Engen Kaalfontein | 2025-12-01 | 17465.4 | 2026-05-20 | 0 | 1 | 17465.4
Engen Kaalfontein | 2026-01-01 | 17370.9 | 2026-05-20 | 0 | 1 | 17370.9
Engen Kaalfontein | 2026-02-01 | 15077.7 | 2026-05-20 | 0 | 1 | 15077.7
Engen Kaalfontein | 2026-03-01 | 14634 | 2026-05-20 | 0 | 1 | 14634
Engen Kaalfontein | 2026-04-01 | 12420 | 2026-05-20 | 0 | 1 | 12420
Engen Kaalfontein | 2026-05-01 | 11402.1 | 2026-05-20 | 0 | 1 | 11402.1
Engen Kaalfontein | 2026-06-01 | 9989.1 | 2026-05-20 | 0.032854 | 0.99977 | 9986.7949
Engen Kaalfontein | 2026-07-01 | 10986.3 | 2026-05-20 | 0.11499 | 0.99919 | 10977.4293
Engen Kaalfontein | 2026-08-01 | 13108.77 | 2026-05-20 | 0.19986 | 0.9986 | 13090.3787
Engen Kaalfontein | 2026-09-01 | 14833.17 | 2026-05-20 | 0.28474 | 0.998 | 14803.5309
Engen Kaalfontein | 2026-10-01 | 17053.2 | 2026-05-20 | 0.36687 | 0.99743 | 17009.3082
Engen Kaalfontein | 2026-11-01 | 17239.5 | 2026-05-20 | 0.45175 | 0.99683 | 17184.88
Engen Kaalfontein | 2026-12-01 | 17465.4 | 2026-05-20 | 0.53388 | 0.99626 | 17400.022
Checkers Lichtenburg | 2024-01-01 | 26451 | 2026-04-17 | 0 | 1 | 26451
Checkers Lichtenburg | 2024-02-01 | 23215.5 | 2026-04-17 | 0 | 1 | 23215.5
Checkers Lichtenburg | 2024-03-01 | 23034.6 | 2026-04-17 | 0 | 1 | 23034.6
Checkers Lichtenburg | 2024-04-01 | 19930.5 | 2026-04-17 | 0 | 1 | 19930.5
Checkers Lichtenburg | 2024-05-01 | 18754.2 | 2026-04-17 | 0 | 1 | 18754.2
Checkers Lichtenburg | 2024-06-01 | 16767.9 | 2026-04-17 | 0 | 1 | 16767.9
Checkers Lichtenburg | 2024-07-01 | 18261 | 2026-04-17 | 0 | 1 | 18261
Checkers Lichtenburg | 2024-08-01 | 21311.1 | 2026-04-17 | 0 | 1 | 21311.1
Checkers Lichtenburg | 2024-09-01 | 23659.2 | 2026-04-17 | 0 | 1 | 23659.2
Checkers Lichtenburg | 2024-10-01 | 26865.9 | 2026-04-17 | 0 | 1 | 26865.9
Checkers Lichtenburg | 2024-11-01 | 27153.9 | 2026-04-17 | 0 | 1 | 27153.9
Checkers Lichtenburg | 2024-12-01 | 27402.3 | 2026-04-17 | 0 | 1 | 27402.3
Checkers Lichtenburg | 2025-01-01 | 26451 | 2026-04-17 | 0 | 1 | 26451
Checkers Lichtenburg | 2025-02-01 | 23215.5 | 2026-04-17 | 0 | 1 | 23215.5
Checkers Lichtenburg | 2025-03-01 | 23034.6 | 2026-04-17 | 0 | 1 | 23034.6
Checkers Lichtenburg | 2025-04-01 | 19930.5 | 2026-04-17 | 0 | 1 | 19930.5
Checkers Lichtenburg | 2025-05-01 | 18754.2 | 2026-04-17 | 0 | 1 | 18754.2
Checkers Lichtenburg | 2025-06-01 | 16767.9 | 2026-04-17 | 0 | 1 | 16767.9
Checkers Lichtenburg | 2025-07-01 | 18261 | 2026-04-17 | 0 | 1 | 18261
Checkers Lichtenburg | 2025-08-01 | 21311.1 | 2026-04-17 | 0 | 1 | 21311.1
Checkers Lichtenburg | 2025-09-01 | 23659.2 | 2026-04-17 | 0 | 1 | 23659.2
Checkers Lichtenburg | 2025-10-01 | 26865.9 | 2026-04-17 | 0 | 1 | 26865.9
Checkers Lichtenburg | 2025-11-01 | 27153.9 | 2026-04-17 | 0 | 1 | 27153.9
Checkers Lichtenburg | 2025-12-01 | 27402.3 | 2026-04-17 | 0 | 1 | 27402.3
Checkers Lichtenburg | 2026-01-01 | 26451 | 2026-04-17 | 0 | 1 | 26451
Checkers Lichtenburg | 2026-02-01 | 23215.5 | 2026-04-17 | 0 | 1 | 23215.5
Checkers Lichtenburg | 2026-03-01 | 23034.6 | 2026-04-17 | 0 | 1 | 23034.6
Checkers Lichtenburg | 2026-04-01 | 19930.5 | 2026-04-17 | 0 | 1 | 19930.5
Checkers Lichtenburg | 2026-05-01 | 18754.2 | 2026-04-17 | 0.03833 | 0.99973 | 18749.1511
Checkers Lichtenburg | 2026-06-01 | 16767.9 | 2026-04-17 | 0.1232 | 0.99913 | 16753.3944
Checkers Lichtenburg | 2026-07-01 | 18261 | 2026-04-17 | 0.20534 | 0.99856 | 18234.6788
Checkers Lichtenburg | 2026-08-01 | 21311.1 | 2026-04-17 | 0.29021 | 0.99796 | 21267.6988
Checkers Lichtenburg | 2026-09-01 | 23659.2 | 2026-04-17 | 0.37509 | 0.99737 | 23596.944
Checkers Lichtenburg | 2026-10-01 | 26865.9 | 2026-04-17 | 0.45722 | 0.99679 | 26779.7505
Checkers Lichtenburg | 2026-11-01 | 27153.9 | 2026-04-17 | 0.54209 | 0.9962 | 27050.6944
Checkers Lichtenburg | 2026-12-01 | 27402.3 | 2026-04-17 | 0.62423 | 0.99562 | 27282.4047
Alpine Heath Resort | 2024-01-01 | 28877.4 | 2026-04-28 | 0 | 1 | 28877.4
Alpine Heath Resort | 2024-02-01 | 25884.9 | 2026-04-28 | 0 | 1 | 25884.9
Alpine Heath Resort | 2024-03-01 | 27341.1 | 2026-04-28 | 0 | 1 | 27341.1
Alpine Heath Resort | 2024-04-01 | 27823.5 | 2026-04-28 | 0 | 1 | 27823.5
Alpine Heath Resort | 2024-05-01 | 29920.5 | 2026-04-28 | 0 | 1 | 29920.5
Alpine Heath Resort | 2024-06-01 | 28644.3 | 2026-04-28 | 0 | 1 | 28644.3
Alpine Heath Resort | 2024-07-01 | 28051.2 | 2026-04-28 | 0 | 1 | 28051.2
Alpine Heath Resort | 2024-08-01 | 31649.4 | 2026-04-28 | 0 | 1 | 31649.4
Alpine Heath Resort | 2024-09-01 | 28250.1 | 2026-04-28 | 0 | 1 | 28250.1
Alpine Heath Resort | 2024-10-01 | 28466.1 | 2026-04-28 | 0 | 1 | 28466.1
Alpine Heath Resort | 2024-11-01 | 28991.7 | 2026-04-28 | 0 | 1 | 28991.7
Alpine Heath Resort | 2024-12-01 | 28903.5 | 2026-04-28 | 0 | 1 | 28903.5
Alpine Heath Resort | 2025-01-01 | 28877.4 | 2026-04-28 | 0 | 1 | 28877.4
Alpine Heath Resort | 2025-02-01 | 25884.9 | 2026-04-28 | 0 | 1 | 25884.9
Alpine Heath Resort | 2025-03-01 | 27341.1 | 2026-04-28 | 0 | 1 | 27341.1
Alpine Heath Resort | 2025-04-01 | 27823.5 | 2026-04-28 | 0 | 1 | 27823.5
Alpine Heath Resort | 2025-05-01 | 29920.5 | 2026-04-28 | 0 | 1 | 29920.5
Alpine Heath Resort | 2025-06-01 | 28644.3 | 2026-04-28 | 0 | 1 | 28644.3
Alpine Heath Resort | 2025-07-01 | 28051.2 | 2026-04-28 | 0 | 1 | 28051.2
Alpine Heath Resort | 2025-08-01 | 31649.4 | 2026-04-28 | 0 | 1 | 31649.4
Alpine Heath Resort | 2025-09-01 | 28250.1 | 2026-04-28 | 0 | 1 | 28250.1
Alpine Heath Resort | 2025-10-01 | 28466.1 | 2026-04-28 | 0 | 1 | 28466.1
Alpine Heath Resort | 2025-11-01 | 28991.7 | 2026-04-28 | 0 | 1 | 28991.7
Alpine Heath Resort | 2025-12-01 | 28903.5 | 2026-04-28 | 0 | 1 | 28903.5
Alpine Heath Resort | 2026-01-01 | 28877.4 | 2026-04-28 | 0 | 1 | 28877.4
Alpine Heath Resort | 2026-02-01 | 25884.9 | 2026-04-28 | 0 | 1 | 25884.9
Alpine Heath Resort | 2026-03-01 | 27341.1 | 2026-04-28 | 0 | 1 | 27341.1
Alpine Heath Resort | 2026-04-01 | 27823.5 | 2026-04-28 | 0 | 1 | 27823.5
Alpine Heath Resort | 2026-05-01 | 29920.5 | 2026-04-28 | 0.0082136 | 0.99994 | 29918.7737
Alpine Heath Resort | 2026-06-01 | 28644.3 | 2026-04-28 | 0.093087 | 0.99935 | 28625.5756
Alpine Heath Resort | 2026-07-01 | 28051.2 | 2026-04-28 | 0.17522 | 0.99877 | 28016.6939
Alpine Heath Resort | 2026-08-01 | 31649.4 | 2026-04-28 | 0.2601 | 0.99817 | 31591.627
Alpine Heath Resort | 2026-09-01 | 28250.1 | 2026-04-28 | 0.34497 | 0.99758 | 28181.7251
Alpine Heath Resort | 2026-10-01 | 28466.1 | 2026-04-28 | 0.4271 | 0.997 | 28380.8227
Alpine Heath Resort | 2026-11-01 | 28991.7 | 2026-04-28 | 0.51198 | 0.99641 | 28887.6201
Alpine Heath Resort | 2026-12-01 | 28903.5 | 2026-04-28 | 0.59411 | 0.99584 | 28783.1249
Usave Naboomspruit | 2026-07-01 | 4644.9 | 2026-06-12 | 0.052019 | 0.99963 | 4643.203
Usave Naboomspruit | 2026-08-01 | 5254.2 | 2026-06-12 | 0.13689 | 0.99904 | 5249.1499
Usave Naboomspruit | 2026-09-01 | 5567.4 | 2026-06-12 | 0.22177 | 0.99844 | 5558.7337
Usave Naboomspruit | 2026-10-01 | 6030.9 | 2026-06-12 | 0.3039 | 0.99787 | 6018.039
Usave Naboomspruit | 2026-11-01 | 5897.7 | 2026-06-12 | 0.38877 | 0.99727 | 5881.6154
Usave Naboomspruit | 2026-12-01 | 5989.5 | 2026-06-12 | 0.47091 | 0.9967 | 5969.7197
Formulas:
Commissioned Date = XLOOKUP(expected_production[[#This Row],[Site Name]],Table1[[Site Name ]],Table1[Commisioned Date],"")

## performance
Site Name | Date | Measured (kWh) | Expected (kWh) | Performance | PF Band | Discussion
21 Melrose | 2024-01-01 | 1815 | 2355.6475 | 77.05% | Moderate
21 Melrose | 2024-02-01 | 2295 | 2661.7073 | 86.22% | Moderate
21 Melrose | 2024-03-01 | 2474 | 2167.1261 | 114.2% | Expected
21 Melrose | 2024-04-01 | 2136 | 1858.7252 | 114.9% | Expected
21 Melrose | 2024-05-01 | 2212 | 1806.7951 | 122.4% | Expected
21 Melrose | 2024-06-01 | 1863 | 1614 | 115.4% | Expected
21 Melrose | 2024-07-01 | 1943 | 1796.6559 | 108.1% | Expected
21 Melrose | 2024-08-01 | 1710 | 2094.8492 | 81.63% | Moderate
21 Melrose | 2024-09-01 | 1579 | 2250.2646 | 70.17% | Moderate
21 Melrose | 2024-10-01 | 1593 | 2379.7412 | 66.94% | Poor
21 Melrose | 2024-11-01 | 1794 | 2327.6446 | 77.07% | Moderate
21 Melrose | 2024-12-01 | 1794 | 2450.7032 | 73.2% | Moderate
21 Melrose | 2025-01-01 | 1992 | 2339.1242 | 85.16% | Moderate
21 Melrose | 2025-02-01 | 1458 | 2643.0373 | 55.16% | Poor
21 Melrose | 2025-03-01 | 1382 | 2151.9666 | 64.22% | Poor
21 Melrose | 2025-04-01 | 1183 | 1845.723 | 64.09% | Poor
21 Melrose | 2025-05-01 | 1860 | 1794.1562 | 103.7% | Expected
21 Melrose | 2025-06-01 | 1756.6 | 1602.7097 | 109.6% | Expected
21 Melrose | 2025-07-01 | 1742 | 1784.0879 | 97.64% | Expected
21 Melrose | 2025-08-01 | 1613 | 2080.1953 | 77.54% | Moderate
21 Melrose | 2025-09-01 | 1358.7 | 2234.5235 | 60.8% | Poor
21 Melrose | 2025-10-01 | 1601 | 2363.0944 | 67.75% | Poor
21 Melrose | 2025-11-01 | 1444 | 2311.3622 | 62.47% | Poor
21 Melrose | 2025-12-01 | 1375 | 2433.5599 | 56.5% | Poor
21 Melrose | 2026-01-01 | 1549 | 2322.7615 | 66.69% | Poor
21 Melrose | 2026-02-01 | 1362 | 2624.5486 | 51.89% | Poor
21 Melrose | 2026-03-01 | 1237 | 2136.9131 | 57.89% | Poor
21 Melrose | 2026-04-01 | 830 | 1832.8117 | 45.29% | Poor
21 Melrose | 2026-05-01 | 1169.9 | 1781.6057 | 65.67% | Poor
21 Melrose | 2026-06-01 | 1287 | 1591.4984 | 80.87% | Moderate
21 Melrose | 2026-07-01 | 1638 | 1771.6078 | 92.46% | Expected | NO
21 Melrose | 2026-08-01 | 1374 | 2065.6438 | 66.52% | Poor | NO
21 Melrose | 2026-09-01 | 1161.6 | 2218.8925 | 52.35% | Poor | NO
21 Melrose | 2026-10-01 |  | 2346.564
21 Melrose | 2026-11-01 |  | 2295.1937
21 Melrose | 2026-12-01 |  | 2416.5366
African Global Plastics | 2024-01-01 | 23024 | 22474.3721 | 102.4% | Expected
African Global Plastics | 2024-02-01 | 23235 | 19737.8612 | 117.7% | Expected
African Global Plastics | 2024-03-01 | 23235 | 20088.0404 | 115.7% | Expected
African Global Plastics | 2024-04-01 | 19307 | 16704.7042 | 115.6% | Expected
African Global Plastics | 2024-05-01 | 18418 | 15905.5757 | 115.8% | Expected
African Global Plastics | 2024-06-01 | 15949 | 14298.847 | 111.5% | Expected
African Global Plastics | 2024-07-01 | 17174 | 15822.8402 | 108.5% | Expected
African Global Plastics | 2024-08-01 | 13588 | 18417.5872 | 73.78% | Moderate
African Global Plastics | 2024-09-01 | 20254 | 20271.3464 | 99.91% | Expected
African Global Plastics | 2024-10-01 | 27693 | 22162.3907 | 125% | Expected
African Global Plastics | 2024-11-01 | 24041 | 22347.6498 | 107.6% | Expected
African Global Plastics | 2024-12-01 | 25076 | 23581.7005 | 106.3% | Expected
African Global Plastics | 2025-01-01 | 22439 | 22316.7296 | 100.5% | Expected
African Global Plastics | 2025-02-01 | 14790 | 19599.4135 | 75.46% | Moderate
African Global Plastics | 2025-03-01 | 15371 | 19947.5201 | 77.06% | Moderate
African Global Plastics | 2025-04-01 | 13930 | 16587.851 | 83.98% | Moderate
African Global Plastics | 2025-05-01 | 15263 | 15794.3126 | 96.64% | Expected
African Global Plastics | 2025-06-01 | 11722.16 | 14198.8233 | 82.56% | Moderate
African Global Plastics | 2025-07-01 | 3209 | 15712.1558 | 20.42% | Poor
African Global Plastics | 2025-08-01 | 11143 | 18288.752 | 60.93% | Poor
African Global Plastics | 2025-09-01 | 11503 | 20129.5437 | 57.14% | Poor
African Global Plastics | 2025-10-01 | 12856 | 22007.3598 | 58.42% | Poor
African Global Plastics | 2025-11-01 | 11518 | 22191.3229 | 51.9% | Poor
African Global Plastics | 2025-12-01 | 12208 | 23416.7412 | 52.13% | Poor
African Global Plastics | 2026-01-01 | 14027 | 22160.6191 | 63.3% | Poor
African Global Plastics | 2026-02-01 | 12261 | 19462.3111 | 63% | Poor
African Global Plastics | 2026-03-01 | 10788 | 19807.9827 | 54.46% | Poor
African Global Plastics | 2026-04-01 | 9392.09 | 16471.8153 | 57.02% | Poor
African Global Plastics | 2026-05-01 | 11425.9 | 15683.8278 | 72.85% | Moderate
African Global Plastics | 2026-06-01 | 10184.42 | 14099.4994 | 72.23% | Moderate
African Global Plastics | 2026-07-01 | 13136.5304 | 15602.2457 | 84.2% | Moderate | NO
African Global Plastics | 2026-08-01 | 13435.047 | 18160.8181 | 73.98% | Moderate | NO
African Global Plastics | 2026-09-01 | 12622.0164 | 19988.733 | 63.15% | Poor | NO
African Global Plastics | 2026-10-01 |  | 21853.4133
African Global Plastics | 2026-11-01 |  | 22036.0896
African Global Plastics | 2026-12-01 |  | 23252.9358
Alpine Heath Residential | 2024-01-01 |  | 4801.5
Alpine Heath Residential | 2024-02-01 |  | 4303.8
Alpine Heath Residential | 2024-03-01 |  | 4545.9
Alpine Heath Residential | 2024-04-01 |  | 4619.7
Alpine Heath Residential | 2024-05-01 |  | 4990.5
Alpine Heath Residential | 2024-06-01 |  | 4761.9
Alpine Heath Residential | 2024-07-01 |  | 4680.9
Alpine Heath Residential | 2024-08-01 |  | 5249.7
Alpine Heath Residential | 2024-09-01 |  | 4694.4
Alpine Heath Residential | 2024-10-01 |  | 4732.2
Alpine Heath Residential | 2024-11-01 |  | 4822.2
Alpine Heath Residential | 2024-12-01 |  | 4805.1
Alpine Heath Residential | 2025-01-01 | 2400 | 4801.5 | 49.98% | Poor
Alpine Heath Residential | 2025-02-01 | 3000 | 4301.2348 | 69.75% | Poor
Alpine Heath Residential | 2025-03-01 | 3144 | 4540.7447 | 69.24% | Poor
Alpine Heath Residential | 2025-04-01 | 2310 | 4611.7106 | 50.09% | Poor
Alpine Heath Residential | 2025-05-01 | 3866 | 4978.9958 | 77.65% | Moderate
Alpine Heath Residential | 2025-06-01 | 3102 | 4748.0911 | 65.33% | Poor
Alpine Heath Residential | 2025-07-01 |  | 4664.6339
Alpine Heath Residential | 2025-08-01 | 4721 | 5228.3392 | 90.3% | Expected
Alpine Heath Residential | 2025-09-01 | 4200 | 4672.5121 | 89.89% | Moderate
Alpine Heath Residential | 2025-10-01 | 3499 | 4707.419 | 74.33% | Moderate
Alpine Heath Residential | 2025-11-01 | 4045 | 4794.0886 | 84.37% | Moderate
Alpine Heath Residential | 2025-12-01 | 4277 | 4774.3329 | 89.58% | Moderate
Alpine Heath Residential | 2026-01-01 | 3071 | 4767.9124 | 64.41% | Poor
Alpine Heath Residential | 2026-02-01 | 3013 | 4271.1467 | 70.54% | Moderate
Alpine Heath Residential | 2026-03-01 | 2340.8 | 4508.9811 | 51.91% | Poor
Alpine Heath Residential | 2026-04-01 | 1505.4 | 4579.4507 | 32.87% | Poor
Alpine Heath Residential | 2026-05-01 | 1467 | 4944.1666 | 29.67% | Poor
Alpine Heath Residential | 2026-06-01 | 2778 | 4714.8771 | 58.92% | Poor
Alpine Heath Residential | 2026-07-01 | 2644 | 4632.0037 | 57.08% | Poor | NO
Alpine Heath Residential | 2026-08-01 | 2758 | 5191.7658 | 53.12% | Poor | NO
Alpine Heath Residential | 2026-09-01 | 2338 | 4639.8268 | 50.39% | Poor | NO
Alpine Heath Residential | 2026-10-01 |  | 4674.4896
Alpine Heath Residential | 2026-11-01 |  | 4760.5529
Alpine Heath Residential | 2026-12-01 |  | 4740.9353
BP Parys | 2024-01-01 |  | 8151.3
BP Parys | 2024-02-01 |  | 7235.1
BP Parys | 2024-03-01 |  | 7075.8
BP Parys | 2024-04-01 |  | 5754.6
BP Parys | 2024-05-01 |  | 5424.3
BP Parys | 2024-06-01 |  | 4787.1
BP Parys | 2024-07-01 |  | 5360.4
BP Parys | 2024-08-01 |  | 6363
BP Parys | 2024-09-01 |  | 7218.9
BP Parys | 2024-10-01 |  | 7839
BP Parys | 2024-11-01 |  | 8191.8
BP Parys | 2024-12-01 |  | 8225.1104
BP Parys | 2025-01-01 | 5900 | 8143.7786 | 72.45% | Moderate
BP Parys | 2025-02-01 | 4277 | 7224.1157 | 59.2% | Poor
BP Parys | 2025-03-01 | 4770 | 7061.254 | 67.55% | Poor
BP Parys | 2025-04-01 | 3375 | 5739.3472 | 58.8% | Poor
BP Parys | 2025-05-01 | 3507 | 5406.8022 | 64.86% | Poor
BP Parys | 2025-06-01 | 2400 | 4768.8136 | 50.33% | Poor
BP Parys | 2025-07-01 | 2169 | 5336.8436 | 40.64% | Poor
BP Parys | 2025-08-01 | 968.6 | 6331.2618 | 15.3% | Poor
BP Parys | 2025-09-01 | 2001.5 | 7178.6115 | 27.88% | Poor
BP Parys | 2025-10-01 | 3111 | 7790.7544 | 39.93% | Poor
BP Parys | 2025-11-01 | 1605 | 8136.5306 | 19.73% | Poor
BP Parys | 2025-12-01 |  | 8167.5739
BP Parys | 2026-01-01 |  | 8086.811
BP Parys | 2026-02-01 | 6068 | 7173.5813 | 84.59% | Moderate
BP Parys | 2026-03-01 | 4800 | 7011.8589 | 68.46% | Poor
BP Parys | 2026-04-01 | 4318 | 5699.1991 | 75.77% | Moderate
BP Parys | 2026-05-01 | 3727.7 | 5368.9804 | 69.43% | Poor
BP Parys | 2026-06-01 | 3149 | 4735.4547 | 66.5% | Poor
Alpine Heath Resort | 2026-07-01 | 27942 | 28016.6939 | 99.73% | Expected | NO
BP Parys | 2026-08-01 | 3313 | 6286.9732 | 52.7% | Poor | YES
BP Parys | 2026-09-01 | 4204.16 | 7128.3954 | 58.98% | Poor | NO
BP Parys | 2026-10-01 |  | 7736.2563
BP Parys | 2026-11-01 |  | 8079.6137
BP Parys | 2026-12-01 |  | 8110.4398
Bendstore Plaza Shops | 2024-01-01 | 7453 | 16142.5424 | 46.17% | Poor
Bendstore Plaza Shops | 2024-02-01 | 10174 | 13875.5601 | 73.32% | Moderate
Bendstore Plaza Shops | 2024-03-01 | 12197 | 15331.7194 | 79.55% | Moderate
Bendstore Plaza Shops | 2024-04-01 | 9850 | 14750.6798 | 66.78% | Poor
Bendstore Plaza Shops | 2024-05-01 | 10329 | 14272.4558 | 72.37% | Moderate
Bendstore Plaza Shops | 2024-06-01 | 9684 | 12916.2141 | 74.98% | Moderate
Bendstore Plaza Shops | 2024-07-01 | 10193 | 13586.4467 | 75.02% | Moderate
Bendstore Plaza Shops | 2024-08-01 | 9840 | 15174.9119 | 64.84% | Poor
Bendstore Plaza Shops | 2024-09-01 | 3277 | 15246.4877 | 21.49% | Poor
Bendstore Plaza Shops | 2024-10-01 | 12496 | 14635.0681 | 85.38% | Moderate
Bendstore Plaza Shops | 2024-11-01 | 12909 | 14502.2012 | 89.01% | Moderate
Bendstore Plaza Shops | 2024-12-01 | 12587 | 15932.4055 | 79% | Moderate
Bendstore Plaza Shops | 2025-01-01 | 13816 | 16029.3134 | 86.19% | Moderate
Bendstore Plaza Shops | 2025-02-01 | 11397 | 13778.2325 | 82.72% | Moderate
Bendstore Plaza Shops | 2025-03-01 | 12740 | 15224.4706 | 83.68% | Moderate
Bendstore Plaza Shops | 2025-04-01 | 9167 | 14647.4954 | 62.58% | Poor
Bendstore Plaza Shops | 2025-05-01 | 9630 | 14172.6167 | 67.95% | Poor
Bendstore Plaza Shops | 2025-06-01 | 9081.44 | 12825.8622 | 70.81% | Moderate
Bendstore Plaza Shops | 2025-07-01 | 9450 | 13491.4065 | 70.04% | Moderate
Bendstore Plaza Shops | 2025-08-01 | 10695 | 15068.76 | 70.97% | Moderate
Bendstore Plaza Shops | 2025-09-01 | 8585 | 15139.8351 | 56.7% | Poor
Bendstore Plaza Shops | 2025-10-01 | 9077.9 | 14532.6925 | 62.47% | Poor
Bendstore Plaza Shops | 2025-11-01 | 10382 | 14400.755 | 72.09% | Moderate
Bendstore Plaza Shops | 2025-12-01 | 13631 | 15820.9547 | 86.16% | Moderate
Bendstore Plaza Shops | 2026-01-01 | 11296 | 15917.1848 | 70.97% | Moderate
Bendstore Plaza Shops | 2026-02-01 | 11241.7805 | 13681.8506 | 82.17% | Moderate
Bendstore Plaza Shops | 2026-03-01 | 10628 | 15117.972 | 70.3% | Moderate
Bendstore Plaza Shops | 2026-04-01 | 8541.19 | 14545.0329 | 58.72% | Poor
Bendstore Plaza Shops | 2026-05-01 | 9563.61 | 14073.4761 | 67.95% | Poor
Bendstore Plaza Shops | 2026-06-01 | 7968.17 | 12736.1424 | 62.56% | Poor
Bendstore Plaza Shops | 2026-07-01 | 10351.41 | 13397.031 | 77.27% | Moderate | NO
Bendstore Plaza Shops | 2026-08-01 | 11244.861 | 14963.3506 | 75.15% | Moderate | NO
Bendstore Plaza Shops | 2026-09-01 | 8314.17 | 15033.9285 | 55.3% | Poor | NO
Bendstore Plaza Shops | 2026-10-01 |  | 14431.033
Bendstore Plaza Shops | 2026-11-01 |  | 14300.0185
Bendstore Plaza Shops | 2026-12-01 |  | 15710.2836
Bendstore Spar | 2024-01-01 | 55000 | 51295.0004 | 107.2% | Expected
Bendstore Spar | 2024-02-01 | 46799 | 44060.0532 | 106.2% | Expected
Bendstore Spar | 2024-03-01 | 40582 | 48664.3381 | 83.39% | Moderate
Bendstore Spar | 2024-04-01 | 39615 | 46749.9908 | 84.74% | Moderate
Bendstore Spar | 2024-05-01 | 39494 | 45150.6295 | 87.47% | Moderate
Bendstore Spar | 2024-06-01 | 35378 | 40808.7544 | 86.69% | Moderate
Bendstore Spar | 2024-07-01 | 38293 | 42945.6375 | 89.17% | Moderate
Bendstore Spar | 2024-08-01 | 38554 | 48050.6978 | 80.24% | Moderate
Bendstore Spar | 2024-09-01 | 37782 | 48356.7435 | 78.13% | Moderate
Bendstore Spar | 2024-10-01 | 47662 | 46485.3238 | 102.5% | Expected
Bendstore Spar | 2024-11-01 | 48184 | 46099.4341 | 104.5% | Expected
Bendstore Spar | 2024-12-01 | 44138 | 50295.7431 | 87.76% | Moderate
Bendstore Spar | 2025-01-01 | 52262 | 50935.2007 | 102.6% | Expected
Bendstore Spar | 2025-02-01 | 40904 | 43751.0017 | 93.49% | Expected
Bendstore Spar | 2025-03-01 | 45751 | 48323.92 | 94.68% | Expected
Bendstore Spar | 2025-04-01 | 30758 | 46422.9641 | 66.26% | Poor
Bendstore Spar | 2025-05-01 | 34925 | 44834.7906 | 77.9% | Moderate
Bendstore Spar | 2025-06-01 | 29716.71 | 40523.288 | 73.33% | Moderate
Bendstore Spar | 2025-07-01 | 27958 | 42645.2231 | 65.56% | Poor
Bendstore Spar | 2025-08-01 | 30682 | 47714.5724 | 64.3% | Poor
Bendstore Spar | 2025-09-01 | 44171 | 48018.4771 | 91.99% | Expected
Bendstore Spar | 2025-10-01 | 53279 | 46160.1485 | 115.4% | Expected
Bendstore Spar | 2025-11-01 | 44434 | 45776.9581 | 97.07% | Expected
Bendstore Spar | 2025-12-01 | 54661 | 49943.9131 | 109.4% | Expected
Bendstore Spar | 2026-01-01 | 47457 | 50578.8975 | 93.83% | Expected
Bendstore Spar | 2026-02-01 | 49608.8533 | 43444.9536 | 114.2% | Expected
Bendstore Spar | 2026-03-01 | 41208 | 47985.8833 | 85.88% | Moderate
Bendstore Spar | 2026-04-01 | 36936.35 | 46098.225 | 80.13% | Moderate
Bendstore Spar | 2026-05-01 | 38743.02 | 44521.1612 | 87.02% | Moderate
Bendstore Spar | 2026-06-01 | 31578.49 | 40239.8184 | 78.48% | Moderate
Bendstore Spar | 2026-07-01 | 39160 | 42346.9101 | 92.47% | Expected | NO
Bendstore Spar | 2026-08-01 | 44122.4391 | 47380.7982 | 93.12% | Expected | NO
Mdluli | 2026-09-01 | 10471.23 | 14939.897 | 70.09% | Moderate | NO
Bendstore Spar | 2026-10-01 |  | 45837.2479
Bendstore Spar | 2026-11-01 |  | 45456.738
Bendstore Spar | 2026-12-01 |  | 49594.5441
Beyerskloof | 2024-01-01 | 8244 | 13781.7979 | 59.82% | Poor
Beyerskloof | 2024-02-01 | 7277 | 11348.6632 | 64.12% | Poor
Beyerskloof | 2024-03-01 | 6614 | 10864.2715 | 60.88% | Poor
Beyerskloof | 2024-04-01 | 4053 | 7811.5063 | 51.88% | Poor
Beyerskloof | 2024-05-01 | 3743 | 5937.3774 | 63.04% | Poor
Beyerskloof | 2024-06-01 | 3473 | 5148.9393 | 67.45% | Poor
Beyerskloof | 2024-07-01 | 4260 | 5543.1234 | 76.85% | Moderate
Beyerskloof | 2024-08-01 | 5497 | 6929.4784 | 79.33% | Moderate
Beyerskloof | 2024-09-01 | 2600 | 8900.6932 | 29.21% | Poor
Beyerskloof | 2024-10-01 | 8200 | 11251.0031 | 72.88% | Moderate
Beyerskloof | 2024-11-01 | 6700 | 12634.1826 | 53.03% | Poor
Beyerskloof | 2024-12-01 | 8100 | 13784.4648 | 58.76% | Poor
Beyerskloof | 2025-01-01 | 9900 | 13685.1279 | 72.34% | Moderate
Beyerskloof | 2025-02-01 | 9200 | 11269.06 | 81.64% | Moderate
Beyerskloof | 2025-03-01 | 4480 | 10788.2735 | 41.53% | Poor
Beyerskloof | 2025-04-01 | 4096 | 7756.863 | 52.8% | Poor
Beyerskloof | 2025-05-01 | 3388 | 5895.8441 | 57.46% | Poor
Beyerskloof | 2025-06-01 | 2306.13 | 5112.9213 | 45.1% | Poor
Beyerskloof | 2025-07-01 | 2919 | 5504.348 | 53.03% | Poor
Beyerskloof | 2025-08-01 | 5355 | 6881.0051 | 77.82% | Moderate
Beyerskloof | 2025-09-01 | 8600 | 8838.4309 | 97.3% | Expected
Beyerskloof | 2025-10-01 | 10599 | 11172.2998 | 94.87% | Expected
Beyerskloof | 2025-11-01 | 12569 | 12545.8036 | 100.2% | Expected
Beyerskloof | 2025-12-01 | 13572 | 13688.0393 | 99.15% | Expected
Beyerskloof | 2026-01-01 | 13416 | 13589.3973 | 98.72% | Expected
Beyerskloof | 2026-02-01 | 10034.177 | 11190.2304 | 89.67% | Moderate
Beyerskloof | 2026-03-01 | 10400 | 10712.8071 | 97.08% | Expected
Beyerskloof | 2026-04-01 | 7344.6 | 7702.602 | 95.35% | Expected
Beyerskloof | 2026-05-01 | 5508.9 | 5854.6013 | 94.1% | Expected
Beyerskloof | 2026-06-01 | 5030.25 | 5077.1553 | 99.08% | Expected
Beyerskloof | 2026-07-01 | 5251.38 | 5465.8439 | 96.08% | Expected | NO
Beyerskloof | 2026-08-01 | 6385.91 | 6832.8709 | 93.46% | Expected | NO
Beyerskloof | 2026-09-01 | 8881.77 | 8776.6041 | 101.2% | Expected | NO
Beyerskloof | 2026-10-01 |  | 11094.1471
Beyerskloof | 2026-11-01 |  | 12458.0429
Beyerskloof | 2026-12-01 |  | 13592.2884
Buffalo Rock | 2024-01-01 |  | 2197.6881
Buffalo Rock | 2024-02-01 |  | 1978.2663
Buffalo Rock | 2024-03-01 |  | 2120.696
Buffalo Rock | 2024-04-01 |  | 1760.814
Buffalo Rock | 2024-05-01 |  | 1624.4982
Buffalo Rock | 2024-06-01 |  | 1473.087
Buffalo Rock | 2024-07-01 |  | 1603.799
Buffalo Rock | 2024-08-01 |  | 1753.1096
Buffalo Rock | 2024-09-01 |  | 1855.7584
Buffalo Rock | 2024-10-01 |  | 1886.8502
Buffalo Rock | 2024-11-01 |  | 1820.5466
Buffalo Rock | 2024-12-01 |  | 1969.4109
Buffalo Rock | 2025-01-01 |  | 2182.2728
Buffalo Rock | 2025-02-01 |  | 1964.3901
Buffalo Rock | 2025-03-01 |  | 2105.8612
Buffalo Rock | 2025-04-01 |  | 1748.4967
Buffalo Rock | 2025-05-01 |  | 1613.1345
Buffalo Rock | 2025-06-01 |  | 1462.7825
Buffalo Rock | 2025-07-01 |  | 1592.5801
Buffalo Rock | 2025-08-01 |  | 1740.8462
Buffalo Rock | 2025-09-01 |  | 1842.7769
Buffalo Rock | 2025-10-01 | 1109 | 1873.6512 | 59.19% | Poor
Buffalo Rock | 2025-11-01 |  | 1807.8115
Buffalo Rock | 2025-12-01 |  | 1955.6344
Buffalo Rock | 2026-01-01 |  | 2167.0073
Buffalo Rock | 2026-02-01 |  | 1950.6487
Buffalo Rock | 2026-03-01 |  | 2091.1302
Buffalo Rock | 2026-04-01 |  | 1736.2656
Buffalo Rock | 2026-05-01 |  | 1601.8502
Buffalo Rock | 2026-06-01 |  | 1452.55
BP Parys | 2026-07-01 | 3615 | 5299.5112 | 68.21% | Poor | NO
Buffalo Rock | 2026-08-01 | 926 | 1728.6686 | 53.57% | Poor | YES
Buffalo Rock | 2026-09-01 | 668.4 | 1829.8863 | 36.53% | Poor | NO
Buffalo Rock | 2026-10-01 |  | 1860.5446
Buffalo Rock | 2026-11-01 |  | 1795.1654
Buffalo Rock | 2026-12-01 |  | 1941.9543
Checkers De Aar | 2024-01-01 |  | 26689.5
Checkers De Aar | 2024-02-01 |  | 20674.8
Checkers De Aar | 2024-03-01 |  | 20095.2
Checkers De Aar | 2024-04-01 |  | 16286.4
Checkers De Aar | 2024-05-01 |  | 13518.9
Checkers De Aar | 2024-06-01 |  | 11864.7
Checkers De Aar | 2024-07-01 |  | 13582.5678
Checkers De Aar | 2024-08-01 |  | 17090.5833
Checkers De Aar | 2024-09-01 |  | 19473.9886
Checkers De Aar | 2024-10-01 |  | 24027.1735
Checkers De Aar | 2024-11-01 |  | 25815.8135
Checkers De Aar | 2024-12-01 |  | 27897.0348
Checkers De Aar | 2025-01-01 | 31100 | 26582.4353 | 117% | Expected
Checkers De Aar | 2025-02-01 | 23180 | 20579.5899 | 112.6% | Expected
Checkers De Aar | 2025-03-01 | 20838 | 19991.8904 | 104.2% | Expected
Checkers De Aar | 2025-04-01 | 16626 | 16193.0143 | 102.7% | Expected
Checkers De Aar | 2025-05-01 | 15218 | 13433.63 | 113.3% | Expected
Checkers De Aar | 2025-06-01 | 12425.8 | 11782.8368 | 105.5% | Expected
Checkers De Aar | 2025-07-01 | 13246 | 13487.5547 | 98.21% | Expected
Checkers De Aar | 2025-08-01 | 16953 | 16971.0308 | 99.89% | Expected
Checkers De Aar | 2025-09-01 | 19367 | 19337.7636 | 100.2% | Expected
Checkers De Aar | 2025-10-01 | 25648.18 | 23859.098 | 107.5% | Expected
Checkers De Aar | 2025-11-01 | 26677 | 25635.2261 | 104.1% | Expected
Checkers De Aar | 2025-12-01 | 30286 | 27701.8888 | 109.3% | Expected
Checkers De Aar | 2026-01-01 | 30117 | 26396.4851 | 114.1% | Expected
Checkers De Aar | 2026-02-01 | 22084 | 20435.631 | 108.1% | Expected
Checkers De Aar | 2026-03-01 | 22201 | 19852.0426 | 111.8% | Expected
Checkers De Aar | 2026-04-01 | 16660.7 | 16079.7405 | 103.6% | Expected
Checkers De Aar | 2026-05-01 | 13372.29 | 13339.6587 | 100.2% | Expected
Checkers De Aar | 2026-06-01 | 9763.7 | 11700.4132 | 83.45% | Moderate
Buffalo Rock | 2026-07-01 | 719 | 1581.4396 | 45.46% | Poor | NO
Checkers De Aar | 2026-08-01 | 12651.55 | 16852.3147 | 75.07% | Moderate | YES
Usave Naboomspruit | 2026-09-01 | 4005.8959 | 5558.7337 | 72.06% | Moderate | NO
Checkers De Aar | 2026-10-01 |  | 23692.1983
Checkers De Aar | 2026-11-01 |  | 25455.9019
Checkers De Aar | 2026-12-01 |  | 27508.1078
Checkers Silverlakes Gen | 2024-01-01 |  | 21105
Checkers Silverlakes Gen | 2024-02-01 |  | 18220.5
Checkers Silverlakes Gen | 2024-03-01 |  | 18368.1
Checkers Silverlakes Gen | 2024-04-01 |  | 15103.8
Checkers Silverlakes Gen | 2024-05-01 |  | 14130
Checkers Silverlakes Gen | 2024-06-01 |  | 12619.8
Checkers Silverlakes Gen | 2024-07-01 |  | 14002.2
Checkers Silverlakes Gen | 2024-08-01 |  | 16641.9
Checkers Silverlakes Gen | 2024-09-01 |  | 18626.4
Checkers Silverlakes Gen | 2024-10-01 |  | 20503.8
Checkers Silverlakes Gen | 2024-11-01 |  | 20601
Checkers Silverlakes Gen | 2024-12-01 |  | 22024.8
Checkers Silverlakes Gen | 2025-01-01 |  | 21105
Checkers Silverlakes Gen | 2025-02-01 |  | 18220.5
Checkers Silverlakes Gen | 2025-03-01 | 17913 | 18368.1 | 97.52% | Expected
Checkers Silverlakes Gen | 2025-04-01 | 14938 | 15103.8 | 98.9% | Expected
Checkers Silverlakes Gen | 2025-05-01 | 18066 | 14130 | 127.9% | Expected
Checkers Silverlakes Gen | 2025-06-01 | 12974.1 | 12619.8 | 102.8% | Expected
Checkers Silverlakes Gen | 2025-07-01 | 13938 | 14002.2 | 99.54% | Expected
Checkers Silverlakes Gen | 2025-08-01 | 18460 | 16641.9 | 110.9% | Expected
Checkers Silverlakes Gen | 2025-09-01 | 17970 | 18626.4 | 96.48% | Expected
Checkers Silverlakes Gen | 2025-10-01 | 22232 | 20503.8 | 108.4% | Expected
Checkers Silverlakes Gen | 2025-11-01 | 17351 | 20601 | 84.22% | Moderate
Checkers Silverlakes Gen | 2025-12-01 | 21073 | 22024.8 | 95.68% | Expected
Checkers Silverlakes Gen | 2026-01-01 | 22123 | 21105 | 104.8% | Expected
Checkers Silverlakes Gen | 2026-02-01 | 16600 | 18220.5 | 91.11% | Expected
Checkers Silverlakes Gen | 2026-03-01 | 17500 | 18368.1 | 95.27% | Expected
Checkers Silverlakes Gen | 2026-04-01 | 15400 | 15103.8 | 102% | Expected
Checkers Silverlakes Gen | 2026-05-01 | 15615 | 14130 | 110.5% | Expected
Checkers Silverlakes Gen | 2026-06-01 | 12373.57 | 12619.8 | 98.05% | Expected
Checkers De Aar | 2026-07-01 | 8756.05 | 13393.2062 | 65.38% | Poor | YES
Checkers Silverlakes Gen | 2026-08-01 | 15825 | 16641.9 | 95.09% | Expected | NO
Checkers Silverlakes Gen | 2026-09-01 | 18200 | 18626.4 | 97.71% | Expected | NO
Checkers Silverlakes Gen | 2026-10-01 |  | 20503.8
Checkers Silverlakes Gen | 2026-11-01 |  | 20601
Checkers Silverlakes Gen | 2026-12-01 |  | 22024.8
Checkers Silverlakes No Gen | 2024-01-01 |  | 21105
Checkers Silverlakes No Gen | 2024-02-01 |  | 18220.5
Checkers Silverlakes No Gen | 2024-03-01 |  | 18368.1
Checkers Silverlakes No Gen | 2024-04-01 |  | 15103.8
Checkers Silverlakes No Gen | 2024-05-01 |  | 14130
Checkers Silverlakes No Gen | 2024-06-01 |  | 12619.8
Checkers Silverlakes No Gen | 2024-07-01 |  | 14002.2
Checkers Silverlakes No Gen | 2024-08-01 |  | 16641.9
Checkers Silverlakes No Gen | 2024-09-01 |  | 18626.4
Checkers Silverlakes No Gen | 2024-10-01 |  | 20503.8
Checkers Silverlakes No Gen | 2024-11-01 |  | 20601
Checkers Silverlakes No Gen | 2024-12-01 |  | 22024.8
Checkers Silverlakes No Gen | 2025-01-01 |  | 21105
Checkers Silverlakes No Gen | 2025-02-01 |  | 18220.5
Checkers Silverlakes No Gen | 2025-03-01 | 16558 | 18368.1 | 90.15% | Expected
Checkers Silverlakes No Gen | 2025-04-01 | 13087 | 15103.8 | 86.65% | Moderate
Checkers Silverlakes No Gen | 2025-05-01 | 15171 | 14130 | 107.4% | Expected
Checkers Silverlakes No Gen | 2025-06-01 | 9655.7 | 12619.8 | 76.51% | Moderate
Checkers Silverlakes No Gen | 2025-07-01 | 10531.6 | 14002.2 | 75.21% | Moderate
Checkers Silverlakes No Gen | 2025-08-01 | 14730 | 16641.9 | 88.51% | Moderate
Checkers Silverlakes No Gen | 2025-09-01 | 12165 | 18626.4 | 65.31% | Poor
Checkers Silverlakes No Gen | 2025-10-01 | 20277 | 20503.8 | 98.89% | Expected
Checkers Silverlakes No Gen | 2025-11-01 | 15371 | 20601 | 74.61% | Moderate
Checkers Silverlakes No Gen | 2025-12-01 | 13568 | 22024.8 | 61.6% | Poor
Checkers Silverlakes No Gen | 2026-01-01 | 21287 | 21105 | 100.9% | Expected
Checkers Silverlakes No Gen | 2026-02-01 | 19200 | 18220.5 | 105.4% | Expected
Checkers Silverlakes No Gen | 2026-03-01 | 16030 | 18368.1 | 87.27% | Moderate
Checkers Silverlakes No Gen | 2026-04-01 | 13700 | 15103.8 | 90.71% | Expected
Checkers Silverlakes No Gen | 2026-05-01 | 13287 | 14130 | 94.03% | Expected
Checkers Silverlakes No Gen | 2026-06-01 | 10602.24 | 12619.8 | 84.01% | Moderate
Checkers Lichtenburg | 2026-07-01 | 16617.1608 | 18234.6788 | 91.13% | Expected | YES
Checkers Silverlakes No Gen | 2026-08-01 | 18200 | 16641.9 | 109.4% | Expected | NO
TPF Foods | 2026-09-01 | 2619.92 | 3588.8101 | 73% | Moderate | NO
Checkers Silverlakes No Gen | 2026-10-01 |  | 20503.8
Checkers Silverlakes No Gen | 2026-11-01 |  | 20601
Checkers Silverlakes No Gen | 2026-12-01 |  | 22024.8
Checkrite Inanda | 2024-01-01 |  | 8664.3
Checkrite Inanda | 2024-02-01 |  | 8100
Checkrite Inanda | 2024-03-01 |  | 7805.7
Checkrite Inanda | 2024-04-01 |  | 6534
Checkrite Inanda | 2024-05-01 |  | 5592.6
Checkrite Inanda | 2024-06-01 |  | 5059.8
Checkrite Inanda | 2024-07-01 |  | 5371.7901
Checkrite Inanda | 2024-08-01 |  | 6481.1606
Checkrite Inanda | 2024-09-01 |  | 6906.0613
Checkrite Inanda | 2024-10-01 |  | 8018.7358
Checkrite Inanda | 2024-11-01 |  | 7993.3065
Checkrite Inanda | 2024-12-01 |  | 8521.6944
Checkrite Inanda | 2025-01-01 | 8900 | 8633.1953 | 103.1% | Expected
Checkrite Inanda | 2025-02-01 | 5390 | 8066.1106 | 66.82% | Poor
Checkrite Inanda | 2025-03-01 | 5378 | 7768.8572 | 69.23% | Poor
Checkrite Inanda | 2025-04-01 | 3410 | 6499.2836 | 52.47% | Poor
Checkrite Inanda | 2025-05-01 | 3628 | 5559.6767 | 65.26% | Poor
Checkrite Inanda | 2025-06-01 | 5836 | 5027.0153 | 116.1% | Expected
Checkrite Inanda | 2025-07-01 | 6830 | 5334.2132 | 128% | Expected
Checkrite Inanda | 2025-08-01 | 7659 | 6435.8234 | 119% | Expected
Checkrite Inanda | 2025-09-01 | 5799 | 6857.7519 | 84.56% | Moderate
Checkrite Inanda | 2025-10-01 | 6484.6 | 7962.6429 | 81.44% | Moderate
Checkrite Inanda | 2025-11-01 | 7636 | 7937.3915 | 96.2% | Expected
Checkrite Inanda | 2025-12-01 | 7000 | 8462.0833 | 82.72% | Moderate
Checkrite Inanda | 2026-01-01 | 6305 | 8572.8041 | 73.55% | Moderate
Checkrite Inanda | 2026-02-01 | 4373.4359 | 8009.6864 | 54.6% | Poor
Checkrite Inanda | 2026-03-01 | 4958 | 7714.5123 | 64.27% | Poor
Checkrite Inanda | 2026-04-01 | 6980.52 | 6453.8196 | 108.2% | Expected
Checkrite Inanda | 2026-05-01 | 6633.98 | 5520.7855 | 120.2% | Expected
Checkrite Inanda | 2026-06-01 | 5387.22 | 4991.8502 | 107.9% | Expected
Checkers Silverlakes Gen | 2026-07-01 | 16600 | 14002.2 | 118.6% | Expected | NO
Checkrite Inanda | 2026-08-01 | 6595.107 | 6390.8034 | 103.2% | Expected | NO
U Save Botrivier | 2026-09-01 | 3820.9749 | 5210.7544 | 73.33% | Moderate | NO
Checkrite Inanda | 2026-10-01 |  | 7906.9424
Checkrite Inanda | 2026-11-01 |  | 7881.8677
Checkrite Inanda | 2026-12-01 |  | 8402.8891
Club Houghton | 2024-01-01 | 3578 | 5698.0728 | 62.79% | Poor
Club Houghton | 2024-02-01 | 3594 | 4767.7809 | 75.38% | Moderate
Club Houghton | 2024-03-01 | 3674 | 4848.612 | 75.77% | Moderate
Club Houghton | 2024-04-01 | 3533 | 4092.9886 | 86.32% | Moderate
Club Houghton | 2024-05-01 | 3191 | 3881.2614 | 82.22% | Moderate
Club Houghton | 2024-06-01 | 2884 | 3411.7011 | 84.53% | Moderate
Club Houghton | 2024-07-01 | 3894 | 3814.6833 | 102.1% | Expected
Club Houghton | 2024-08-01 | 4058 | 4487.2195 | 90.43% | Expected
Club Houghton | 2024-09-01 | 3726 | 4950.0809 | 75.27% | Moderate
Club Houghton | 2024-10-01 | 4063 | 5516.8687 | 73.65% | Moderate
Club Houghton | 2024-11-01 | 3998 | 5610.8218 | 71.26% | Moderate
Club Houghton | 2024-12-01 | 3593 | 5916.8111 | 60.73% | Poor
Club Houghton | 2025-01-01 | 3726 | 5658.1047 | 65.85% | Poor
Club Houghton | 2025-02-01 | 3060 | 4734.3381 | 64.63% | Poor
Club Houghton | 2025-03-01 | 3350 | 4814.6949 | 69.58% | Poor
Club Houghton | 2025-04-01 | 2383 | 4064.3572 | 58.63% | Poor
Club Houghton | 2025-05-01 | 3026 | 3854.1111 | 78.51% | Moderate
Club Houghton | 2025-06-01 | 2637.9 | 3387.8355 | 77.86% | Moderate
Club Houghton | 2025-07-01 | 2506 | 3787.9988 | 66.16% | Poor
Club Houghton | 2025-08-01 | 2144 | 4455.8304 | 48.12% | Poor
Club Houghton | 2025-09-01 | 2520 | 4915.454 | 51.27% | Poor
Club Houghton | 2025-10-01 | 2989 | 5478.277 | 54.56% | Poor
Club Houghton | 2025-11-01 | 2384 | 5571.5728 | 42.79% | Poor
Club Houghton | 2025-12-01 | 2166 | 5875.4216 | 36.87% | Poor
Club Houghton | 2026-01-01 | 2756 | 5618.525 | 49.05% | Poor
Club Houghton | 2026-02-01 | 1526 | 4701.2204 | 32.46% | Poor
Club Houghton | 2026-03-01 | 1909 | 4781.015 | 39.93% | Poor
Club Houghton | 2026-04-01 | 2190.9 | 4035.9261 | 54.28% | Poor
Club Houghton | 2026-05-01 | 2313.3 | 3827.1507 | 60.44% | Poor
Club Houghton | 2026-06-01 | 1184 | 3364.1368 | 35.19% | Poor
Checkers Silverlakes No Gen | 2026-07-01 | 14345 | 14002.2 | 102.4% | Expected | NO
Club Houghton | 2026-08-01 | 4021 | 4424.6608 | 90.88% | Expected | NO
Kool Village | 2026-09-01 | 7912.61 | 10701.9 | 73.94% | Moderate | NO
Club Houghton | 2026-10-01 |  | 5439.9552
Club Houghton | 2026-11-01 |  | 5532.5984
Club Houghton | 2026-12-01 |  | 5834.3217
Coldstar International | 2024-01-01 | 5665 | 4836.2763 | 117.1% | Expected
Coldstar International | 2024-02-01 | 3554 | 4437.826 | 80.08% | Moderate
Coldstar International | 2024-03-01 | 1 | 4487.0024 | 0.02229% | Poor
Coldstar International | 2024-04-01 | 1 | 3751.4232 | 0.02666% | Poor
Coldstar International | 2024-05-01 | 1 | 3470.7889 | 0.02881% | Poor
Coldstar International | 2024-06-01 | 3309 | 3139.191 | 105.4% | Expected
Coldstar International | 2024-07-01 | 2293 | 3361.9868 | 68.2% | Poor
Coldstar International | 2024-08-01 | 1967 | 3793.6289 | 51.85% | Poor
Coldstar International | 2024-09-01 | 3009 | 3740.902 | 80.44% | Moderate
Coldstar International | 2024-10-01 | 4500 | 4164.1159 | 108.1% | Expected
Coldstar International | 2024-11-01 | 3918 | 4256.5219 | 92.05% | Expected
Coldstar International | 2024-12-01 | 2583 | 4963.1891 | 52.04% | Poor
Coldstar International | 2025-01-01 | 3426 | 4802.3531 | 71.34% | Moderate
Coldstar International | 2025-02-01 | 3380.46 | 4406.6976 | 76.71% | Moderate
Coldstar International | 2025-03-01 | 3717 | 4455.6148 | 83.42% | Moderate
Coldstar International | 2025-04-01 | 2027 | 3725.1812 | 54.41% | Poor
Coldstar International | 2025-05-01 | 3199 | 3446.51 | 92.82% | Expected
Coldstar International | 2025-06-01 | 2899.41 | 3117.2317 | 93.01% | Expected
Coldstar International | 2025-07-01 | 3705 | 3338.4689 | 111% | Expected
Coldstar International | 2025-08-01 | 4242 | 3767.0916 | 112.6% | Expected
Coldstar International | 2025-09-01 | 3928 | 3714.7336 | 105.7% | Expected
Coldstar International | 2025-10-01 | 4810 | 4134.987 | 116.3% | Expected
Coldstar International | 2025-11-01 | 5556 | 4226.7466 | 131.4% | Expected
Coldstar International | 2025-12-01 | 5696 | 4928.4705 | 115.6% | Expected
Coldstar International | 2026-01-01 | 5960 | 4768.7595 | 125% | Expected
Coldstar International | 2026-02-01 | 5548 | 4375.8718 | 126.8% | Expected
Coldstar International | 2026-03-01 | 5036 | 4424.4468 | 113.8% | Expected
Coldstar International | 2026-04-01 | 4183.27 | 3699.1227 | 113.1% | Expected
Coldstar International | 2026-05-01 | 4320 | 3422.4009 | 126.2% | Expected
Coldstar International | 2026-06-01 | 3510 | 3095.4259 | 113.4% | Expected
Checkrite Inanda | 2026-07-01 | 5573.8 | 5296.8991 | 105.2% | Expected | NO
Coldstar International | 2026-08-01 | 4690 | 3740.74 | 125.4% | Expected | NO
Coldstar International | 2026-09-01 | 3950.63 | 3688.7482 | 107.1% | Expected | NO
Coldstar International | 2026-10-01 |  | 4106.0618
Coldstar International | 2026-11-01 |  | 4197.1796
Coldstar International | 2026-12-01 |  | 4893.9947
Cultura Fresh | 2024-01-01 |  | 11798.1
Cultura Fresh | 2024-02-01 |  | 10269.9
Cultura Fresh | 2024-03-01 |  | 10571.4
Cultura Fresh | 2024-04-01 |  | 8335.8
Cultura Fresh | 2024-05-01 |  | 6723.9
Cultura Fresh | 2024-06-01 |  | 5859.9
Cultura Fresh | 2024-07-01 |  | 6453
Cultura Fresh | 2024-08-01 |  | 7491.6
Cultura Fresh | 2024-09-01 |  | 8859.4983
Cultura Fresh | 2024-10-01 |  | 10350.3473
Cultura Fresh | 2024-11-01 |  | 10954.2448
Cultura Fresh | 2024-12-01 |  | 11604.335
Cultura Fresh | 2025-01-01 |  | 11764.3395
Cultura Fresh | 2025-02-01 |  | 10234.4089
Cultura Fresh | 2025-03-01 |  | 10529.1954
Cultura Fresh | 2025-04-01 |  | 8297.5722
Cultura Fresh | 2025-05-01 |  | 6689.2037
Cultura Fresh | 2025-06-01 |  | 5826.1875
Cultura Fresh | 2025-07-01 |  | 6412.1746
Cultura Fresh | 2025-08-01 |  | 7439.7669
Cultura Fresh | 2025-09-01 | 8715 | 8797.5241 | 99.06% | Expected
Cultura Fresh | 2025-10-01 | 11487.6 | 10277.9443 | 111.8% | Expected
Cultura Fresh | 2025-11-01 | 11643 | 10877.6174 | 107% | Expected
Cultura Fresh | 2025-12-01 | 11559 | 11523.1601 | 100.3% | Expected
Cultura Fresh | 2026-01-01 | 12880 | 11682.0453 | 110.3% | Expected
Cultura Fresh | 2026-02-01 | 9660 | 10162.8169 | 95.05% | Expected
Cultura Fresh | 2026-03-01 | 9967 | 10455.5413 | 95.33% | Expected
Cultura Fresh | 2026-04-01 | 4183 | 8239.5288 | 50.77% | Poor
Cultura Fresh | 2026-05-01 |  | 6642.4112
Cultura Fresh | 2026-06-01 |  | 5785.432
Club Houghton | 2026-07-01 | 3646 | 3761.5008 | 96.93% | Expected | NO
Cultura Fresh | 2026-08-01 |  | 7387.724 |  |  | YES
Cultura Fresh | 2026-09-01 |  | 8735.9834 |  |  | NO
Cultura Fresh | 2026-10-01 |  | 10206.0477
Cultura Fresh | 2026-11-01 |  | 10801.526
Cultura Fresh | 2026-12-01 |  | 11442.553
Demco | 2024-01-01 |  | 33516
Demco | 2024-02-01 |  | 28776.8
Demco | 2024-03-01 |  | 29186.4
Demco | 2024-04-01 |  | 24678.4
Demco | 2024-05-01 |  | 23380.8
Demco | 2024-06-01 |  | 20986.4
Demco | 2024-07-01 |  | 23248.9393
Demco | 2024-08-01 |  | 27282.7777
Demco | 2024-09-01 |  | 30267.7266
Demco | 2024-10-01 |  | 32956.7449
Demco | 2024-11-01 |  | 33127.0008
Demco | 2024-12-01 |  | 34953.9543
Demco | 2025-01-01 | 17200 | 33388.6136 | 51.51% | Poor
Demco | 2025-02-01 | 15760 | 28650.3397 | 55.01% | Poor
Demco | 2025-03-01 | 15700 | 29042.4959 | 54.06% | Poor
Demco | 2025-04-01 | 10223 | 24542.0863 | 41.65% | Poor
Demco | 2025-05-01 | 14225 | 23238.2421 | 61.21% | Poor
Demco | 2025-06-01 | 14376.5 | 20846.0091 | 68.97% | Poor
Demco | 2025-07-01 | 15177.99 | 23086.3077 | 65.74% | Poor
Demco | 2025-08-01 | 16924 | 27091.9286 | 62.47% | Poor
Demco | 2025-09-01 | 16705 | 30055.997 | 55.58% | Poor
Demco | 2025-10-01 | 21308.4 | 32726.205 | 65.11% | Poor
Demco | 2025-11-01 | 12744 | 32895.27 | 38.74% | Poor
Demco | 2025-12-01 | 7631 | 34709.4435 | 21.99% | Poor
Demco | 2026-01-01 | 7744.97 | 33155.0527 | 23.36% | Poor
Demco | 2026-02-01 | 13221 | 28449.9241 | 46.47% | Poor
Demco | 2026-03-01 | 14695 | 28839.3371 | 50.95% | Poor
Demco | 2026-04-01 | 14798.11 | 24370.4088 | 60.72% | Poor
Demco | 2026-05-01 | 13154.32 | 23075.6853 | 57.01% | Poor
Demco | 2026-06-01 | 11956.63 | 20700.1866 | 57.76% | Poor
Coldstar International | 2026-07-01 | 3547 | 3315.1156 | 107% | Expected | NO
Demco | 2026-08-01 | 14955 | 26902.4144 | 55.59% | Poor | NO
Demco | 2026-09-01 | 18244.51 | 29845.7485 | 61.13% | Poor | NO
Demco | 2026-10-01 |  | 32497.2778
Demco | 2026-11-01 |  | 32665.1602
Demco | 2026-12-01 |  | 34466.6432
Engen Lotus Gardens | 2024-01-01 |  | 2461.5
Engen Lotus Gardens | 2024-02-01 |  | 2300.4
Engen Lotus Gardens | 2024-03-01 |  | 2281.5
Engen Lotus Gardens | 2024-04-01 |  | 2197.8
Engen Lotus Gardens | 2024-05-01 |  | 2226.6
Engen Lotus Gardens | 2024-06-01 |  | 2480.4
Engen Lotus Gardens | 2024-07-01 |  | 2349.9
Engen Lotus Gardens | 2024-08-01 |  | 2520
Engen Lotus Gardens | 2024-09-01 |  | 2436.3
Engen Lotus Gardens | 2024-10-01 |  | 2425.5
Engen Lotus Gardens | 2024-11-01 |  | 2356.2
Engen Lotus Gardens | 2024-12-01 |  | 2437.2
Engen Lotus Gardens | 2025-01-01 |  | 2461.5
Engen Lotus Gardens | 2025-02-01 |  | 2300.4
Engen Lotus Gardens | 2025-03-01 |  | 2281.5
Engen Lotus Gardens | 2025-04-01 |  | 2197.8
Engen Lotus Gardens | 2025-05-01 |  | 2226.6
Engen Lotus Gardens | 2025-06-01 |  | 2480.4
Engen Lotus Gardens | 2025-07-01 |  | 2349.9
Engen Lotus Gardens | 2025-08-01 |  | 2520
Engen Lotus Gardens | 2025-09-01 |  | 2436.3
Engen Lotus Gardens | 2025-10-01 |  | 2425.5
Engen Lotus Gardens | 2025-11-01 |  | 2355.7016
Engen Lotus Gardens | 2025-12-01 |  | 2435.279
Engen Lotus Gardens | 2026-01-01 | 3245 | 2458.0938 | 132% | Expected
Engen Lotus Gardens | 2026-02-01 | 3122 | 2295.8476 | 136% | Expected
Engen Lotus Gardens | 2026-03-01 | 2817 | 2275.7591 | 123.8% | Expected
Engen Lotus Gardens | 2026-04-01 | 2735.53 | 2190.9631 | 124.9% | Expected
Engen Lotus Gardens | 2026-05-01 | 3239.91 | 2218.3932 | 146% | Expected
Engen Lotus Gardens | 2026-06-01 | 2723 | 2469.7848 | 110.3% | Expected
Cultura Fresh | 2026-07-01 | 0 | 6367.32 | 0% | Poor | YES
Engen Lotus Gardens | 2026-08-01 | 3368.28 | 2506.2733 | 134.4% | Expected | NO
Engen Lotus Gardens | 2026-09-01 | 2640.395 | 2421.5851 | 109% | Expected | NO
Engen Lotus Gardens | 2026-10-01 |  | 2409.4597
Engen Lotus Gardens | 2026-11-01 |  | 2339.2229
Engen Lotus Gardens | 2026-12-01 |  | 2418.2436
Giba Gorge Main | 2024-01-01 | 9736 | 13373.2539 | 72.8% | Moderate
Giba Gorge Main | 2024-02-01 | 8912 | 12244.8977 | 72.78% | Moderate
Giba Gorge Main | 2024-03-01 | 9597 | 12529.9285 | 76.59% | Moderate
Giba Gorge Main | 2024-04-01 | 7950 | 10753.2489 | 73.93% | Moderate
Giba Gorge Main | 2024-05-01 | 7482 | 9705.3671 | 77.09% | Moderate
Giba Gorge Main | 2024-06-01 | 6656 | 9065.0685 | 73.42% | Moderate
Giba Gorge Main | 2024-07-01 | 11170 | 9571.1608 | 116.7% | Expected
Giba Gorge Main | 2024-08-01 | 11290 | 10610.9414 | 106.4% | Expected
Giba Gorge Main | 2024-09-01 | 8578 | 10696.0199 | 80.2% | Moderate
Giba Gorge Main | 2024-10-01 | 12704 | 11882.1033 | 106.9% | Expected
Giba Gorge Main | 2024-11-01 | 5700 | 12063.7883 | 47.25% | Poor
Giba Gorge Main | 2024-12-01 |  | 13179.6712
Giba Gorge Main | 2025-01-01 |  | 13279.4495
Giba Gorge Main | 2025-02-01 |  | 12159.008
Giba Gorge Main | 2025-03-01 | 6684 | 12442.2788 | 53.72% | Poor
Giba Gorge Main | 2025-04-01 | 3992 | 10678.0275 | 37.39% | Poor
Giba Gorge Main | 2025-05-01 | 6009 | 9637.4759 | 62.35% | Poor
Giba Gorge Main | 2025-06-01 | 5530.9 | 9001.6563 | 61.44% | Poor
Giba Gorge Main | 2025-07-01 | 6694 | 9504.2084 | 70.43% | Moderate
Giba Gorge Main | 2025-08-01 | 7750 | 10536.7154 | 73.55% | Moderate
Giba Gorge Main | 2025-09-01 | 7031 | 10621.1988 | 66.2% | Poor
Giba Gorge Main | 2025-10-01 | 9805 | 11798.9853 | 83.1% | Moderate
Giba Gorge Main | 2025-11-01 | 9365 | 11979.3994 | 78.18% | Moderate
Giba Gorge Main | 2025-12-01 | 5379 | 13087.4765 | 41.1% | Poor
Giba Gorge Main | 2026-01-01 | 4979.16 | 13186.5568 | 37.76% | Poor
Giba Gorge Main | 2026-02-01 | 2172.67 | 12073.953 | 17.99% | Poor
Giba Gorge Main | 2026-03-01 | 350 | 12355.2423 | 2.833% | Poor
Giba Gorge Main | 2026-04-01 | 194.99 | 10603.3323 | 1.839% | Poor
Giba Gorge Main | 2026-05-01 |  | 9570.0596
Giba Gorge Main | 2026-06-01 | 3521 | 8938.6877 | 39.39% | Poor
Demco | 2026-07-01 | 12633 | 22924.8138 | 55.11% | Poor | NO
Giba Gorge Main | 2026-08-01 | 4981 | 10463.0087 | 47.61% | Poor | NO
Giba Gorge Main | 2026-09-01 | 5324.68 | 10546.9011 | 50.49% | Poor | NO
Giba Gorge Main | 2026-10-01 |  | 11716.4487
Giba Gorge Main | 2026-11-01 |  | 11895.6008
Giba Gorge Main | 2026-12-01 |  | 12995.9266
Giba Gorge Storage | 2024-01-01 | 4830 | 11208.0006 | 43.09% | Poor
Giba Gorge Storage | 2024-02-01 | 7231 | 9980.2772 | 72.45% | Moderate
Giba Gorge Storage | 2024-03-01 | 5436 | 10223.3279 | 53.17% | Poor
Giba Gorge Storage | 2024-04-01 | 5158 | 8689.8715 | 59.36% | Poor
Giba Gorge Storage | 2024-05-01 | 3827 | 7821.9497 | 48.93% | Poor
Giba Gorge Storage | 2024-06-01 | 3220 | 7228.9094 | 44.54% | Poor
Giba Gorge Storage | 2024-07-01 | 5497 | 7716.0965 | 71.24% | Moderate
Giba Gorge Storage | 2024-08-01 | 4475 | 8587.5885 | 52.11% | Poor
Giba Gorge Storage | 2024-09-01 | 1847 | 8776.1182 | 21.05% | Poor
Giba Gorge Storage | 2024-10-01 | 1575 | 9751.7385 | 16.15% | Poor
Giba Gorge Storage | 2024-11-01 | 5700 | 9796.7354 | 58.18% | Poor
Giba Gorge Storage | 2024-12-01 | 1938 | 10878.6429 | 17.81% | Poor
Giba Gorge Storage | 2025-01-01 | 5227 | 11129.3841 | 46.97% | Poor
Giba Gorge Storage | 2025-02-01 | 5137 | 9910.2723 | 51.84% | Poor
Giba Gorge Storage | 2025-03-01 | 5031 | 10151.8134 | 49.56% | Poor
Giba Gorge Storage | 2025-04-01 | 3147 | 8629.0839 | 36.47% | Poor
Giba Gorge Storage | 2025-05-01 | 4797 | 7767.2334 | 61.76% | Poor
Giba Gorge Storage | 2025-06-01 | 3255.49 | 7178.3415 | 45.35% | Poor
Giba Gorge Storage | 2025-07-01 | 5212 | 7662.1207 | 68.02% | Poor
Giba Gorge Storage | 2025-08-01 | 1743.88 | 8527.5163 | 20.45% | Poor
Giba Gorge Storage | 2025-09-01 | 4503 | 8714.7272 | 51.67% | Poor
Giba Gorge Storage | 2025-10-01 | 6159 | 9683.5229 | 63.6% | Poor
Giba Gorge Storage | 2025-11-01 | 6232 | 9728.205 | 64.06% | Poor
Giba Gorge Storage | 2025-12-01 | 5380 | 10802.5443 | 49.8% | Poor
Giba Gorge Storage | 2026-01-01 | 7601.5 | 11051.5315 | 68.78% | Poor
Giba Gorge Storage | 2026-02-01 | 6347.07 | 9840.9477 | 64.5% | Poor
Giba Gorge Storage | 2026-03-01 | 7063 | 10080.7992 | 70.06% | Moderate
Giba Gorge Storage | 2026-04-01 | 4736.87 | 8568.7215 | 55.28% | Poor
Giba Gorge Storage | 2026-05-01 | 4375.54 | 7712.8998 | 56.73% | Poor
Giba Gorge Storage | 2026-06-01 | 3483 | 7128.1274 | 48.86% | Poor
Engen Kaalfontein | 2026-07-01 | 6140 | 10977.4293 | 55.93% | Poor | YES
Giba Gorge Storage | 2026-08-01 | 5110 | 8467.8644 | 60.35% | Poor | NO
Giba Gorge Storage | 2026-09-01 | 5755.15 | 8653.7657 | 66.5% | Poor | NO
Giba Gorge Storage | 2026-10-01 |  | 9615.7845
Giba Gorge Storage | 2026-11-01 |  | 9660.154
Giba Gorge Storage | 2026-12-01 |  | 10726.9781
Golden Spot Resort | 2024-01-01 | 961 | 4025.808 | 23.87% | Poor
Golden Spot Resort | 2024-02-01 | 798 | 3632.8907 | 21.97% | Poor
Golden Spot Resort | 2024-03-01 | 398 | 3936.1227 | 10.11% | Poor
Golden Spot Resort | 2024-04-01 | 1334 | 3260.1051 | 40.92% | Poor
Golden Spot Resort | 2024-05-01 | 1953 | 3030.2205 | 64.45% | Poor
Golden Spot Resort | 2024-06-01 | 1657 | 2770.1636 | 59.82% | Poor
Golden Spot Resort | 2024-07-01 | 1845 | 3021.3091 | 61.07% | Poor
Golden Spot Resort | 2024-08-01 | 2034 | 3271.2084 | 62.18% | Poor
Golden Spot Resort | 2024-09-01 | 1982 | 3461.9353 | 57.25% | Poor
Golden Spot Resort | 2024-10-01 | 2181 | 3475.9855 | 62.74% | Poor
Golden Spot Resort | 2024-11-01 | 1783 | 3314.4291 | 53.8% | Poor
Golden Spot Resort | 2024-12-01 | 2366 | 3553.8325 | 66.58% | Poor
Golden Spot Resort | 2025-01-01 | 2514 | 3997.5697 | 62.89% | Poor
Golden Spot Resort | 2025-02-01 | 2930 | 3607.4084 | 81.22% | Moderate
Golden Spot Resort | 2025-03-01 | 1758 | 3908.5886 | 44.98% | Poor
Golden Spot Resort | 2025-04-01 | 1646 | 3237.2999 | 50.84% | Poor
Golden Spot Resort | 2025-05-01 | 2386 | 3009.0234 | 79.29% | Moderate
Golden Spot Resort | 2025-06-01 | 1228 | 2750.7857 | 44.64% | Poor
Golden Spot Resort | 2025-07-01 | 1684 | 3000.1743 | 56.13% | Poor
Golden Spot Resort | 2025-08-01 | 1766.1 | 3248.3255 | 54.37% | Poor
Golden Spot Resort | 2025-09-01 | 1960 | 3437.7183 | 57.01% | Poor
Golden Spot Resort | 2025-10-01 | 2119 | 3451.6702 | 61.39% | Poor
Golden Spot Resort | 2025-11-01 | 1774 | 3291.244 | 53.9% | Poor
Golden Spot Resort | 2025-12-01 | 2120 | 3528.9726 | 60.07% | Poor
Golden Spot Resort | 2026-01-01 | 647 | 3969.6058 | 16.3% | Poor
Golden Spot Resort | 2026-02-01 | 1429 | 3582.1738 | 39.89% | Poor
Golden Spot Resort | 2026-03-01 | 1816 | 3881.2472 | 46.79% | Poor
Golden Spot Resort | 2026-04-01 | 3513.5 | 3214.6543 | 109.3% | Expected
Golden Spot Resort | 2026-05-01 | 3029 | 2987.9746 | 101.4% | Expected
Golden Spot Resort | 2026-06-01 | 2484 | 2731.5434 | 90.94% | Expected
Engen Lotus Gardens | 2026-07-01 | 3388.4248 | 2338.4937 | 144.9% | Expected | NO
Golden Spot Resort | 2026-08-01 | 1628 | 3225.6027 | 50.47% | Poor | NO
Golden Spot Resort | 2026-09-01 | 747.8 | 3413.6706 | 21.91% | Poor | YES
Golden Spot Resort | 2026-10-01 |  | 3427.525
Golden Spot Resort | 2026-11-01 |  | 3268.221
Golden Spot Resort | 2026-12-01 |  | 3504.2866
Golden Spot Shops | 2024-01-01 | 1880 | 3602.7242 | 52.18% | Poor
Golden Spot Shops | 2024-02-01 | 1559 | 3238.7278 | 48.14% | Poor
Golden Spot Shops | 2024-03-01 | 1596 | 3588.7224 | 44.47% | Poor
Golden Spot Shops | 2024-04-01 | 2170 | 2945.1316 | 73.68% | Moderate
Golden Spot Shops | 2024-05-01 | 2876 | 2705.5978 | 106.3% | Expected
Golden Spot Shops | 2024-06-01 | 2499 | 2443.9522 | 102.3% | Expected
Golden Spot Shops | 2024-07-01 | 2895 | 2680.9918 | 108% | Expected
Golden Spot Shops | 2024-08-01 | 3177 | 2948.9399 | 107.7% | Expected
Golden Spot Shops | 2024-09-01 | 3048 | 3119.339 | 97.71% | Expected
Golden Spot Shops | 2024-10-01 | 3449 | 3149.6334 | 109.5% | Expected
Golden Spot Shops | 2024-11-01 | 3441 | 2982.9289 | 115.4% | Expected
Golden Spot Shops | 2024-12-01 | 3537 | 3169.9825 | 111.6% | Expected
Golden Spot Shops | 2025-01-01 | 3700 | 3577.4535 | 103.4% | Expected
Golden Spot Shops | 2025-02-01 | 2900 | 3216.0103 | 90.17% | Expected
Golden Spot Shops | 2025-03-01 | 3471 | 3563.6185 | 97.4% | Expected
Golden Spot Shops | 2025-04-01 | 2668 | 2924.5298 | 91.23% | Expected
Golden Spot Shops | 2025-05-01 | 3127 | 2686.6715 | 116.4% | Expected
Golden Spot Shops | 2025-06-01 | 2748.4 | 2426.8562 | 113.2% | Expected
Golden Spot Shops | 2025-07-01 | 2501 | 2662.2377 | 93.94% | Expected
Golden Spot Shops | 2025-08-01 | 299.8 | 2928.3114 | 10.24% | Poor
Golden Spot Shops | 2025-09-01 | 2705 | 3097.5186 | 87.33% | Moderate
Golden Spot Shops | 2025-10-01 | 2939 | 3127.601 | 93.97% | Expected
Golden Spot Shops | 2025-11-01 | 2609 | 2962.0626 | 88.08% | Moderate
Golden Spot Shops | 2025-12-01 | 3364 | 3147.8078 | 106.9% | Expected
Golden Spot Shops | 2026-01-01 | 3086 | 3552.4284 | 86.87% | Moderate
Golden Spot Shops | 2026-02-01 | 3628 | 3193.5136 | 113.6% | Expected
Golden Spot Shops | 2026-03-01 | 2909 | 3538.6902 | 82.21% | Moderate
Golden Spot Shops | 2026-04-01 | 2558.1 | 2904.072 | 88.09% | Moderate
Golden Spot Shops | 2026-05-01 | 3029.6 | 2667.8776 | 113.6% | Expected
Golden Spot Shops | 2026-06-01 | 2477 | 2409.8798 | 102.8% | Expected
Giba Gorge Main | 2026-07-01 | 5136 | 9437.7243 | 54.42% | Poor | NO
Golden Spot Shops | 2026-08-01 |  | 2907.8272 |  |  | NO
Golden Spot Shops | 2026-09-01 | 0 | 3075.8507 | 0% | Poor | NO
Golden Spot Shops | 2026-10-01 |  | 3105.7228
Golden Spot Shops | 2026-11-01 |  | 2941.3423
Golden Spot Shops | 2026-12-01 |  | 3125.7882
Grootpan | 2024-01-01 |  | 29074.5
Grootpan | 2024-02-01 |  | 26716.5
Grootpan | 2024-03-01 |  | 27941.4
Grootpan | 2024-04-01 |  | 25610.4
Grootpan | 2024-05-01 |  | 25802.1
Grootpan | 2024-06-01 |  | 23428.8
Grootpan | 2024-07-01 |  | 25632
Grootpan | 2024-08-01 |  | 28549.8
Grootpan | 2024-09-01 |  | 29561.4
Grootpan | 2024-10-01 |  | 31417.2
Grootpan | 2024-11-01 |  | 30121.2
Grootpan | 2024-12-01 |  | 29445.3
Grootpan | 2025-01-01 |  | 29074.5
Grootpan | 2025-02-01 |  | 26716.5
Grootpan | 2025-03-01 |  | 27941.4
Grootpan | 2025-04-01 |  | 25610.4
Grootpan | 2025-05-01 |  | 25802.1
Grootpan | 2025-06-01 |  | 23428.8
Grootpan | 2025-07-01 |  | 25632
Grootpan | 2025-08-01 |  | 28549.8
Grootpan | 2025-09-01 |  | 29561.4
Grootpan | 2025-10-01 |  | 31417.2
Grootpan | 2025-11-01 |  | 30121.2
Grootpan | 2025-12-01 |  | 29445.3
Grootpan | 2026-01-01 |  | 29074.5
Grootpan | 2026-02-01 |  | 26716.5
Grootpan | 2026-03-01 | 2780 | 27941.4 | 9.949% | Poor
Grootpan | 2026-04-01 | 14950 | 51194.2093 | 29.2% | Poor
Grootpan | 2026-05-01 | 6540 | 25773.8301 | 25.37% | Poor
Grootpan | 2026-06-01 | 7560 | 23389.1815 | 32.32% | Poor
Giba Gorge Storage | 2026-07-01 | 4112 | 7608.5224 | 54.04% | Poor | NO
Golden Spot Resort | 2026-07-01 | 857 | 2979.1874 | 28.77% | Poor | YES
Grootpan | 2026-08-01 | 18070 | 28468.1042 | 63.47% | Poor | NO
Grootpan | 2026-09-01 | 9230 | 29459.2406 | 31.33% | Poor | YES
Grootpan | 2026-10-01 |  | 31290.5683
Grootpan | 2026-11-01 |  | 29981.9114
Grootpan | 2026-12-01 |  | 29292.2313
HB Dunn | 2024-01-01 |  | 4235.4
HB Dunn | 2024-02-01 |  | 3699
HB Dunn | 2024-03-01 |  | 3788.1
HB Dunn | 2024-04-01 |  | 3184.2
HB Dunn | 2024-05-01 |  | 3052.4477
HB Dunn | 2024-06-01 | 1659 | 2750.2422 | 60.32% | Poor
HB Dunn | 2024-07-01 | 2542 | 3025.4989 | 84.02% | Moderate
HB Dunn | 2024-08-01 | 2833 | 3540.2212 | 80.02% | Moderate
HB Dunn | 2024-09-01 | 2688 | 3901.708 | 68.89% | Poor
HB Dunn | 2024-10-01 | 3664 | 4090.5721 | 89.57% | Moderate
HB Dunn | 2024-11-01 | 3499 | 4105.1717 | 85.23% | Moderate
HB Dunn | 2024-12-01 | 2842 | 4359.117 | 65.2% | Poor
HB Dunn | 2025-01-01 | 3075 | 4215.0036 | 72.95% | Moderate
HB Dunn | 2025-02-01 | 3328 | 3678.9927 | 90.46% | Expected
HB Dunn | 2025-03-01 | 2317 | 3765.5824 | 61.53% | Poor
HB Dunn | 2025-04-01 | 3007 | 3163.3856 | 95.06% | Expected
HB Dunn | 2025-05-01 | 3516 | 3031.0952 | 116% | Expected
HB Dunn | 2025-06-01 | 2912.8 | 2731.0037 | 106.7% | Expected
HB Dunn | 2025-07-01 | 2789 | 3004.3349 | 92.83% | Expected
HB Dunn | 2025-08-01 | 3342 | 3515.4566 | 95.07% | Expected
HB Dunn | 2025-09-01 | 3079 | 3874.4146 | 79.47% | Moderate
HB Dunn | 2025-10-01 | 3708 | 4061.9576 | 91.29% | Expected
HB Dunn | 2025-11-01 | 2852 | 4076.4551 | 69.96% | Poor
HB Dunn | 2025-12-01 | 2386 | 4328.624 | 55.12% | Poor
HB Dunn | 2026-01-01 | 1855 | 4185.5187 | 44.32% | Poor
HB Dunn | 2026-02-01 | 3786 | 3653.2573 | 103.6% | Expected
HB Dunn | 2026-03-01 | 2926 | 3739.2413 | 78.25% | Moderate
HB Dunn | 2026-04-01 | 1520 | 3141.257 | 48.39% | Poor
HB Dunn | 2026-05-01 | 2675.6 | 3009.892 | 88.89% | Moderate
HB Dunn | 2026-06-01 | 2896 | 2711.8997 | 106.8% | Expected
Golden Spot Shops | 2026-07-01 | 1400 | 2643.6147 | 52.96% | Poor | NO
HB Dunn | 2026-08-01 | 2805 | 3490.8651 | 80.35% | Moderate | NO
Plastiplate | 2026-09-01 | 6058.46 | 8097.5337 | 74.82% | Moderate | NO
HB Dunn | 2026-10-01 |  | 4033.5433
HB Dunn | 2026-11-01 |  | 4047.9393
HB Dunn | 2026-12-01 |  | 4298.3443
Helderberg Collage | 2024-01-01 | 32658 | 38406.6905 | 85.03% | Moderate
Helderberg Collage | 2024-02-01 | 26200 | 32048.7699 | 81.75% | Moderate
Helderberg Collage | 2024-03-01 | 23764 | 31211.9668 | 76.14% | Moderate
Helderberg Collage | 2024-04-01 | 17748 | 22862.2667 | 77.63% | Moderate
Helderberg Collage | 2024-05-01 | 12623 | 17370.7589 | 72.67% | Moderate
Helderberg Collage | 2024-06-01 | 9466 | 14433.2799 | 65.58% | Poor
Helderberg Collage | 2024-07-01 | 8265 | 16212.1565 | 50.98% | Poor
Helderberg Collage | 2024-08-01 | 14669 | 20174.1201 | 72.71% | Moderate
Helderberg Collage | 2024-09-01 | 20334 | 25763.957 | 78.92% | Moderate
Helderberg Collage | 2024-10-01 | 26318 | 31860.5288 | 82.6% | Moderate
Helderberg Collage | 2024-11-01 | 29589 | 35782.1944 | 82.69% | Moderate
Helderberg Collage | 2024-12-01 | 31807 | 38665.8215 | 82.26% | Moderate
Helderberg Collage | 2025-01-01 | 32545 | 38137.2935 | 85.34% | Moderate
Helderberg Collage | 2025-02-01 | 20706 | 31823.9695 | 65.06% | Poor
Helderberg Collage | 2025-03-01 | 16650 | 30993.6321 | 53.72% | Poor
Helderberg Collage | 2025-04-01 | 13216 | 22702.34 | 58.21% | Poor
Helderberg Collage | 2025-05-01 | 8710 | 17249.2465 | 50.49% | Poor
Helderberg Collage | 2025-06-01 | 7500.92 | 14332.3159 | 52.34% | Poor
Helderberg Collage | 2025-07-01 | 9649 | 16098.7488 | 59.94% | Poor
Helderberg Collage | 2025-08-01 | 13424 | 20032.9976 | 67.01% | Poor
Helderberg Collage | 2025-09-01 | 19447 | 25583.7323 | 76.01% | Moderate
Helderberg Collage | 2025-10-01 | 33678 | 31637.6572 | 106.4% | Expected
Helderberg Collage | 2025-11-01 | 40164 | 35531.8899 | 113% | Expected
Helderberg Collage | 2025-12-01 | 42482 | 38395.3453 | 110.6% | Expected
Helderberg Collage | 2026-01-01 | 40719 | 37870.5146 | 107.5% | Expected
Helderberg Collage | 2026-02-01 | 29862 | 31601.3536 | 94.5% | Expected
Helderberg Collage | 2026-03-01 | 30793 | 30776.8246 | 100.1% | Expected
Helderberg Collage | 2026-04-01 | 19657.41 | 22543.532 | 87.2% | Moderate
Helderberg Collage | 2026-05-01 | 14538.69 | 17128.5841 | 84.88% | Moderate
Helderberg Collage | 2026-06-01 | 14538.69 | 14232.0581 | 102.2% | Expected
Grootpan | 2026-07-01 | 8390 | 25573.8963 | 32.81% | Poor | YES
Helderberg Collage | 2026-08-01 | 20567 | 19892.8622 | 103.4% | Expected | NO
Helderberg Collage | 2026-09-01 | 24320.29 | 25404.7683 | 95.73% | Expected | NO
Helderberg Collage | 2026-10-01 |  | 31416.3447
Helderberg Collage | 2026-11-01 |  | 35283.3363
Helderberg Collage | 2026-12-01 |  | 38126.7612
Hilston Rotoflo | 2024-01-01 | 17880 | 29258.2001 | 61.11% | Poor
Hilston Rotoflo | 2024-02-01 | 18790 | 25545.4856 | 73.56% | Moderate
Hilston Rotoflo | 2024-03-01 | 22610 | 24067.2001 | 93.95% | Expected
Hilston Rotoflo | 2024-04-01 | 20030 | 21415.3947 | 93.53% | Expected
Hilston Rotoflo | 2024-05-01 | 17820 | 19169.3315 | 92.96% | Expected
Hilston Rotoflo | 2024-06-01 | 11000 | 16949.6461 | 64.9% | Poor
Hilston Rotoflo | 2024-07-01 | 17460 | 18858.4833 | 92.58% | Expected
Hilston Rotoflo | 2024-08-01 | 24290 | 21979.0817 | 110.5% | Expected
Hilston Rotoflo | 2024-09-01 | 22510 | 24435.1816 | 92.12% | Expected
Hilston Rotoflo | 2024-10-01 | 31780 | 27182.9641 | 116.9% | Expected
Hilston Rotoflo | 2024-11-01 | 30100 | 28526.8373 | 105.5% | Expected
Hilston Rotoflo | 2024-12-01 | 17966 | 28018.1186 | 64.12% | Poor
Hilston Rotoflo | 2025-01-01 | 20808 | 29052.9736 | 71.62% | Moderate
Hilston Rotoflo | 2025-02-01 | 21538 | 25366.3013 | 84.91% | Moderate
Hilston Rotoflo | 2025-03-01 | 22662 | 23898.8446 | 94.82% | Expected
Hilston Rotoflo | 2025-04-01 | 17413 | 21265.5892 | 81.88% | Moderate
Hilston Rotoflo | 2025-05-01 | 20430 | 19035.2377 | 107.3% | Expected
Hilston Rotoflo | 2025-06-01 | 18398.74 | 16831.0795 | 109.3% | Expected
Hilston Rotoflo | 2025-07-01 | 19115 | 18726.564 | 102.1% | Expected
Hilston Rotoflo | 2025-08-01 | 21942 | 21825.333 | 100.5% | Expected
Hilston Rotoflo | 2025-09-01 | 21707 | 24264.252 | 89.46% | Moderate
Hilston Rotoflo | 2025-10-01 | 28392 | 26992.8131 | 105.2% | Expected
Hilston Rotoflo | 2025-11-01 | 24635 | 28327.2857 | 86.97% | Moderate
Hilston Rotoflo | 2025-12-01 | 13946 | 27822.1255 | 50.13% | Poor
Hilston Rotoflo | 2026-01-01 | 25775 | 28849.7415 | 89.34% | Moderate
Hilston Rotoflo | 2026-02-01 | 24391 | 25188.8583 | 96.83% | Expected
Hilston Rotoflo | 2026-03-01 | 22838 | 23731.6668 | 96.23% | Expected
Hilston Rotoflo | 2026-04-01 | 19038.02 | 21116.8316 | 90.16% | Expected
Hilston Rotoflo | 2026-05-01 | 19892 | 18902.0819 | 105.2% | Expected
Hilston Rotoflo | 2026-06-01 | 13234 | 16713.3423 | 79.18% | Moderate
Hilston Rotoflo | 2026-08-01 | 23217 | 21672.6599 | 107.1% | Expected | NO
Hilston Rotoflo | 2026-09-01 | 22918 | 24094.518 | 95.12% | Expected | NO
Hilston Rotoflo | 2026-10-01 |  | 26803.9923
Hilston Rotoflo | 2026-11-01 |  | 28129.1299
Hilston Rotoflo | 2026-12-01 |  | 27627.5035
Huis Herfsblaar | 2024-01-01 |  | 30214.8
Huis Herfsblaar | 2024-02-01 |  | 26381.7
Huis Herfsblaar | 2024-03-01 |  | 27566.1
Huis Herfsblaar | 2024-04-01 |  | 23747.4
Huis Herfsblaar | 2024-05-01 |  | 22569.3
Huis Herfsblaar | 2024-06-01 | 5360 | 20228.4 | 26.5% | Poor
Huis Herfsblaar | 2024-07-01 | 22610 | 22349.4713 | 101.2% | Expected
Huis Herfsblaar | 2024-08-01 | 23490 | 26946.7248 | 87.17% | Moderate
Huis Herfsblaar | 2024-09-01 | 20740 | 28800.0375 | 72.01% | Moderate
Huis Herfsblaar | 2024-10-01 | 32140 | 30198.1203 | 106.4% | Expected
Huis Herfsblaar | 2024-11-01 | 32300 | 29304.88 | 110.2% | Expected
Huis Herfsblaar | 2024-12-01 | 29734 | 31120.8865 | 95.54% | Expected
Huis Herfsblaar | 2025-01-01 | 30000 | 30101.6974 | 99.66% | Expected
Huis Herfsblaar | 2025-02-01 | 20560 | 26267.2805 | 78.27% | Moderate
Huis Herfsblaar | 2025-03-01 | 19975 | 27431.7675 | 72.82% | Moderate
Huis Herfsblaar | 2025-04-01 | 19104 | 23617.5914 | 80.89% | Moderate
Huis Herfsblaar | 2025-05-01 | 23300 | 22432.9842 | 103.9% | Expected
Huis Herfsblaar | 2025-06-01 | 17947.87 | 20094.2392 | 89.32% | Moderate
Huis Herfsblaar | 2025-07-01 | 13847 | 22193.1317 | 62.39% | Poor
Huis Herfsblaar | 2025-08-01 | 22606 | 26758.2263 | 84.48% | Moderate
Huis Herfsblaar | 2025-09-01 | 23653 | 28598.5747 | 82.71% | Moderate
Huis Herfsblaar | 2025-10-01 | 29483 | 29986.8776 | 98.32% | Expected
Huis Herfsblaar | 2025-11-01 | 22193 | 29099.8857 | 76.26% | Moderate
Huis Herfsblaar | 2025-12-01 | 27897 | 30903.1889 | 90.27% | Expected
Huis Herfsblaar | 2026-01-01 | 26300 | 29891.1293 | 87.99% | Moderate
Huis Herfsblaar | 2026-02-01 | 27127.919 | 26083.535 | 104% | Expected
Huis Herfsblaar | 2026-03-01 | 23100 | 27239.8761 | 84.8% | Moderate
Huis Herfsblaar | 2026-04-01 | 19981.06 | 23452.381 | 85.2% | Moderate
Huis Herfsblaar | 2026-05-01 | 20533.1 | 22276.0604 | 92.18% | Expected
Huis Herfsblaar | 2026-06-01 | 15001.1 | 19953.6754 | 75.18% | Moderate
HB Dunn | 2026-07-01 | 2598 | 2983.3189 | 87.08% | Moderate | NO
Huis Herfsblaar | 2026-08-01 | 23941.67 | 26571.0465 | 90.1% | Expected | NO
Shoprite Thokoza | 2026-09-01 | 11994.93 | 16028.7181 | 74.83% | Moderate | NO
Huis Herfsblaar | 2026-10-01 |  | 29777.1127
Huis Herfsblaar | 2026-11-01 |  | 28896.3255
Huis Herfsblaar | 2026-12-01 |  | 30687.0141
IPID - Floor 4 | 2024-01-01 |  | 7573.5
IPID - Floor 4 | 2024-02-01 |  | 6513.75
IPID - Floor 4 | 2024-03-01 |  | 6841.35
IPID - Floor 4 | 2024-04-01 |  | 618.3
IPID - Floor 4 | 2024-05-01 |  | 5924.7
IPID - Floor 4 | 2024-06-01 |  | 5295.6
IPID - Floor 4 | 2024-07-01 |  | 5785.2
IPID - Floor 4 | 2024-08-01 |  | 6585.3
IPID - Floor 4 | 2024-09-01 |  | 7018.65
IPID - Floor 4 | 2024-10-01 |  | 7479.45
IPID - Floor 4 | 2024-11-01 |  | 7552.8
IPID - Floor 4 | 2024-12-01 |  | 7415.1
IPID - Floor 4 | 2025-01-01 |  | 7573.5
IPID - Floor 4 | 2025-02-01 |  | 6513.75
IPID - Floor 4 | 2025-03-01 |  | 6841.35
IPID - Floor 4 | 2025-04-01 |  | 618.3
IPID - Floor 4 | 2025-05-01 |  | 5924.7
IPID - Floor 4 | 2025-06-01 |  | 5295.6
IPID - Floor 4 | 2025-07-01 |  | 5785.2
IPID - Floor 4 | 2025-08-01 |  | 6585.3
IPID - Floor 4 | 2025-09-01 |  | 7018.65
IPID - Floor 4 | 2025-10-01 |  | 7479.45
IPID - Floor 4 | 2025-11-01 |  | 7548.7339
IPID - Floor 4 | 2025-12-01 | 5820 | 7406.8332 | 78.58% | Moderate
IPID - Floor 4 | 2026-01-01 | 7914 | 7560.5477 | 104.7% | Expected
IPID - Floor 4 | 2026-02-01 | 8094 | 6498.7344 | 124.5% | Expected
IPID - Floor 4 | 2026-03-01 | 6511 | 6821.9046 | 95.44% | Expected
IPID - Floor 4 | 2026-04-01 | 6094.6 | 6161.7511 | 98.91% | Expected
IPID - Floor 4 | 2026-05-01 | 7117.7 | 5900.9331 | 120.6% | Expected
IPID - Floor 4 | 2026-06-01 | 5909 | 5271.2131 | 112.1% | Expected
Helderberg Collage | 2026-07-01 | 14156 | 15986.1345 | 88.55% | Moderate | NO
IPID - Floor 4 | 2026-08-01 | 7937 | 6547.2882 | 121.2% | Expected | NO
IPID - Floor 4 | 2026-09-01 | 7314.8 | 6973.9777 | 104.9% | Expected | NO
IPID - Floor 4 | 2026-10-01 |  | 7427.5581
IPID - Floor 4 | 2026-11-01 |  | 7495.9288
IPID - Floor 4 | 2026-12-01 |  | 7355.0208
IPID - Floor 6 | 2024-01-01 |  | 7573.5
IPID - Floor 6 | 2024-02-01 |  | 6513.75
IPID - Floor 6 | 2024-03-01 |  | 6841.35
IPID - Floor 6 | 2024-04-01 |  | 618.3
IPID - Floor 6 | 2024-05-01 |  | 5924.7
IPID - Floor 6 | 2024-06-01 |  | 5295.6
IPID - Floor 6 | 2024-07-01 |  | 5785.2
IPID - Floor 6 | 2024-08-01 |  | 6585.3
IPID - Floor 6 | 2024-09-01 |  | 7018.65
IPID - Floor 6 | 2024-10-01 |  | 7479.45
IPID - Floor 6 | 2024-11-01 |  | 7552.8
IPID - Floor 6 | 2024-12-01 |  | 7415.1
IPID - Floor 6 | 2025-01-01 |  | 7573.5
IPID - Floor 6 | 2025-02-01 |  | 6513.75
IPID - Floor 6 | 2025-03-01 |  | 6841.35
IPID - Floor 6 | 2025-04-01 |  | 618.3
IPID - Floor 6 | 2025-05-01 |  | 5924.7
IPID - Floor 6 | 2025-06-01 |  | 5295.6
IPID - Floor 6 | 2025-07-01 |  | 5785.2
IPID - Floor 6 | 2025-08-01 |  | 6585.3
IPID - Floor 6 | 2025-09-01 |  | 7018.65
IPID - Floor 6 | 2025-10-01 |  | 7479.45
IPID - Floor 6 | 2025-11-01 |  | 7548.7339
IPID - Floor 6 | 2025-12-01 | 5820 | 7406.8332 | 78.58% | Moderate
IPID - Floor 6 | 2026-01-01 | 5904 | 7560.5477 | 78.09% | Moderate
IPID - Floor 6 | 2026-02-01 | 5406 | 6498.7344 | 83.19% | Moderate
IPID - Floor 6 | 2026-03-01 | 4115 | 6821.9046 | 60.32% | Poor
IPID - Floor 6 | 2026-04-01 | 4377 | 6161.7511 | 71.04% | Moderate
IPID - Floor 6 | 2026-05-01 | 4300 | 5900.9331 | 72.87% | Moderate
IPID - Floor 6 | 2026-06-01 | 3139.7 | 5271.2131 | 59.56% | Poor
Hilston Rotoflo | 2026-07-01 | 17975 | 18595.5675 | 96.66% | Expected | NO
IPID - Floor 6 | 2026-08-01 | 5281 | 6547.2882 | 80.66% | Moderate | NO
IPID - Floor 6 | 2026-09-01 | 4730 | 6973.9777 | 67.82% | Poor | NO
IPID - Floor 6 | 2026-10-01 |  | 7427.5581
IPID - Floor 6 | 2026-11-01 |  | 7495.9288
IPID - Floor 6 | 2026-12-01 |  | 7355.0208
Kool Village | 2024-01-01 | 13629 | 12213 | 111.6% | Expected
Kool Village | 2024-02-01 | 12014 | 10570.5 | 113.7% | Expected
Kool Village | 2024-03-01 | 12428 | 10619.1 | 117% | Expected
Kool Village | 2024-04-01 | 9084 | 9139.5 | 99.39% | Expected
Kool Village | 2024-05-01 | 8049 | 8593.2 | 93.67% | Expected
Kool Village | 2024-06-01 | 6600 | 7680.6 | 85.93% | Moderate
Kool Village | 2024-07-01 | 7832 | 8550.9 | 91.59% | Expected
Kool Village | 2024-08-01 | 8766 | 9997.2 | 87.68% | Moderate
Kool Village | 2024-09-01 | 9208 | 10701.9 | 86.04% | Moderate
Kool Village | 2024-10-01 | 12879 | 11834.1 | 108.8% | Expected
Kool Village | 2024-11-01 | 13410 | 12129.3 | 110.6% | Expected
Kool Village | 2024-12-01 | 13869 | 12998.7 | 106.7% | Expected
Kool Village | 2025-01-01 | 13136 | 12213 | 107.6% | Expected
Kool Village | 2025-02-01 | 10624 | 10570.5 | 100.5% | Expected
Kool Village | 2025-03-01 | 10420 | 10619.1 | 98.13% | Expected
Kool Village | 2025-04-01 | 7391 | 9139.5 | 80.87% | Moderate
Kool Village | 2025-05-01 | 7947 | 8593.2 | 92.48% | Expected
Kool Village | 2025-06-01 | 6390.63 | 7680.6 | 83.2% | Moderate
Kool Village | 2025-07-01 | 7146 | 8550.9 | 83.57% | Moderate
Kool Village | 2025-08-01 | 7396 | 9997.2 | 73.98% | Moderate
Kool Village | 2025-09-01 | 8160 | 10701.9 | 76.25% | Moderate
Kool Village | 2025-10-01 | 10866 | 11834.1 | 91.82% | Expected
Kool Village | 2025-11-01 | 10612 | 12129.3 | 87.49% | Moderate
Kool Village | 2025-12-01 | 11236 | 12998.7 | 86.44% | Moderate
Kool Village | 2026-01-01 | 13357 | 12213 | 109.4% | Expected
Kool Village | 2026-02-01 | 9365 | 10570.5 | 88.6% | Moderate
Kool Village | 2026-03-01 | 7814 | 10619.1 | 73.58% | Moderate
Kool Village | 2026-04-01 | 5599.56 | 9139.5 | 61.27% | Poor
Kool Village | 2026-05-01 | 5867.76 | 8593.2 | 68.28% | Poor
Kool Village | 2026-06-01 | 4645.31 | 7680.6 | 60.48% | Poor
Huis Herfsblaar | 2026-07-01 | 20850.76 | 22037.8858 | 94.61% | Expected | NO
Kool Village | 2026-08-01 | 8388.6689 | 9997.2 | 83.91% | Moderate | NO
Club Houghton | 2026-09-01 | 3663 | 4881.0693 | 75.05% | Moderate | YES
Kool Village | 2026-10-01 |  | 11834.1
Kool Village | 2026-11-01 |  | 12129.3
Kool Village | 2026-12-01 |  | 12998.7
Makalali | 2024-01-01 |  | 16525.8451
Makalali | 2024-02-01 |  | 14887.6787
Makalali | 2024-03-01 |  | 16240.8813
Makalali | 2024-04-01 |  | 15003.9515
Makalali | 2024-05-01 |  | 15164.8043
Makalali | 2024-06-01 |  | 14061.0544
Makalali | 2024-07-01 |  | 15048.0785
Makalali | 2024-08-01 |  | 16222.8628
Makalali | 2024-09-01 |  | 16132.4379
Makalali | 2024-10-01 |  | 15734.1588
Makalali | 2024-11-01 |  | 15182.6523
Makalali | 2024-12-01 |  | 16082.1794
Makalali | 2025-01-01 |  | 16409.9275
Makalali | 2025-02-01 |  | 14783.2517
Makalali | 2025-03-01 |  | 16127.2727
Makalali | 2025-04-01 |  | 14898.9955
Makalali | 2025-05-01 |  | 15058.7231
Makalali | 2025-06-01 |  | 13962.6941
Makalali | 2025-07-01 |  | 14942.8138
Makalali | 2025-08-01 |  | 16109.3802
Makalali | 2025-09-01 |  | 16019.5879
Makalali | 2025-10-01 |  | 15624.0948
Makalali | 2025-11-01 |  | 15076.4462
Makalali | 2025-12-01 |  | 15969.681
Makalali | 2026-01-01 | 13394 | 16295.1364 | 82.2% | Moderate
Makalali | 2026-02-01 | 16065 | 14679.8396 | 109.4% | Expected
Makalali | 2026-03-01 | 733 | 16014.4588 | 4.577% | Poor
Makalali | 2026-04-01 | 4797.7 | 14794.7737 | 32.43% | Poor
Makalali | 2026-05-01 | 5970.07 | 14953.3839 | 39.92% | Poor
Makalali | 2026-06-01 | 5060.4 | 13865.0219 | 36.5% | Poor
IPID - Floor 4 | 2026-07-01 | 7311 | 5755.2369 | 127% | Expected | NO
Makalali | 2026-08-01 | 7086.5031 | 15996.6915 | 44.3% | Poor | NO
Makalali | 2026-09-01 | 4821.7015 | 15907.5273 | 30.31% | Poor | NO
Makalali | 2026-10-01 |  | 15514.8008
Makalali | 2026-11-01 |  | 14970.9831
Makalali | 2026-12-01 |  | 15857.9694
Mambha Cash & Carry | 2024-01-01 | 18892 | 22065.7348 | 85.62% | Moderate
Mambha Cash & Carry | 2024-02-01 | 18598 | 19285.4136 | 96.44% | Expected
Mambha Cash & Carry | 2024-03-01 | 18598 | 19397.7357 | 95.88% | Expected
Mambha Cash & Carry | 2024-04-01 | 15678 | 15639.9631 | 100.2% | Expected
Mambha Cash & Carry | 2024-05-01 | 14588 | 13339.7934 | 109.4% | Expected
Mambha Cash & Carry | 2024-06-01 | 12745 | 11993.7618 | 106.3% | Expected
Mambha Cash & Carry | 2024-07-01 | 14803 | 12950.4536 | 114.3% | Expected
Mambha Cash & Carry | 2024-08-01 | 15941 | 15265.4022 | 104.4% | Expected
Mambha Cash & Carry | 2024-09-01 | 13907 | 16375.1762 | 84.93% | Moderate
Mambha Cash & Carry | 2024-10-01 | 19899 | 19177.7305 | 103.8% | Expected
Mambha Cash & Carry | 2024-11-01 | 18123 | 19736.1762 | 91.83% | Expected
Mambha Cash & Carry | 2024-12-01 | 18905 | 22164.4423 | 85.29% | Moderate
Mambha Cash & Carry | 2025-01-01 | 19907 | 21910.9586 | 90.85% | Expected
Mambha Cash & Carry | 2025-02-01 | 15243 | 19150.1395 | 79.6% | Moderate
Mambha Cash & Carry | 2025-03-01 | 17983 | 19262.0441 | 93.36% | Expected
Mambha Cash & Carry | 2025-04-01 | 13643 | 15530.558 | 87.85% | Moderate
Mambha Cash & Carry | 2025-05-01 | 15993 | 13246.4786 | 120.7% | Expected
Mambha Cash & Carry | 2025-06-01 | 13300.84 | 11909.8627 | 111.7% | Expected
Mambha Cash & Carry | 2025-07-01 | 12259 | 12859.8623 | 95.33% | Expected
Mambha Cash & Carry | 2025-08-01 | 14893 | 15158.6172 | 98.25% | Expected
Mambha Cash & Carry | 2025-09-01 | 13710 | 16260.6282 | 84.31% | Moderate
Mambha Cash & Carry | 2025-10-01 | 17312 | 19043.578 | 90.91% | Expected
Mambha Cash & Carry | 2025-11-01 | 19748 | 19598.1172 | 100.8% | Expected
Mambha Cash & Carry | 2025-12-01 | 19810 | 22009.3971 | 90.01% | Expected
Mambha Cash & Carry | 2026-01-01 | 21506.5322 | 21757.6866 | 98.85% | Expected
Mambha Cash & Carry | 2026-02-01 | 21266.5806 | 19016.1799 | 111.8% | Expected
Mambha Cash & Carry | 2026-03-01 | 18344 | 19127.3018 | 95.9% | Expected
Mambha Cash & Carry | 2026-04-01 | 14760.15 | 15421.9183 | 95.71% | Expected
Mambha Cash & Carry | 2026-05-01 | 14261.66 | 13153.8165 | 108.4% | Expected
Mambha Cash & Carry | 2026-06-01 | 12292.03 | 11826.5506 | 103.9% | Expected
IPID - Floor 6 | 2026-07-01 | 3841 | 5755.2369 | 66.74% | Poor | NO
Mambha Cash & Carry | 2026-08-01 | 15549.0352 | 15052.5793 | 103.3% | Expected | NO
HB Dunn | 2026-09-01 | 2916.4 | 3847.3122 | 75.8% | Moderate | NO
Mambha Cash & Carry | 2026-10-01 |  | 18910.3638
Mambha Cash & Carry | 2026-11-01 |  | 19461.024
Mambha Cash & Carry | 2026-12-01 |  | 21855.4364
Mathe Group Company | 2024-01-01 | 52780 | 60599.5172 | 87.1% | Moderate
Mathe Group Company | 2024-02-01 | 40425 | 54968.1636 | 73.54% | Moderate
Mathe Group Company | 2024-03-01 | 52832 | 57292.5308 | 92.21% | Expected
Mathe Group Company | 2024-04-01 | 46312 | 48300.2274 | 95.88% | Expected
Mathe Group Company | 2024-05-01 | 45881 | 43700.3079 | 105% | Expected
Mathe Group Company | 2024-06-01 | 36174 | 40345.7012 | 89.66% | Moderate
Mathe Group Company | 2024-07-01 | 49449 | 43320.8436 | 114.1% | Expected
Mathe Group Company | 2024-08-01 | 50022 | 47866.5319 | 104.5% | Expected
Mathe Group Company | 2024-09-01 | 41179 | 49520.6662 | 83.16% | Moderate
Mathe Group Company | 2024-10-01 | 38998 | 54309.8364 | 71.81% | Moderate
Mathe Group Company | 2024-11-01 | 54400 | 55607.3174 | 97.83% | Expected
Mathe Group Company | 2024-12-01 | 48109 | 59987.4341 | 80.2% | Moderate
Mathe Group Company | 2025-01-01 | 50600 | 60174.4526 | 84.09% | Moderate
Mathe Group Company | 2025-02-01 | 39450 | 54582.5992 | 72.28% | Moderate
Mathe Group Company | 2025-03-01 | 50665 | 56891.7566 | 89.06% | Moderate
Mathe Group Company | 2025-04-01 | 33121 | 47962.3565 | 69.06% | Poor
Mathe Group Company | 2025-05-01 | 49152 | 43394.6143 | 113.3% | Expected
Mathe Group Company | 2025-06-01 | 39999.41 | 40063.4739 | 99.84% | Expected
Mathe Group Company | 2025-07-01 | 42250 | 43017.8045 | 98.22% | Expected
Mathe Group Company | 2025-08-01 | 42926 | 47531.6947 | 90.31% | Expected
Mathe Group Company | 2025-09-01 | 40517.3 | 49174.258 | 82.4% | Moderate
Mathe Group Company | 2025-10-01 | 46787.68 | 53929.9269 | 86.76% | Moderate
Mathe Group Company | 2025-11-01 | 53245 | 55218.3316 | 96.43% | Expected
Mathe Group Company | 2025-12-01 | 48360 | 59567.8084 | 81.18% | Moderate
Mathe Group Company | 2026-01-01 | 49681.6714 | 59753.5187 | 83.14% | Moderate
Mathe Group Company | 2026-02-01 | 58060.8339 | 54200.7816 | 107.1% | Expected
Mathe Group Company | 2026-03-01 | 50832 | 56493.7859 | 89.98% | Moderate
Mathe Group Company | 2026-04-01 | 41412.22 | 47626.849 | 86.95% | Moderate
Mathe Group Company | 2026-05-01 | 46300.95 | 43091.0592 | 107.4% | Expected
Mathe Group Company | 2026-06-01 | 37511.86 | 39783.2209 | 94.29% | Expected
Kool Village | 2026-07-01 | 6582.2 | 8550.9 | 76.98% | Moderate | YES
Mathe Group Company | 2026-08-01 | 49938.125 | 47199.1998 | 105.8% | Expected | NO
Trouw Nutrition | 2026-09-01 | 10023.98 | 13089.1709 | 76.58% | Moderate | YES
Mathe Group Company | 2026-10-01 |  | 53552.6749
Mathe Group Company | 2026-11-01 |  | 54832.0669
Mathe Group Company | 2026-12-01 |  | 59151.1182
Mdluli | 2024-01-01 |  | 15870.6
Mdluli | 2024-02-01 |  | 14825.7
Mdluli | 2024-03-01 |  | 17314.2
Mdluli | 2024-04-01 | 6916 | 15358.5 | 45.03% | Poor
Mdluli | 2024-05-01 | 14281 | 15193.3086 | 94% | Expected
Mdluli | 2024-06-01 | 12149 | 14476.5658 | 83.92% | Moderate
Mdluli | 2024-07-01 | 15601 | 15368.7158 | 101.5% | Expected
Mdluli | 2024-08-01 | 7706 | 15581.4029 | 49.46% | Poor
Mdluli | 2024-09-01 | 1 | 15151.1267 | 0.0066% | Poor
Mdluli | 2024-10-01 | 7310 | 14303.5859 | 51.11% | Poor
Mdluli | 2024-11-01 | 13770 | 13207.5099 | 104.3% | Expected
Mdluli | 2024-12-01 |  | 13778.7479
Mdluli | 2025-01-01 | 4700 | 15791.7423 | 29.76% | Poor
Mdluli | 2025-02-01 | 12300 | 14743.2416 | 83.43% | Moderate
Mdluli | 2025-03-01 | 13554 | 17208.6315 | 78.76% | Moderate
Mdluli | 2025-04-01 | 9839 | 15255.7576 | 64.49% | Poor
Mdluli | 2025-05-01 |  | 15087.028
Mdluli | 2025-06-01 | 12605.8 | 14375.2989 | 87.69% | Moderate
Mdluli | 2025-07-01 | 8064 | 15261.2081 | 52.84% | Poor
Mdluli | 2025-08-01 | 13494 | 15472.4075 | 87.21% | Moderate
Mdluli | 2025-09-01 | 11744.7 | 15045.1411 | 78.06% | Moderate
Mdluli | 2025-10-01 | 13202 | 14203.529 | 92.95% | Expected
Mdluli | 2025-11-01 | 10765 | 13115.1203 | 82.08% | Moderate
Mdluli | 2025-12-01 | 13231 | 13682.3624 | 96.7% | Expected
Mdluli | 2026-01-01 | 11720.01 | 15681.2755 | 74.74% | Moderate
Mdluli | 2026-02-01 | 15533 | 14640.1093 | 106.1% | Expected
Mdluli | 2026-03-01 | 12559 | 17088.2532 | 73.49% | Moderate
Mdluli | 2026-04-01 | 11577.01 | 15149.0401 | 76.42% | Moderate
Mdluli | 2026-05-01 | 13966.89 | 14981.4908 | 93.23% | Expected
Mdluli | 2026-06-01 | 11309.7 | 14274.7405 | 79.23% | Moderate
Makalali | 2026-07-01 | 6010.4032 | 14838.2854 | 40.51% | Poor | NO
Mdluli | 2026-08-01 | 14728.02 | 15364.1745 | 95.86% | Expected | NO
Bendstore Spar | 2026-09-01 | 36563.6 | 47682.577 | 76.68% | Moderate | NO
Mdluli | 2026-10-01 |  | 14104.1722
Mdluli | 2026-11-01 |  | 13023.3771
Mdluli | 2026-12-01 |  | 13586.6512
Medipost | 2024-01-01 |  | 53361.9
Medipost | 2024-02-01 |  | 43750.8
Medipost | 2024-03-01 |  | 40931.1
Medipost | 2024-04-01 |  | 29080.8
Medipost | 2024-05-01 |  | 21434.4
Medipost | 2024-06-01 |  | 17483.4
Medipost | 2024-07-01 |  | 19783.8
Medipost | 2024-08-01 |  | 25524
Medipost | 2024-09-01 |  | 33381.9
Medipost | 2024-10-01 |  | 43038
Medipost | 2024-11-01 |  | 49565.7
Medipost | 2024-12-01 |  | 54135.9
Medipost | 2025-01-01 |  | 53361.9
Medipost | 2025-02-01 |  | 43750.8
Medipost | 2025-03-01 |  | 40927.9513
Medipost | 2025-04-01 |  | 29061.2314
Medipost | 2025-05-01 |  | 21407.6215
Medipost | 2025-06-01 |  | 17451.1501
Medipost | 2025-07-01 |  | 19735.9164
Medipost | 2025-08-01 |  | 25447.0471
Medipost | 2025-09-01 |  | 33261.4196
Medipost | 2025-10-01 |  | 42857.9344
Medipost | 2025-11-01 |  | 49328.9045
Medipost | 2025-12-01 | 44400 | 53846.1942 | 82.46% | Moderate
Medipost | 2026-01-01 | 44972.3 | 53044.7014 | 84.78% | Moderate
Medipost | 2026-02-01 | 44384 | 43464.811 | 102.1% | Expected
Medipost | 2026-03-01 | 42181 | 40641.6511 | 103.8% | Expected
Medipost | 2026-04-01 | 29438.84 | 28857.9415 | 102% | Expected
Medipost | 2026-05-01 | 20478.6 | 21257.8704 | 96.33% | Expected
Medipost | 2026-06-01 | 18349.15 | 17329.0754 | 105.9% | Expected
Mambha Cash & Carry | 2026-07-01 | 12604.391 | 12769.9046 | 98.7% | Expected | NO
Medipost | 2026-08-01 | 26558.07 | 25269.0392 | 105.1% | Expected | NO
Medipost | 2026-09-01 | 31565.57 | 33028.7485 | 95.57% | Expected | NO
Medipost | 2026-10-01 |  | 42558.1335
Medipost | 2026-11-01 |  | 48983.8377
Medipost | 2026-12-01 |  | 53469.5279
Meredale Heights | 2024-01-01 | 3824 | 5059.167 | 75.59% | Moderate
Meredale Heights | 2024-02-01 | 3746 | 4591.8718 | 81.58% | Moderate
Meredale Heights | 2024-03-01 | 3799 | 5061.8154 | 75.05% | Moderate
Meredale Heights | 2024-04-01 | 3854 | 4851.9362 | 79.43% | Moderate
Meredale Heights | 2024-05-01 | 4391 | 5156.71 | 85.15% | Moderate
Meredale Heights | 2024-06-01 | 4167 | 4983.4293 | 83.62% | Moderate
Meredale Heights | 2024-07-01 | 4515 | 5360.5496 | 84.23% | Moderate
Meredale Heights | 2024-08-01 | 4113 | 5610.2515 | 73.31% | Moderate
Meredale Heights | 2024-09-01 | 3620 | 5556.1893 | 65.15% | Poor
Meredale Heights | 2024-10-01 | 4760 | 5458.365 | 87.21% | Moderate
Meredale Heights | 2024-11-01 | 3916 | 5076.0147 | 77.15% | Moderate
Meredale Heights | 2024-12-01 | 4124 | 5185.3158 | 79.53% | Moderate
Meredale Heights | 2025-01-01 | 3080 | 5023.6804 | 61.31% | Poor
Meredale Heights | 2025-02-01 | 2400 | 4559.6629 | 52.64% | Poor
Meredale Heights | 2025-03-01 | 2832 | 5026.4069 | 56.34% | Poor
Meredale Heights | 2025-04-01 | 2690 | 4817.9958 | 55.83% | Poor
Meredale Heights | 2025-05-01 | 3597 | 5120.6377 | 70.25% | Moderate
Meredale Heights | 2025-06-01 | 4831.17 | 4948.5691 | 97.63% | Expected
Meredale Heights | 2025-07-01 | 5152 | 5323.0514 | 96.79% | Expected
Meredale Heights | 2025-08-01 | 5913 | 5571.0065 | 106.1% | Expected
Meredale Heights | 2025-09-01 | 5163 | 5517.3225 | 93.58% | Expected
Meredale Heights | 2025-10-01 | 5859 | 5420.1825 | 108.1% | Expected
Meredale Heights | 2025-11-01 | 4665 | 5040.5069 | 92.55% | Expected
Meredale Heights | 2025-12-01 | 5472 | 5149.0434 | 106.3% | Expected
Meredale Heights | 2026-01-01 | 5579.67 | 4988.5386 | 111.8% | Expected
Meredale Heights | 2026-02-01 | 4787 | 4527.767 | 105.7% | Expected
Meredale Heights | 2026-03-01 | 4406 | 4991.246 | 88.27% | Moderate
Meredale Heights | 2026-04-01 | 4506.8 | 4784.2929 | 94.2% | Expected
Meredale Heights | 2026-05-01 | 5143.42 | 5084.8177 | 101.2% | Expected
Meredale Heights | 2026-06-01 | 4820.5 | 4913.9527 | 98.1% | Expected
Mathe Group Company | 2026-07-01 | 40997.1224 | 42716.8853 | 95.97% | Expected | NO
Meredale Heights | 2026-08-01 | 6058 | 5532.0361 | 109.5% | Expected | NO
Meredale Heights | 2026-09-01 | 5214.57 | 5478.7276 | 95.18% | Expected | NO
Meredale Heights | 2026-10-01 |  | 5382.2671
Meredale Heights | 2026-11-01 |  | 5005.2474
Meredale Heights | 2026-12-01 |  | 5113.0247
Monument Park Checkers | 2024-01-01 |  | 40416.3
Monument Park Checkers | 2024-02-01 |  | 33988.5
Monument Park Checkers | 2024-03-01 | 41550.8 | 35131.7243 | 118.3% | Expected
Monument Park Checkers | 2024-04-01 | 25447.6 | 29885.0021 | 85.15% | Moderate
Monument Park Checkers | 2024-05-01 | 28056 | 28349.4758 | 98.96% | Expected
Monument Park Checkers | 2024-06-01 | 27241 | 25596.0777 | 106.4% | Expected
Monument Park Checkers | 2024-07-01 | 31078 | 28294.6875 | 109.8% | Expected
Monument Park Checkers | 2024-08-01 | 33515 | 32908.9863 | 101.8% | Expected
Monument Park Checkers | 2024-09-01 | 34245 | 36391.3894 | 94.1% | Expected
Monument Park Checkers | 2024-10-01 | 46108 | 39519.0522 | 116.7% | Expected
Monument Park Checkers | 2024-11-01 | 42922 | 39560.8877 | 108.5% | Expected
Monument Park Checkers | 2024-12-01 | 44138 | 42294.4985 | 104.4% | Expected
Monument Park Checkers | 2025-01-01 | 41100 | 40178.3719 | 102.3% | Expected
Monument Park Checkers | 2025-02-01 | 30900 | 33768.2732 | 91.51% | Expected
Monument Park Checkers | 2025-03-01 | 31593 | 34885.97 | 90.56% | Expected
Monument Park Checkers | 2025-04-01 | 25646 | 29675.9497 | 86.42% | Moderate
Monument Park Checkers | 2025-05-01 | 33184 | 28151.1648 | 117.9% | Expected
Monument Park Checkers | 2025-06-01 | 29359.5 | 25417.0273 | 115.5% | Expected
Monument Park Checkers | 2025-07-01 | 23487 | 28096.7597 | 83.59% | Moderate
Monument Park Checkers | 2025-08-01 | 34316 | 32678.7805 | 105% | Expected
Monument Park Checkers | 2025-09-01 | 33632.7 | 36136.8234 | 93.07% | Expected
Monument Park Checkers | 2025-10-01 | 41353 | 39242.6075 | 105.4% | Expected
Monument Park Checkers | 2025-11-01 | 44434 | 39284.1504 | 113.1% | Expected
Monument Park Checkers | 2025-12-01 | 40551 | 41998.6389 | 96.55% | Expected
Monument Park Checkers | 2026-01-01 | 42821 | 39897.3151 | 107.3% | Expected
Monument Park Checkers | 2026-02-01 | 39129 | 33532.0565 | 116.7% | Expected
Monument Park Checkers | 2026-03-01 | 31935 | 34641.9348 | 92.19% | Expected
Monument Park Checkers | 2026-04-01 | 26513.02 | 29468.3598 | 89.97% | Moderate
Monument Park Checkers | 2026-05-01 | 29984.36 | 27954.241 | 107.3% | Expected
Monument Park Checkers | 2026-06-01 | 23145.12 | 25239.2295 | 91.7% | Expected
Mdluli | 2026-07-01 | 13303 | 15154.4525 | 87.78% | Moderate | NO
Monument Park Checkers | 2026-08-01 | 35675.901 | 32450.1851 | 109.9% | Expected | NO
Monument Park Checkers | 2026-09-01 | 33460.18 | 35884.0382 | 93.25% | Expected | NO
Monument Park Checkers | 2026-10-01 |  | 38968.0966
Monument Park Checkers | 2026-11-01 |  | 39009.3489
Monument Park Checkers | 2026-12-01 |  | 41704.849
Nkambeni Industrial | 2024-01-01 |  | 23494.2439
Nkambeni Industrial | 2024-02-01 |  | 21618.2968
Nkambeni Industrial | 2024-03-01 |  | 24132.9682
Nkambeni Industrial | 2024-04-01 |  | 20780.5133
Nkambeni Industrial | 2024-05-01 |  | 19923.2904
Nkambeni Industrial | 2024-06-01 |  | 18392.0907
Nkambeni Industrial | 2024-07-01 |  | 19903.9083
Nkambeni Industrial | 2024-08-01 |  | 20921.6293
Nkambeni Industrial | 2024-09-01 |  | 21257.7779
Nkambeni Industrial | 2024-10-01 |  | 20807.7612
Nkambeni Industrial | 2024-11-01 |  | 19698.1516
Nkambeni Industrial | 2024-12-01 |  | 21003.4726
Nkambeni Industrial | 2025-01-01 | 21130 | 23329.4477 | 90.57% | Expected
Nkambeni Industrial | 2025-02-01 | 17140 | 21466.6591 | 79.84% | Moderate
Nkambeni Industrial | 2025-03-01 |  | 23964.1526
Nkambeni Industrial | 2025-04-01 |  | 20635.1489
Nkambeni Industrial | 2025-05-01 |  | 19783.9225
Nkambeni Industrial | 2025-06-01 |  | 18263.4338
Nkambeni Industrial | 2025-07-01 |  | 19764.6759
Nkambeni Industrial | 2025-08-01 |  | 20775.2778
Nkambeni Industrial | 2025-09-01 |  | 21109.075
Nkambeni Industrial | 2025-10-01 |  | 20662.2062
Nkambeni Industrial | 2025-11-01 |  | 19560.3586
Nkambeni Industrial | 2025-12-01 |  | 20856.5486
Nkambeni Industrial | 2026-01-01 | 9830 | 23166.253 | 42.43% | Poor
Nkambeni Industrial | 2026-02-01 | 20200 | 21316.4949 | 94.76% | Expected
Nkambeni Industrial | 2026-03-01 | 16198 | 23796.5179 | 68.07% | Poor
Nkambeni Industrial | 2026-04-01 |  | 20490.8014
Nkambeni Industrial | 2026-05-01 |  | 19645.5295
Nkambeni Industrial | 2026-06-01 |  | 18135.677
Medipost | 2026-07-01 | 20358.73 | 19597.8593 | 103.9% | Expected | NO
Nkambeni Industrial | 2026-08-01 |  | 20629.95 |  |  | NO
Nkambeni Industrial | 2026-09-01 |  | 20961.4122 |  |  | NO
Nkambeni Industrial | 2026-10-01 |  | 20517.6695
Nkambeni Industrial | 2026-11-01 |  | 19423.5295
Nkambeni Industrial | 2026-12-01 |  | 20710.6523
Olievenhoutbosch 1 | 2024-01-01 |  | 46872
Olievenhoutbosch 1 | 2024-02-01 |  | 40989.6
Olievenhoutbosch 1 | 2024-03-01 |  | 39989.7
Olievenhoutbosch 1 | 2024-04-01 |  | 34783.2
Olievenhoutbosch 1 | 2024-05-01 |  | 32139
Olievenhoutbosch 1 | 2024-06-01 |  | 28357.2
Olievenhoutbosch 1 | 2024-07-01 |  | 31229.1
Olievenhoutbosch 1 | 2024-08-01 |  | 36815.4
Olievenhoutbosch 1 | 2024-09-01 |  | 40778.1
Olievenhoutbosch 1 | 2024-10-01 |  | 46212.3
Olievenhoutbosch 1 | 2024-11-01 |  | 46653.3
Olievenhoutbosch 1 | 2024-12-01 |  | 47656.8
Olievenhoutbosch 1 | 2025-01-01 |  | 46872
Olievenhoutbosch 1 | 2025-02-01 |  | 40989.6
Olievenhoutbosch 1 | 2025-03-01 |  | 39989.7
Olievenhoutbosch 1 | 2025-04-01 |  | 34783.2
Olievenhoutbosch 1 | 2025-05-01 |  | 32139
Olievenhoutbosch 1 | 2025-06-01 |  | 28357.2
Olievenhoutbosch 1 | 2025-07-01 |  | 31229.1
Olievenhoutbosch 1 | 2025-08-01 |  | 36815.4
Olievenhoutbosch 1 | 2025-09-01 |  | 40778.1
Olievenhoutbosch 1 | 2025-10-01 | 42200 | 46206.079 | 91.33% | Expected
Olievenhoutbosch 1 | 2025-11-01 | 37652 | 46619.2169 | 80.76% | Moderate
Olievenhoutbosch 1 | 2025-12-01 | 32569 | 47594.5152 | 68.43% | Poor
Olievenhoutbosch 1 | 2026-01-01 | 43979.9977 | 46782.8405 | 94.01% | Expected
Olievenhoutbosch 1 | 2026-02-01 | 35538.4873 | 40887.2456 | 86.92% | Moderate
Olievenhoutbosch 1 | 2026-03-01 | 34079 | 39868.3673 | 85.48% | Moderate
Olievenhoutbosch 1 | 2026-04-01 | 26385.27 | 34656.9956 | 76.13% | Moderate
Olievenhoutbosch 1 | 2026-05-01 | 29535.2 | 32003.9189 | 92.29% | Expected
Olievenhoutbosch 1 | 2026-06-01 | 18559 | 28221.1834 | 65.76% | Poor
Meredale Heights | 2026-07-01 | 5690 | 5285.8154 | 107.6% | Expected | NO
Olievenhoutbosch 1 | 2026-08-01 | 35179.4355 | 36595.8548 | 96.13% | Expected | NO
Alpine Heath Resort | 2026-09-01 | 21788 | 28181.7251 | 77.31% | Moderate | NO
Olievenhoutbosch 1 | 2026-10-01 |  | 45882.8571
Olievenhoutbosch 1 | 2026-11-01 |  | 46293.1049
Olievenhoutbosch 1 | 2026-12-01 |  | 47261.5808
Olievenhoutbosch 2 | 2024-01-01 |  | 12369.6
Olievenhoutbosch 2 | 2024-02-01 |  | 10801.8
Olievenhoutbosch 2 | 2024-03-01 |  | 10537.2
Olievenhoutbosch 2 | 2024-04-01 |  | 9173.7
Olievenhoutbosch 2 | 2024-05-01 |  | 8503.2
Olievenhoutbosch 2 | 2024-06-01 |  | 7545.6
Olievenhoutbosch 2 | 2024-07-01 |  | 8307
Olievenhoutbosch 2 | 2024-08-01 |  | 9720.9
Olievenhoutbosch 2 | 2024-09-01 |  | 10755.9
Olievenhoutbosch 2 | 2024-10-01 |  | 12190.5
Olievenhoutbosch 2 | 2024-11-01 |  | 12263.4
Olievenhoutbosch 2 | 2024-12-01 |  | 12539.7
Olievenhoutbosch 2 | 2025-01-01 |  | 12369.6
Olievenhoutbosch 2 | 2025-02-01 |  | 10801.8
Olievenhoutbosch 2 | 2025-03-01 |  | 10537.2
Olievenhoutbosch 2 | 2025-04-01 |  | 9173.7
Olievenhoutbosch 2 | 2025-05-01 |  | 8503.2
Olievenhoutbosch 2 | 2025-06-01 |  | 7545.6
Olievenhoutbosch 2 | 2025-07-01 |  | 8307
Olievenhoutbosch 2 | 2025-08-01 |  | 9720.9
Olievenhoutbosch 2 | 2025-09-01 |  | 10755.9
Olievenhoutbosch 2 | 2025-10-01 | 11800 | 12188.8589 | 96.81% | Expected
Olievenhoutbosch 2 | 2025-11-01 | 9938 | 12254.4408 | 81.1% | Moderate
Olievenhoutbosch 2 | 2025-12-01 | 9094 | 12523.3113 | 72.62% | Moderate
Olievenhoutbosch 2 | 2026-01-01 | 11835.674 | 12346.0707 | 95.87% | Expected
Olievenhoutbosch 2 | 2026-02-01 | 9479.8288 | 10774.827 | 87.98% | Moderate
Olievenhoutbosch 2 | 2026-03-01 | 9043 | 10505.2291 | 86.08% | Moderate
Olievenhoutbosch 2 | 2026-04-01 | 7039.32 | 9140.4149 | 77.01% | Moderate
Olievenhoutbosch 2 | 2026-05-01 | 8144.81 | 8467.4608 | 96.19% | Expected
Olievenhoutbosch 2 | 2026-06-01 | 5600 | 7509.4072 | 74.57% | Moderate
Monument Park Checkers | 2026-07-01 | 27326.29 | 27900.2166 | 97.94% | Expected | NO
Olievenhoutbosch 2 | 2026-08-01 | 9590.4249 | 9662.9303 | 99.25% | Expected | NO
The Alec | 2026-09-01 | 4853.26 | 6201.3598 | 78.26% | Moderate | NO
Olievenhoutbosch 2 | 2026-10-01 |  | 12103.5951
Olievenhoutbosch 2 | 2026-11-01 |  | 12168.7182
Olievenhoutbosch 2 | 2026-12-01 |  | 12435.7079
Opal Students | 2024-01-01 | 337 | 5672.4123 | 5.941% | Poor
Opal Students | 2024-02-01 | 4222 | 4767.1197 | 88.57% | Moderate
Opal Students | 2024-03-01 | 5410 | 4918.7326 | 110% | Expected
Opal Students | 2024-04-01 | 4799 | 4342.1115 | 110.5% | Expected
Opal Students | 2024-05-01 | 4368 | 4174.7664 | 104.6% | Expected
Opal Students | 2024-06-01 | 3307 | 3798.9219 | 87.05% | Moderate
Opal Students | 2024-07-01 | 3819 | 4193.1369 | 91.08% | Expected
Opal Students | 2024-08-01 | 5147 | 4813.957 | 106.9% | Expected
Opal Students | 2024-09-01 | 4101 | 5263.3283 | 77.92% | Moderate
Opal Students | 2024-10-01 | 6591 | 5624.7344 | 117.2% | Expected
Opal Students | 2024-11-01 | 4960 | 5578.532 | 88.91% | Moderate
Opal Students | 2024-12-01 | 652 | 5943.79 | 10.97% | Poor
Opal Students | 2025-01-01 | 720 | 5632.6242 | 12.78% | Poor
Opal Students | 2025-02-01 | 3776 | 4733.6815 | 79.77% | Moderate
Opal Students | 2025-03-01 | 4415 | 4884.3249 | 90.39% | Expected
Opal Students | 2025-04-01 | 3551 | 4311.7374 | 82.36% | Moderate
Opal Students | 2025-05-01 | 4580 | 4145.563 | 110.5% | Expected
Opal Students | 2025-06-01 | 3965.8 | 3772.3476 | 105.1% | Expected
Opal Students | 2025-07-01 | 4015 | 4163.805 | 96.43% | Expected
Opal Students | 2025-08-01 | 4593 | 4780.2823 | 96.08% | Expected
Opal Students | 2025-09-01 | 4428 | 5226.5101 | 84.72% | Moderate
Opal Students | 2025-10-01 | 6002 | 5585.3881 | 107.5% | Expected
Opal Students | 2025-11-01 | 4286 | 5539.5089 | 77.37% | Moderate
Opal Students | 2025-12-01 | 985 | 5902.2118 | 16.69% | Poor
Opal Students | 2026-01-01 | 1496.8 | 5593.2227 | 26.76% | Poor
Opal Students | 2026-02-01 | 4735 | 4700.5684 | 100.7% | Expected
Opal Students | 2026-03-01 | 4747 | 4850.158 | 97.87% | Expected
Opal Students | 2026-04-01 | 4036.9 | 4281.5759 | 94.29% | Expected
Opal Students | 2026-05-01 | 4180 | 4116.5638 | 101.5% | Expected
Opal Students | 2026-06-01 | 3164 | 3745.9592 | 84.46% | Moderate
Nkambeni Industrial | 2026-07-01 | 0 | 19626.4176 | 0% | Poor | NO
Opal Students | 2026-08-01 | 4901 | 4746.8432 | 103.2% | Expected | NO
Opal Students | 2026-09-01 | 4904 | 5189.9495 | 94.49% | Expected | NO
Opal Students | 2026-10-01 |  | 5546.3171
Opal Students | 2026-11-01 |  | 5500.7588
Opal Students | 2026-12-01 |  | 5860.9245
Orthochem Bethlehem | 2024-01-01 | 27336 | 41057.3833 | 66.58% | Poor
Orthochem Bethlehem | 2024-02-01 | 34673 | 35822.8744 | 96.79% | Expected
Orthochem Bethlehem | 2024-03-01 | 35335 | 36383.9186 | 97.12% | Expected
Orthochem Bethlehem | 2024-04-01 | 23354 | 33422.3507 | 69.88% | Poor
Orthochem Bethlehem | 2024-05-01 | 24682 | 32761.4542 | 75.34% | Moderate
Orthochem Bethlehem | 2024-06-01 | 21004 | 29820.8518 | 70.43% | Moderate
Orthochem Bethlehem | 2024-07-01 | 24855 | 32227.787 | 77.12% | Moderate
Orthochem Bethlehem | 2024-08-01 | 27804 | 36223.577 | 76.76% | Moderate
Orthochem Bethlehem | 2024-09-01 | 24854 | 37059.5266 | 67.07% | Poor
Orthochem Bethlehem | 2024-10-01 | 41343 | 39825.2302 | 103.8% | Expected
Orthochem Bethlehem | 2024-11-01 | 40614 | 39947.6424 | 101.7% | Expected
Orthochem Bethlehem | 2024-12-01 | 20454 | 42172.6352 | 48.5% | Poor
Orthochem Bethlehem | 2025-01-01 | 35500 | 40769.3936 | 87.08% | Moderate
Orthochem Bethlehem | 2025-02-01 | 33170 | 35571.6011 | 93.25% | Expected
Orthochem Bethlehem | 2025-03-01 | 29562 | 36129.4049 | 81.82% | Moderate
Orthochem Bethlehem | 2025-04-01 | 23660 | 33188.5538 | 71.29% | Moderate
Orthochem Bethlehem | 2025-05-01 | 27021 | 32532.2804 | 83.06% | Moderate
Orthochem Bethlehem | 2025-06-01 | 23016.87 | 29612.2483 | 77.73% | Moderate
Orthochem Bethlehem | 2025-07-01 | 23980 | 32002.3464 | 74.93% | Moderate
Orthochem Bethlehem | 2025-08-01 | 26825 | 35970.1849 | 74.58% | Moderate
Orthochem Bethlehem | 2025-09-01 | 29989 | 36800.2869 | 81.49% | Moderate
Orthochem Bethlehem | 2025-10-01 | 39431.18 | 39546.6438 | 99.71% | Expected
Orthochem Bethlehem | 2025-11-01 | 36933 | 39668.1997 | 93.1% | Expected
Orthochem Bethlehem | 2025-12-01 | 24542 | 41877.6281 | 58.6% | Poor
Orthochem Bethlehem | 2026-01-01 | 38558.8383 | 40484.2025 | 95.24% | Expected
Orthochem Bethlehem | 2026-02-01 | 35289.5949 | 35322.7698 | 99.91% | Expected
Orthochem Bethlehem | 2026-03-01 | 33082 | 35876.6715 | 92.21% | Expected
Orthochem Bethlehem | 2026-04-01 | 26958.67 | 32956.3924 | 81.8% | Moderate
Orthochem Bethlehem | 2026-05-01 | 28264.56 | 32304.7098 | 87.49% | Moderate
Orthochem Bethlehem | 2026-06-01 | 20267.33 | 29405.1039 | 68.92% | Poor
Olievenhoutbosch 1 | 2026-07-01 | 27717.5927 | 31061.3815 | 89.23% | Moderate | YES
Orthochem Bethlehem | 2026-08-01 | 24964.912 | 35718.5654 | 69.89% | Poor | YES
Orthochem Bethlehem | 2026-09-01 | 22767.1484 | 36542.8606 | 62.3% | Poor | NO
Orthochem Bethlehem | 2026-10-01 |  | 39270.0061
Orthochem Bethlehem | 2026-11-01 |  | 39390.7117
Orthochem Bethlehem | 2026-12-01 |  | 41584.6846
PNB Unlimited | 2024-01-01 | 12283 | 11292.6341 | 108.8% | Expected
PNB Unlimited | 2024-02-01 | 11752 | 9644.3615 | 121.9% | Expected
PNB Unlimited | 2024-03-01 | 11293 | 10111.1636 | 111.7% | Expected
PNB Unlimited | 2024-04-01 | 10034 | 8614.661 | 116.5% | Expected
PNB Unlimited | 2024-05-01 | 7886 | 8334.9478 | 94.61% | Expected
PNB Unlimited | 2024-06-01 | 9067 | 7512.3267 | 120.7% | Expected
PNB Unlimited | 2024-07-01 | 8952 | 8275.564 | 108.2% | Expected
PNB Unlimited | 2024-08-01 | 8952 | 9560.1453 | 93.64% | Expected
PNB Unlimited | 2024-09-01 | 8110 | 10427.0635 | 77.78% | Moderate
PNB Unlimited | 2024-10-01 | 12770 | 11106.2029 | 115% | Expected
PNB Unlimited | 2024-11-01 | 10951 | 11031.4901 | 99.27% | Expected
PNB Unlimited | 2024-12-01 | 11135 | 11766.0984 | 94.64% | Expected
PNB Unlimited | 2025-01-01 | 10294 | 11213.4239 | 91.8% | Expected
PNB Unlimited | 2025-02-01 | 7952 | 9576.7129 | 83.03% | Moderate
PNB Unlimited | 2025-03-01 | 9856 | 10040.4337 | 98.16% | Expected
PNB Unlimited | 2025-04-01 | 7739 | 8554.3995 | 90.47% | Expected
PNB Unlimited | 2025-05-01 | 9189 | 8276.643 | 111% | Expected
PNB Unlimited | 2025-06-01 | 7656.32 | 7459.7762 | 102.6% | Expected
PNB Unlimited | 2025-07-01 | 8158 | 8217.6745 | 99.27% | Expected
PNB Unlimited | 2025-08-01 | 5429 | 9493.2699 | 57.19% | Poor
PNB Unlimited | 2025-09-01 | 7249 | 10354.1239 | 70.01% | Moderate
PNB Unlimited | 2025-10-01 | 8107 | 11028.5125 | 73.51% | Moderate
PNB Unlimited | 2025-11-01 | 2305 | 10954.3223 | 21.04% | Poor
PNB Unlimited | 2025-12-01 | 7641 | 11683.7919 | 65.4% | Poor
PNB Unlimited | 2026-01-01 | 9717 | 11134.9835 | 87.27% | Moderate
PNB Unlimited | 2026-02-01 | 8045 | 9509.7216 | 84.6% | Moderate
PNB Unlimited | 2026-03-01 | 7035 | 9970.1986 | 70.56% | Moderate
PNB Unlimited | 2026-04-01 | 3742.54 | 8494.5595 | 44.06% | Poor
PNB Unlimited | 2026-05-01 | 6041.14 | 8218.746 | 73.5% | Moderate
PNB Unlimited | 2026-06-01 | 3334 | 7407.5934 | 45.01% | Poor
Olievenhoutbosch 2 | 2026-07-01 | 7966.5733 | 8262.3866 | 96.42% | Expected | YES
PNB Unlimited | 2026-08-01 | 6624 | 9426.8624 | 70.27% | Moderate | YES
PNB Unlimited | 2026-09-01 | 6723.42 | 10281.6944 | 65.39% | Poor | NO
PNB Unlimited | 2026-10-01 |  | 10951.3656
PNB Unlimited | 2026-11-01 |  | 10877.6944
PNB Unlimited | 2026-12-01 |  | 11602.0611
Plastiplate | 2024-01-01 | 4452 | 8491.8061 | 52.43% | Poor
Plastiplate | 2024-02-01 | 6906 | 7375.8449 | 93.63% | Expected
Plastiplate | 2024-03-01 | 6752 | 7831.2021 | 86.22% | Moderate
Plastiplate | 2024-04-01 | 6350 | 6894.3778 | 92.1% | Expected
Plastiplate | 2024-05-01 | 7236 | 6763.5571 | 107% | Expected
Plastiplate | 2024-06-01 | 6002 | 6283.4238 | 95.52% | Expected
Plastiplate | 2024-07-01 | 7142 | 6842.5037 | 104.4% | Expected
Plastiplate | 2024-08-01 | 6654 | 7730.227 | 86.08% | Moderate
Plastiplate | 2024-09-01 | 6375 | 8212.0218 | 77.63% | Moderate
Plastiplate | 2024-10-01 | 6305 | 8639.4997 | 72.98% | Moderate
Plastiplate | 2024-11-01 | 7074 | 8403.5949 | 84.18% | Moderate
Plastiplate | 2024-12-01 | 3371 | 8946.0246 | 37.68% | Poor
Plastiplate | 2025-01-01 | 5083 | 8432.2419 | 60.28% | Poor
Plastiplate | 2025-02-01 | 4977 | 7324.1083 | 67.95% | Poor
Plastiplate | 2025-03-01 | 5306 | 7776.4211 | 68.23% | Poor
Plastiplate | 2025-04-01 | 4700 | 6846.1501 | 68.65% | Poor
Plastiplate | 2025-05-01 | 6568 | 6716.2445 | 97.79% | Expected
Plastiplate | 2025-06-01 | 6255.59 | 6239.4698 | 100.3% | Expected
Plastiplate | 2025-07-01 | 5980 | 6794.6388 | 88.01% | Moderate
Plastiplate | 2025-08-01 | 6685 | 7676.1523 | 87.09% | Moderate
Plastiplate | 2025-09-01 | 7118 | 8154.5768 | 87.29% | Moderate
Plastiplate | 2025-10-01 | 7677 | 8579.0645 | 89.49% | Moderate
Plastiplate | 2025-11-01 | 5691 | 8344.8099 | 68.2% | Poor
Plastiplate | 2025-12-01 | 3680 | 8883.4451 | 41.43% | Poor
Plastiplate | 2026-01-01 | 5605 | 8373.2564 | 66.94% | Poor
Plastiplate | 2026-02-01 | 7388 | 7272.8746 | 101.6% | Expected
Plastiplate | 2026-03-01 | 6319.4 | 7722.0232 | 81.84% | Moderate
Plastiplate | 2026-04-01 | 4370.48 | 6798.2597 | 64.29% | Poor
Plastiplate | 2026-05-01 | 5968.12 | 6669.2629 | 89.49% | Moderate
Plastiplate | 2026-06-01 | 5956 | 6195.8233 | 96.13% | Expected
Opal Students | 2026-07-01 | 3812 | 4134.6782 | 92.2% | Expected | NO
Plastiplate | 2026-08-01 | 6801 | 7622.4559 | 89.22% | Moderate | NO
Checkers Lichtenburg | 2026-09-01 | 18541.7396 | 23596.944 | 78.58% | Moderate | NO
Plastiplate | 2026-10-01 |  | 8519.052
Plastiplate | 2026-11-01 |  | 8286.4361
Plastiplate | 2026-12-01 |  | 8821.3034
Q-lity Meat | 2024-01-01 | 4700 | 4875.5004 | 96.4% | Expected
Q-lity Meat | 2024-02-01 | 4300 | 4507.3806 | 95.4% | Expected
Q-lity Meat | 2024-03-01 | 5200 | 4730.5361 | 109.9% | Expected
Q-lity Meat | 2024-04-01 | 4500 | 4148.3084 | 108.5% | Expected
Q-lity Meat | 2024-05-01 | 4300 | 4092.1586 | 105.1% | Expected
Q-lity Meat | 2024-06-01 | 3800 | 3703.9003 | 102.6% | Expected
Q-lity Meat | 2024-07-01 | 4100 | 4075.4782 | 100.6% | Expected
Q-lity Meat | 2024-08-01 | 4000 | 4588.2407 | 87.18% | Moderate
Q-lity Meat | 2024-09-01 | 3700 | 4756.212 | 77.79% | Moderate
Q-lity Meat | 2024-10-01 | 5479 | 5022.9805 | 109.1% | Expected
Q-lity Meat | 2024-11-01 | 5500 | 4815.8787 | 114.2% | Expected
Q-lity Meat | 2024-12-01 | 2742 | 5030.3638 | 54.51% | Poor
Q-lity Meat | 2025-01-01 | 5100 | 4841.3021 | 105.3% | Expected
Q-lity Meat | 2025-02-01 | 3970 | 4475.7644 | 88.7% | Moderate
Q-lity Meat | 2025-03-01 | 4540 | 4697.445 | 96.65% | Expected
Q-lity Meat | 2025-04-01 | 3526 | 4119.2901 | 85.6% | Moderate
Q-lity Meat | 2025-05-01 | 4309 | 4063.533 | 106% | Expected
Q-lity Meat | 2025-06-01 | 3564 | 3677.9907 | 96.9% | Expected
Q-lity Meat | 2025-07-01 | 3444 | 4046.9693 | 85.1% | Moderate
Q-lity Meat | 2025-08-01 | 4434 | 4556.1449 | 97.32% | Expected
Q-lity Meat | 2025-09-01 | 4300 | 4722.9413 | 91.04% | Expected
Q-lity Meat | 2025-10-01 | 4956 | 4987.8436 | 99.36% | Expected
Q-lity Meat | 2025-11-01 | 4173 | 4782.1905 | 87.26% | Moderate
Q-lity Meat | 2025-12-01 | 5010 | 4995.1753 | 100.3% | Expected
Q-lity Meat | 2026-01-01 | 4573 | 4807.4361 | 95.12% | Expected
Q-lity Meat | 2026-02-01 | 4586.77 | 4444.4554 | 103.2% | Expected
Q-lity Meat | 2026-03-01 | 4089 | 4664.5853 | 87.66% | Moderate
Q-lity Meat | 2026-04-01 | 844.2 | 4090.4747 | 20.64% | Poor
Q-lity Meat | 2026-05-01 | 0 | 4035.1077 | 0% | Poor
Q-lity Meat | 2026-06-01 |  | 3652.2623
Orthochem Bethlehem | 2026-07-01 | 25915.637 | 31778.4827 | 81.55% | Moderate | YES
Q-lity Meat | 2026-08-01 |  | 4524.2736 |  |  | NO
Q-lity Meat | 2026-09-01 | 0 | 4689.9032 | 0% | Poor | NO
Q-lity Meat | 2026-10-01 |  | 4952.9525
Q-lity Meat | 2026-11-01 |  | 4748.738
Q-lity Meat | 2026-12-01 |  | 4960.2329
Quintondale | 2024-01-01 | 6159 | 5831.4971 | 105.6% | Expected
Quintondale | 2024-02-01 | 4495 | 5232.3605 | 85.91% | Moderate
Quintondale | 2024-03-01 | 5040 | 5626.8025 | 89.57% | Moderate
Quintondale | 2024-04-01 | 4485 | 5015.9594 | 89.41% | Moderate
Quintondale | 2024-05-01 | 4861 | 5130.0762 | 94.75% | Expected
Quintondale | 2024-06-01 | 3929 | 4752.4374 | 82.67% | Moderate
Quintondale | 2024-07-01 | 4619 | 5221.086 | 88.47% | Moderate
Quintondale | 2024-08-01 | 5354 | 5739.3819 | 93.29% | Expected
Quintondale | 2024-09-01 | 4908 | 5921.5488 | 82.88% | Moderate
Quintondale | 2024-10-01 | 6335 | 6023.3893 | 105.2% | Expected
Quintondale | 2024-11-01 | 5824 | 5823.0258 | 100% | Expected
Quintondale | 2024-12-01 | 6091 | 6073.0456 | 100.3% | Expected
Quintondale | 2025-01-01 | 5309 | 5790.5931 | 91.68% | Expected
Quintondale | 2025-02-01 | 3761 | 5195.659 | 72.39% | Moderate
Quintondale | 2025-03-01 | 4074 | 5587.4418 | 72.91% | Moderate
Quintondale | 2025-04-01 | 3902 | 4980.8717 | 78.34% | Moderate
Quintondale | 2025-05-01 | 5047 | 5094.1901 | 99.07% | Expected
Quintondale | 2025-06-01 | 4585.36 | 4719.193 | 97.16% | Expected
Quintondale | 2025-07-01 | 4750 | 5184.5634 | 91.62% | Expected
Quintondale | 2025-08-01 | 4940 | 5699.2337 | 86.68% | Moderate
Quintondale | 2025-09-01 | 4923 | 5880.1262 | 83.72% | Moderate
Quintondale | 2025-10-01 | 5673 | 5981.2543 | 94.85% | Expected
Quintondale | 2025-11-01 | 4641 | 5782.2924 | 80.26% | Moderate
Quintondale | 2025-12-01 | 5262 | 6030.5633 | 87.26% | Moderate
Quintondale | 2026-01-01 | 5546 | 5750.0866 | 96.45% | Expected
Quintondale | 2026-02-01 | 5201.23 | 5159.3142 | 100.8% | Expected
Quintondale | 2026-03-01 | 4579 | 5548.3564 | 82.53% | Moderate
Quintondale | 2026-04-01 | 4134.11 | 4946.0293 | 83.58% | Moderate
Quintondale | 2026-05-01 | 4665.67 | 5058.5551 | 92.23% | Expected
Quintondale | 2026-06-01 | 3785 | 4686.1812 | 80.77% | Moderate
Plastiplate | 2026-07-01 | 6917 | 6747.1088 | 102.5% | Expected | NO
Quintondale | 2026-08-01 | 5246 | 5659.3662 | 92.7% | Expected | NO
Checkers De Aar | 2026-09-01 | 15296.73 | 19202.4916 | 79.66% | Moderate | NO
Quintondale | 2026-10-01 |  | 5939.4141
Quintondale | 2026-11-01 |  | 5741.844
Quintondale | 2026-12-01 |  | 5988.3781
Riverside Lodge | 2024-01-01 | 6600 | 17022.6691 | 38.77% | Poor
Riverside Lodge | 2024-02-01 | 13300 | 14954.9863 | 88.93% | Moderate
Riverside Lodge | 2024-03-01 | 15420 | 16197.5546 | 95.2% | Expected
Riverside Lodge | 2024-04-01 | 12860 | 14161.4564 | 90.81% | Expected
Riverside Lodge | 2024-05-01 | 14610 | 14682.6117 | 99.51% | Expected
Riverside Lodge | 2024-06-01 | 12010 | 13768.5562 | 87.23% | Moderate
Riverside Lodge | 2024-07-01 | 13050 | 14990.0388 | 87.06% | Moderate
Riverside Lodge | 2024-08-01 | 17380 | 16620.2025 | 104.6% | Expected
Riverside Lodge | 2024-09-01 | 15040 | 16780.4253 | 89.63% | Moderate
Riverside Lodge | 2024-10-01 | 16040 | 17412.9907 | 92.12% | Expected
Riverside Lodge | 2024-11-01 | 12800 | 16425.9392 | 77.93% | Moderate
Riverside Lodge | 2024-12-01 | 11928 | 17538.0238 | 68.01% | Poor
Riverside Lodge | 2025-01-01 | 11300 | 16903.2666 | 66.85% | Poor
Riverside Lodge | 2025-02-01 | 8382 | 14850.0872 | 56.44% | Poor
Riverside Lodge | 2025-03-01 | 11945 | 16084.249 | 74.27% | Moderate
Riverside Lodge | 2025-04-01 | 13271 | 14062.3938 | 94.37% | Expected
Riverside Lodge | 2025-05-01 | 17380 | 14579.9035 | 119.2% | Expected
Riverside Lodge | 2025-06-01 | 15760.44 | 13672.2421 | 115.3% | Expected
Riverside Lodge | 2025-07-01 | 15336 | 14885.1801 | 103% | Expected
Riverside Lodge | 2025-08-01 | 18373 | 16503.9405 | 111.3% | Expected
Riverside Lodge | 2025-09-01 | 14826 | 16663.0424 | 88.98% | Moderate
Riverside Lodge | 2025-10-01 | 14653 | 17291.1829 | 84.74% | Moderate
Riverside Lodge | 2025-11-01 | 11613 | 16311.0361 | 71.2% | Moderate
Riverside Lodge | 2025-12-01 | 12623 | 17415.3414 | 72.48% | Moderate
Riverside Lodge | 2026-01-01 | 13947 | 16785.0244 | 83.09% | Moderate
Riverside Lodge | 2026-02-01 | 15878 | 14746.2075 | 107.7% | Expected
Riverside Lodge | 2026-03-01 | 15307 | 15971.7361 | 95.84% | Expected
Riverside Lodge | 2026-04-01 | 13475.98 | 13964.0242 | 96.5% | Expected
Riverside Lodge | 2026-05-01 | 16989.47 | 14477.9138 | 117.3% | Expected
Riverside Lodge | 2026-06-01 | 13699 | 13576.6016 | 100.9% | Expected
PNB Unlimited | 2026-07-01 | 6388 | 8160.1901 | 78.28% | Moderate | NO
Riverside Lodge | 2026-08-01 | 18348 | 16388.4917 | 112% | Expected | NO
Riverside Lodge | 2026-09-01 | 16094 | 16546.4807 | 97.27% | Expected | NO
Riverside Lodge | 2026-10-01 |  | 17170.2272
Riverside Lodge | 2026-11-01 |  | 16196.9367
Riverside Lodge | 2026-12-01 |  | 17293.5172
Roan Foods | 2024-01-01 |  | 20178
Roan Foods | 2024-02-01 |  | 17954
Roan Foods | 2024-03-01 |  | 19150
Roan Foods | 2024-04-01 |  | 18060
Roan Foods | 2024-05-01 |  | 18124
Roan Foods | 2024-06-01 |  | 15908
Roan Foods | 2024-07-01 |  | 16827
Roan Foods | 2024-08-01 |  | 19405
Roan Foods | 2024-09-01 |  | 19981
Roan Foods | 2024-10-01 |  | 22401
Roan Foods | 2024-11-01 |  | 20125
Roan Foods | 2024-12-01 |  | 20771
Roan Foods | 2025-01-01 |  | 20178
Roan Foods | 2025-02-01 |  | 17954
Roan Foods | 2025-03-01 |  | 19150
Roan Foods | 2025-04-01 |  | 18060
Roan Foods | 2025-05-01 |  | 18124
Roan Foods | 2025-06-01 |  | 15908
Roan Foods | 2025-07-01 |  | 16827
Roan Foods | 2025-08-01 |  | 19405
Roan Foods | 2025-09-01 |  | 19981
Roan Foods | 2025-10-01 |  | 22401
Roan Foods | 2025-11-01 |  | 20125
Roan Foods | 2025-12-01 |  | 20771
Roan Foods | 2026-01-01 |  | 20178
Roan Foods | 2026-02-01 |  | 17954
Roan Foods | 2026-03-01 |  | 19150
Roan Foods | 2026-04-01 | 10820 | 18060 | 59.91% | Poor
Roan Foods | 2026-05-01 | 11820 | 18113.8944 | 65.25% | Poor
Roan Foods | 2026-06-01 | 10720 | 15889.6537 | 67.47% | Poor
Q-lity Meat | 2026-07-01 | 0 | 4018.6598 | 0% | Poor | NO
Roan Foods | 2026-08-01 | 9230 | 19359.8949 | 47.68% | Poor | NO
Roan Foods | 2026-09-01 | 11370 | 19922.6745 | 57.07% | Poor | NO
Roan Foods | 2026-10-01 |  | 22322.7271
Roan Foods | 2026-11-01 |  | 20042.7268
Roan Foods | 2026-12-01 |  | 20674.154
SR Morula TF 1 | 2024-01-01 |  | 9307.8
SR Morula TF 1 | 2024-02-01 |  | 8001.9
SR Morula TF 1 | 2024-03-01 |  | 7803.9
SR Morula TF 1 | 2024-04-01 |  | 6785.1
SR Morula TF 1 | 2024-05-01 |  | 6244.2
SR Morula TF 1 | 2024-06-01 |  | 5524.2
SR Morula TF 1 | 2024-07-01 |  | 6086.7
SR Morula TF 1 | 2024-08-01 |  | 2298.1935
SR Morula TF 1 | 2024-09-01 |  | 7864.2
SR Morula TF 1 | 2024-10-01 |  | 9007.2
SR Morula TF 1 | 2024-11-01 |  | 8999.1
SR Morula TF 1 | 2024-12-01 |  | 9241.2
SR Morula TF 1 | 2025-01-01 |  | 9307.8
SR Morula TF 1 | 2025-02-01 |  | 8001.9
SR Morula TF 1 | 2025-03-01 |  | 7803.9
SR Morula TF 1 | 2025-04-01 |  | 6785.1
SR Morula TF 1 | 2025-05-01 |  | 6244.2
SR Morula TF 1 | 2025-06-01 |  | 5524.2
SR Morula TF 1 | 2025-07-01 |  | 6086.7
SR Morula TF 1 | 2025-08-01 | 2845 | 2298.1935 | 123.8% | Expected
SR Morula TF 1 | 2025-09-01 | 7367 | 7862.3852 | 93.7% | Expected
SR Morula TF 1 | 2025-10-01 | 8824 | 8999.9273 | 98.05% | Expected
SR Morula TF 1 | 2025-11-01 | 7686 | 8986.4745 | 85.53% | Moderate
SR Morula TF 1 | 2025-12-01 | 9330 | 9222.9119 | 101.2% | Expected
SR Morula TF 1 | 2026-01-01 | 9387 | 9283.8434 | 101.1% | Expected
SR Morula TF 1 | 2026-02-01 | 8600 | 7976.5475 | 107.8% | Expected
SR Morula TF 1 | 2026-03-01 | 6749 | 7774.9868 | 86.8% | Moderate
SR Morula TF 1 | 2026-04-01 | 6091.51 | 6755.9324 | 90.17% | Expected
SR Morula TF 1 | 2026-05-01 | 6169.97 | 6213.7714 | 99.3% | Expected
SR Morula TF 1 | 2026-06-01 | 4726 | 5494.0035 | 86.02% | Moderate
Quintondale | 2026-07-01 | 4628 | 5148.2962 | 89.89% | Moderate | NO
SR Morula TF 1 | 2026-08-01 | 6659 | 7076.7515 | 94.1% | Expected | NO
Huis Herfsblaar | 2026-09-01 | 23016.89 | 28398.5212 | 81.05% | Moderate | NO
SR Morula TF 1 | 2026-10-01 |  | 8936.9708
SR Morula TF 1 | 2026-11-01 |  | 8923.6121
SR Morula TF 1 | 2026-12-01 |  | 9158.3956
SR Morula TF 1 - Shoprite | 2024-01-01 |  | 28699.56
SR Morula TF 1 - Shoprite | 2024-02-01 |  | 24909.3
SR Morula TF 1 - Shoprite | 2024-03-01 |  | 24570
SR Morula TF 1 - Shoprite | 2024-04-01 |  | 21388.5
SR Morula TF 1 - Shoprite | 2024-05-01 |  | 19723.5
SR Morula TF 1 - Shoprite | 2024-06-01 |  | 17431.2
SR Morula TF 1 - Shoprite | 2024-07-01 |  | 19181.7
SR Morula TF 1 - Shoprite | 2024-08-01 |  | 7231.3548
SR Morula TF 1 - Shoprite | 2024-09-01 |  | 24780.6
SR Morula TF 1 - Shoprite | 2024-10-01 |  | 28127.7
SR Morula TF 1 - Shoprite | 2024-11-01 |  | 28061.1
SR Morula TF 1 - Shoprite | 2024-12-01 |  | 28703.7
SR Morula TF 1 - Shoprite | 2025-01-01 |  | 28699.56
SR Morula TF 1 - Shoprite | 2025-02-01 |  | 24909.3
SR Morula TF 1 - Shoprite | 2025-03-01 |  | 24570
SR Morula TF 1 - Shoprite | 2025-04-01 |  | 21388.5
SR Morula TF 1 - Shoprite | 2025-05-01 |  | 19723.5
SR Morula TF 1 - Shoprite | 2025-06-01 |  | 17431.2
SR Morula TF 1 - Shoprite | 2025-07-01 |  | 19181.7
SR Morula TF 1 - Shoprite | 2025-08-01 | 8229 | 7231.3548 | 113.8% | Expected
SR Morula TF 1 - Shoprite | 2025-09-01 | 21334 | 24774.8816 | 86.11% | Moderate
SR Morula TF 1 - Shoprite | 2025-10-01 | 26578 | 28104.9888 | 94.57% | Expected
SR Morula TF 1 - Shoprite | 2025-11-01 | 22629 | 28021.7309 | 80.76% | Moderate
SR Morula TF 1 - Shoprite | 2025-12-01 | 27791 | 28646.8962 | 97.01% | Expected
SR Morula TF 1 - Shoprite | 2026-01-01 | 27879 | 28625.6926 | 97.39% | Expected
SR Morula TF 1 - Shoprite | 2026-02-01 | 25500 | 24830.3797 | 102.7% | Expected
SR Morula TF 1 - Shoprite | 2026-03-01 | 20753 | 24478.9691 | 84.78% | Moderate
SR Morula TF 1 - Shoprite | 2026-04-01 | 18061.39 | 21296.5556 | 84.81% | Moderate
SR Morula TF 1 - Shoprite | 2026-05-01 | 18908.48 | 19627.3853 | 96.34% | Expected
SR Morula TF 1 - Shoprite | 2026-06-01 | 14035.5 | 17335.9171 | 80.96% | Moderate
Riverside Lodge | 2026-07-01 | 16691 | 14781.0549 | 112.9% | Expected | NO
SR Morula TF 1 - Shoprite | 2026-08-01 | 20112.53 | 22268.3237 | 90.32% | Expected | YES
SR Morula TF 2 | 2026-09-01 | 6579.8013 | 8095.0925 | 81.28% | Moderate | NO
SR Morula TF 1 - Shoprite | 2026-10-01 |  | 27908.388
SR Morula TF 1 - Shoprite | 2026-11-01 |  | 27825.7126
SR Morula TF 1 - Shoprite | 2026-12-01 |  | 28446.5047
SR Morula TF 2 | 2024-01-01 |  | 9601.92
SR Morula TF 2 | 2024-02-01 |  | 8296.74
SR Morula TF 2 | 2024-03-01 |  | 8140.5
SR Morula TF 2 | 2024-04-01 |  | 7017.3
SR Morula TF 2 | 2024-05-01 |  | 6430.32
SR Morula TF 2 | 2024-06-01 |  | 5669.28
SR Morula TF 2 | 2024-07-01 |  | 6247.44
SR Morula TF 2 | 2024-08-01 |  | 2367.7839
SR Morula TF 2 | 2024-09-01 |  | 8154
SR Morula TF 2 | 2024-10-01 |  | 9352.8
SR Morula TF 2 | 2024-11-01 |  | 9353.7
SR Morula TF 2 | 2024-12-01 |  | 9582.3
SR Morula TF 2 | 2025-01-01 |  | 9601.92
SR Morula TF 2 | 2025-02-01 |  | 8296.74
SR Morula TF 2 | 2025-03-01 |  | 8140.5
SR Morula TF 2 | 2025-04-01 |  | 7017.3
SR Morula TF 2 | 2025-05-01 |  | 6430.32
SR Morula TF 2 | 2025-06-01 |  | 5669.28
SR Morula TF 2 | 2025-07-01 |  | 6247.44
SR Morula TF 2 | 2025-08-01 | 2512 | 2367.7839 | 106.1% | Expected
SR Morula TF 2 | 2025-09-01 | 7570 | 8152.1184 | 92.86% | Expected
SR Morula TF 2 | 2025-10-01 | 8856 | 9345.2482 | 94.76% | Expected
SR Morula TF 2 | 2025-11-01 | 7508 | 9340.577 | 80.38% | Moderate
SR Morula TF 2 | 2025-12-01 | 9313 | 9563.3369 | 97.38% | Expected
SR Morula TF 2 | 2026-01-01 | 9484 | 9577.2064 | 99.03% | Expected
SR Morula TF 2 | 2026-02-01 | 8425.8 | 8270.4534 | 101.9% | Expected
SR Morula TF 2 | 2026-03-01 | 7083 | 8110.3398 | 87.33% | Moderate
SR Morula TF 2 | 2026-04-01 | 6207.8 | 6987.1342 | 88.85% | Moderate
SR Morula TF 2 | 2026-05-01 | 6478.04 | 6398.9844 | 101.2% | Expected
SR Morula TF 2 | 2026-06-01 | 4827 | 5638.2904 | 85.61% | Moderate
Roan Foods | 2026-07-01 | 10570 | 16797.8991 | 62.92% | Poor | NO
SR Morula TF 2 | 2026-08-01 | 2900 | 7291.3189 | 39.77% | Poor | YES
SR Morula TF 1 - Shoprite | 2026-09-01 | 20045.69 | 24601.5757 | 81.48% | Moderate | NO
SR Morula TF 2 | 2026-10-01 |  | 9279.8761
SR Morula TF 2 | 2026-11-01 |  | 9275.2375
SR Morula TF 2 | 2026-12-01 |  | 9496.4392
Sakhumnotho | 2024-01-01 | 1720 | 5191.479 | 33.13% | Poor
Sakhumnotho | 2024-02-01 | 1864 | 4656.5573 | 40.03% | Poor
Sakhumnotho | 2024-03-01 | 2167 | 5018.2719 | 43.18% | Poor
Sakhumnotho | 2024-04-01 | 1409 | 4498.5661 | 31.32% | Poor
Sakhumnotho | 2024-05-01 | 1672 | 4604.0626 | 36.32% | Poor
Sakhumnotho | 2024-06-01 | 1125 | 4265.4254 | 26.37% | Poor
Sakhumnotho | 2024-07-01 | 2628 | 4694.8505 | 55.98% | Poor
Sakhumnotho | 2024-08-01 | 794 | 5144.2253 | 15.43% | Poor
Sakhumnotho | 2024-09-01 | 1822 | 5295.0313 | 34.41% | Poor
Sakhumnotho | 2024-10-01 | 2044 | 5391.4829 | 37.91% | Poor
Sakhumnotho | 2024-11-01 | 1984 | 5210.6678 | 38.08% | Poor
Sakhumnotho | 2024-12-01 | 1687 | 5439.6664 | 31.01% | Poor
Sakhumnotho | 2025-01-01 | 2354 | 5191.479 | 45.34% | Poor
Sakhumnotho | 2025-02-01 | 1728 | 4656.5573 | 37.11% | Poor
Sakhumnotho | 2025-03-01 | 1704 | 5018.2719 | 33.96% | Poor
Sakhumnotho | 2025-04-01 | 1518 | 4498.5661 | 33.74% | Poor
Sakhumnotho | 2025-05-01 | 2450 | 4604.0626 | 53.21% | Poor
Sakhumnotho | 2025-06-01 | 2470.27 | 4265.4254 | 57.91% | Poor
Sakhumnotho | 2025-07-01 | 2714 | 4694.8505 | 57.81% | Poor
Sakhumnotho | 2025-08-01 | 2694 | 5144.2253 | 52.37% | Poor
Sakhumnotho | 2025-09-01 | 1488 | 5295.0313 | 28.1% | Poor
Sakhumnotho | 2025-10-01 | 380 | 5391.4829 | 7.048% | Poor
Sakhumnotho | 2025-11-01 |  | 5210.6678
Sakhumnotho | 2025-12-01 |  | 5439.6664
Sakhumnotho | 2026-01-01 |  | 5191.479
Sakhumnotho | 2026-02-01 |  | 4656.5573
Sakhumnotho | 2026-03-01 |  | 5018.2719
Sakhumnotho | 2026-04-01 |  | 4498.5661
Sakhumnotho | 2026-05-01 |  | 4604.0626
Sakhumnotho | 2026-06-01 |  | 4265.4254
Sakhumnotho | 2026-07-01 | 0 | 4694.8505 | 0% | Poor | NO
Sakhumnotho | 2026-08-01 |  | 5144.2253 |  |  | NO
Sakhumnotho | 2026-09-01 |  | 5295.0313 |  |  | NO
Sakhumnotho | 2026-10-01 |  | 5391.4829
Sakhumnotho | 2026-11-01 |  | 5210.6678
Sakhumnotho | 2026-12-01 |  | 5439.6664
SaveMore Alldays - Store | 2024-01-01 | 17948 | 22925.4139 | 78.29% | Moderate
SaveMore Alldays - Store | 2024-02-01 | 16954 | 19806.8948 | 85.6% | Moderate
SaveMore Alldays - Store | 2024-03-01 | 16498 | 21850.8641 | 75.5% | Moderate
SaveMore Alldays - Store | 2024-04-01 | 13514 | 21332.0032 | 63.35% | Poor
SaveMore Alldays - Store | 2024-05-01 | 13524 | 20568.0916 | 65.75% | Poor
SaveMore Alldays - Store | 2024-06-01 | 11348 | 18526.8081 | 61.25% | Poor
SaveMore Alldays - Store | 2024-07-01 | 12215 | 19492.9593 | 62.66% | Poor
SaveMore Alldays - Store | 2024-08-01 | 12637 | 22824.5467 | 55.37% | Poor
SaveMore Alldays - Store | 2024-09-01 | 12990 | 22485.1231 | 57.77% | Poor
SaveMore Alldays - Store | 2024-10-01 | 10518 | 21853.0074 | 48.13% | Poor
SaveMore Alldays - Store | 2024-11-01 | 5878 | 21856.923 | 26.89% | Poor
SaveMore Alldays - Store | 2024-12-01 | 17496 | 23102.5427 | 75.73% | Moderate
SaveMore Alldays - Store | 2025-01-01 | 16026 | 22764.6076 | 70.4% | Moderate
SaveMore Alldays - Store | 2025-02-01 | 13689 | 19667.9629 | 69.6% | Poor
SaveMore Alldays - Store | 2025-03-01 | 11995 | 21698.0123 | 55.28% | Poor
SaveMore Alldays - Store | 2025-04-01 | 6680 | 21182.7811 | 31.54% | Poor
SaveMore Alldays - Store | 2025-05-01 | 11933 | 20424.2131 | 58.43% | Poor
SaveMore Alldays - Store | 2025-06-01 | 9797.26 | 18397.2089 | 53.25% | Poor
SaveMore Alldays - Store | 2025-07-01 | 9134.4 | 19356.6017 | 47.19% | Poor
SaveMore Alldays - Store | 2025-08-01 | 15551 | 22664.8839 | 68.61% | Poor
SaveMore Alldays - Store | 2025-09-01 | 14894 | 22327.8346 | 66.71% | Poor
SaveMore Alldays - Store | 2025-10-01 | 17167 | 21700.1407 | 79.11% | Moderate
SaveMore Alldays - Store | 2025-11-01 | 14437 | 21704.0289 | 66.52% | Poor
SaveMore Alldays - Store | 2025-12-01 | 14721 | 22940.9352 | 64.17% | Poor
SaveMore Alldays - Store | 2026-01-01 | 16129 | 22605.364 | 71.35% | Moderate
SaveMore Alldays - Store | 2026-02-01 | 15901 | 19530.381 | 81.42% | Moderate
SaveMore Alldays - Store | 2026-03-01 | 13942 | 21546.2298 | 64.71% | Poor
SaveMore Alldays - Store | 2026-04-01 | 12240.56 | 21034.6027 | 58.19% | Poor
SaveMore Alldays - Store | 2026-05-01 | 12352.61 | 20281.3411 | 60.91% | Poor
SaveMore Alldays - Store | 2026-06-01 | 11089 | 18268.5162 | 60.7% | Poor
SaveMore Alldays - Store | 2026-07-01 | 12059 | 19221.1979 | 62.74% | Poor | NO
SaveMore Alldays - Store | 2026-08-01 | 13852 | 22506.3379 | 61.55% | Poor | NO
SaveMore Alldays - Store | 2026-09-01 | 13027.93 | 22171.6464 | 58.76% | Poor | NO
SaveMore Alldays - Store | 2026-10-01 |  | 21548.3433
SaveMore Alldays - Store | 2026-11-01 |  | 21552.2043
SaveMore Alldays - Store | 2026-12-01 |  | 22780.4582
Savemore Liquor Alldays | 2024-01-01 | 1424 | 3296.9581 | 43.19% | Poor
Savemore Liquor Alldays | 2024-02-01 | 1471 | 2844.9716 | 51.71% | Poor
Savemore Liquor Alldays | 2024-03-01 | 1705 | 3141.0325 | 54.28% | Poor
Savemore Liquor Alldays | 2024-04-01 | 1306 | 3065.7654 | 42.6% | Poor
Savemore Liquor Alldays | 2024-05-01 | 856 | 2955.6581 | 28.96% | Poor
Savemore Liquor Alldays | 2024-06-01 | 1086 | 2661.5895 | 40.8% | Poor
Savemore Liquor Alldays | 2024-07-01 | 1232 | 2799.413 | 44.01% | Poor
Savemore Liquor Alldays | 2024-08-01 | 1007 | 3279.4306 | 30.71% | Poor
Savemore Liquor Alldays | 2024-09-01 | 1218 | 3229.2517 | 37.72% | Poor
Savemore Liquor Alldays | 2024-10-01 | 1389 | 3142.6241 | 44.2% | Poor
Savemore Liquor Alldays | 2024-11-01 | 1731 | 3143.6141 | 55.06% | Poor
Savemore Liquor Alldays | 2024-12-01 | 1418 | 3321.0631 | 42.7% | Poor
Savemore Liquor Alldays | 2025-01-01 | 1493 | 3273.8322 | 45.6% | Poor
Savemore Liquor Alldays | 2025-02-01 | 1368.9 | 2825.0161 | 48.46% | Poor
Savemore Liquor Alldays | 2025-03-01 | 960 | 3119.0603 | 30.78% | Poor
Savemore Liquor Alldays | 2025-04-01 | 694 | 3044.3196 | 22.8% | Poor
Savemore Liquor Alldays | 2025-05-01 | 580 | 2934.9826 | 19.76% | Poor
Savemore Liquor Alldays | 2025-06-01 | 449.2 | 2642.9711 | 17% | Poor
Savemore Liquor Alldays | 2025-07-01 | 575 | 2779.8304 | 20.68% | Poor
Savemore Liquor Alldays | 2025-08-01 | 1437 | 3256.4902 | 44.13% | Poor
Savemore Liquor Alldays | 2025-09-01 | 1257 | 3206.6624 | 39.2% | Poor
Savemore Liquor Alldays | 2025-10-01 | 1616 | 3120.6407 | 51.78% | Poor
Savemore Liquor Alldays | 2025-11-01 | 1463 | 3121.6238 | 46.87% | Poor
Savemore Liquor Alldays | 2025-12-01 | 1836 | 3297.8315 | 55.67% | Poor
Savemore Liquor Alldays | 2026-01-01 | 1637 | 3250.931 | 50.35% | Poor
Savemore Liquor Alldays | 2026-02-01 | 1801 | 2805.2545 | 64.2% | Poor
Savemore Liquor Alldays | 2026-03-01 | 1516 | 3097.2418 | 48.95% | Poor
Savemore Liquor Alldays | 2026-04-01 | 1353.29 | 3023.0239 | 44.77% | Poor
Savemore Liquor Alldays | 2026-05-01 | 1302.09 | 2914.4517 | 44.68% | Poor
Savemore Liquor Alldays | 2026-06-01 | 1100 | 2624.4829 | 41.91% | Poor
Savemore Liquor Alldays | 2026-07-01 | 1098 | 2760.3849 | 39.78% | Poor | NO
Savemore Liquor Alldays | 2026-08-01 | 1071 | 3233.7103 | 33.12% | Poor | NO
Savemore Liquor Alldays | 2026-09-01 | 1290.91 | 3184.2311 | 40.54% | Poor | NO
Savemore Liquor Alldays | 2026-10-01 |  | 3098.8112
Savemore Liquor Alldays | 2026-11-01 |  | 3099.7874
Savemore Liquor Alldays | 2026-12-01 |  | 3274.7624
Saverite Durban | 2024-01-01 | 8341 | 12446.1538 | 67.02% | Poor
Saverite Durban | 2024-02-01 | 8056 | 10833.4291 | 74.36% | Moderate
Saverite Durban | 2024-03-01 | 7588 | 10846.9627 | 69.96% | Poor
Saverite Durban | 2024-04-01 | 6746 | 8712.26 | 77.43% | Moderate
Saverite Durban | 2024-05-01 | 6595 | 7406.2829 | 89.05% | Moderate
Saverite Durban | 2024-06-01 | 5221 | 6709.5864 | 77.81% | Moderate
Saverite Durban | 2024-07-01 | 6498 | 7223.6379 | 89.95% | Moderate
Saverite Durban | 2024-08-01 | 6727 | 8504.0306 | 79.1% | Moderate
Saverite Durban | 2024-09-01 | 5408 | 9121.1406 | 59.29% | Poor
Saverite Durban | 2024-10-01 | 8018 | 10659.8345 | 75.22% | Moderate
Saverite Durban | 2024-11-01 | 7818 | 11055.4511 | 70.72% | Moderate
Saverite Durban | 2024-12-01 | 9041 | 12562.5302 | 71.97% | Moderate
Saverite Durban | 2025-01-01 | 9601 | 12358.8524 | 77.69% | Moderate
Saverite Durban | 2025-02-01 | 7317 | 10757.44 | 68.02% | Poor
Saverite Durban | 2025-03-01 | 8211 | 10771.0857 | 76.23% | Moderate
Saverite Durban | 2025-04-01 | 6924 | 8651.3158 | 80.03% | Moderate
Saverite Durban | 2025-05-01 | 7428 | 7354.4743 | 101% | Expected
Saverite Durban | 2025-06-01 | 7026.25 | 6662.6513 | 105.5% | Expected
Saverite Durban | 2025-07-01 | 7318 | 7173.1069 | 102% | Expected
Saverite Durban | 2025-08-01 | 7873 | 8444.5429 | 93.23% | Expected
Saverite Durban | 2025-09-01 | 6985 | 9057.3361 | 77.12% | Moderate
Saverite Durban | 2025-10-01 | 9680.31 | 10585.2665 | 91.45% | Expected
Saverite Durban | 2025-11-01 | 11102 | 10978.1158 | 101.1% | Expected
Saverite Durban | 2025-12-01 | 11384 | 12474.6524 | 91.26% | Expected
Saverite Durban | 2026-01-01 | 12215 | 12272.3995 | 99.53% | Expected
Saverite Durban | 2026-02-01 | 11691 | 10682.1893 | 109.4% | Expected
Saverite Durban | 2026-03-01 | 10159 | 10695.7396 | 94.98% | Expected
Saverite Durban | 2026-04-01 | 8032.01 | 8590.7979 | 93.5% | Expected
Saverite Durban | 2026-05-01 | 7738.42 | 7303.0281 | 106% | Expected
Saverite Durban | 2026-06-01 | 6442 | 6616.0446 | 97.37% | Expected
Saverite Durban | 2026-07-01 | 6823 | 7122.9294 | 95.79% | Expected | NO
Saverite Durban | 2026-08-01 | 8202 | 8385.4715 | 97.81% | Expected | NO
Watt Place Rotoflo | 2026-09-01 | 19614.48 | 23964.006 | 81.85% | Moderate | NO
Saverite Durban | 2026-10-01 |  | 10511.2202
Saverite Durban | 2026-11-01 |  | 10901.3214
Saverite Durban | 2026-12-01 |  | 12387.3894
Saverite PMB | 2024-01-01 | 11804 | 12933.1065 | 91.27% | Expected
Saverite PMB | 2024-02-01 | 9158 | 10723.3696 | 85.4% | Moderate
Saverite PMB | 2024-03-01 | 9784 | 11181.616 | 87.5% | Moderate
Saverite PMB | 2024-04-01 | 7858 | 9771.3205 | 80.42% | Moderate
Saverite PMB | 2024-05-01 | 7246 | 8765.6166 | 82.66% | Moderate
Saverite PMB | 2024-06-01 | 6127 | 7609.8503 | 80.51% | Moderate
Saverite PMB | 2024-07-01 | 8521 | 8420.0274 | 101.2% | Expected
Saverite PMB | 2024-08-01 | 9050 | 9578.7354 | 94.48% | Expected
Saverite PMB | 2024-09-01 | 8302 | 10292.7171 | 80.66% | Moderate
Saverite PMB | 2024-10-01 | 11290 | 11296.4847 | 99.94% | Expected
Saverite PMB | 2024-11-01 | 10513 | 12142.7761 | 86.58% | Moderate
Saverite PMB | 2024-12-01 | 11507 | 13020.7212 | 88.37% | Moderate
Saverite PMB | 2025-01-01 | 11679 | 12842.3895 | 90.94% | Expected
Saverite PMB | 2025-02-01 | 7567 | 10648.1524 | 71.06% | Moderate
Saverite PMB | 2025-03-01 | 9564 | 11103.3981 | 86.14% | Moderate
Saverite PMB | 2025-04-01 | 6957 | 9702.9679 | 71.7% | Moderate
Saverite PMB | 2025-05-01 | 7705 | 8704.2991 | 88.52% | Moderate
Saverite PMB | 2025-06-01 | 6515.6 | 7556.6177 | 86.22% | Moderate
Saverite PMB | 2025-07-01 | 7651 | 8361.1274 | 91.51% | Expected
Saverite PMB | 2025-08-01 | 8548 | 9511.73 | 89.87% | Moderate
Saverite PMB | 2025-09-01 | 7542 | 10220.7172 | 73.79% | Moderate
Saverite PMB | 2025-10-01 | 10186 | 11217.4632 | 90.8% | Expected
Saverite PMB | 2025-11-01 | 10802 | 12057.8346 | 89.58% | Moderate
Saverite PMB | 2025-12-01 | 11033 | 12929.6383 | 85.33% | Moderate
Saverite PMB | 2026-01-01 | 7790 | 12752.5541 | 61.09% | Poor
Saverite PMB | 2026-02-01 | 5171.0647 | 10573.6662 | 48.91% | Poor
Saverite PMB | 2026-03-01 | 8153.5 | 11025.7273 | 73.95% | Moderate
Saverite PMB | 2026-04-01 | 7873.17 | 9635.0935 | 81.71% | Moderate
Saverite PMB | 2026-05-01 | 7767.8 | 8643.4106 | 89.87% | Moderate
Saverite PMB | 2026-06-01 | 7190.68 | 7503.7574 | 95.83% | Expected
Saverite PMB | 2026-07-01 | 6825.8941 | 8302.6394 | 82.21% | Moderate | NO
Saverite PMB | 2026-08-01 | 9679.5108 | 9445.1933 | 102.5% | Expected | NO
Saverite PMB | 2026-09-01 | 8602.5566 | 10149.221 | 84.76% | Moderate | NO
Saverite PMB | 2026-10-01 |  | 11138.9945
Saverite PMB | 2026-11-01 |  | 11973.4874
Saverite PMB | 2026-12-01 |  | 12839.1926
Secunda Plaza Shops | 2024-01-01 | 4297 | 4316.0517 | 99.56% | Expected
Secunda Plaza Shops | 2024-02-01 | 4176 | 3785.4253 | 110.3% | Expected
Secunda Plaza Shops | 2024-03-01 | 4682 | 4031.6197 | 116.1% | Expected
Secunda Plaza Shops | 2024-04-01 | 3965 | 3532.0132 | 112.3% | Expected
Secunda Plaza Shops | 2024-05-01 | 3760 | 3578.8675 | 105.1% | Expected
Secunda Plaza Shops | 2024-06-01 | 3240 | 3317.319 | 97.67% | Expected
Secunda Plaza Shops | 2024-07-01 | 3836 | 3616.4025 | 106.1% | Expected
Secunda Plaza Shops | 2024-08-01 | 3915 | 4046.3949 | 96.75% | Expected
Secunda Plaza Shops | 2024-09-01 | 3746 | 4211.5956 | 88.94% | Moderate
Secunda Plaza Shops | 2024-10-01 | 3449 | 4224.2339 | 81.65% | Moderate
Secunda Plaza Shops | 2024-11-01 | 4630 | 4182.741 | 110.7% | Expected
Secunda Plaza Shops | 2024-12-01 | 5059 | 4373.3211 | 115.7% | Expected
Secunda Plaza Shops | 2025-01-01 | 4475 | 4285.7775 | 104.4% | Expected
Secunda Plaza Shops | 2025-02-01 | 3651 | 3758.8731 | 97.13% | Expected
Secunda Plaza Shops | 2025-03-01 | 3912 | 4003.4176 | 97.72% | Expected
Secunda Plaza Shops | 2025-04-01 | 3361 | 3507.3059 | 95.83% | Expected
Secunda Plaza Shops | 2025-05-01 | 3626 | 3553.8325 | 102% | Expected
Secunda Plaza Shops | 2025-06-01 | 3199.19 | 3294.1136 | 97.12% | Expected
Secunda Plaza Shops | 2025-07-01 | 3303 | 3591.1049 | 91.98% | Expected
Secunda Plaza Shops | 2025-08-01 | 3882 | 4018.0894 | 96.61% | Expected
Secunda Plaza Shops | 2025-09-01 | 4064 | 4182.1345 | 97.18% | Expected
Secunda Plaza Shops | 2025-10-01 | 4609 | 4194.6844 | 109.9% | Expected
Secunda Plaza Shops | 2025-11-01 | 3681 | 4153.4818 | 88.62% | Moderate
Secunda Plaza Shops | 2025-12-01 | 1203 | 4342.7287 | 27.7% | Poor
Secunda Plaza Shops | 2026-01-01 | 3014 | 4255.7975 | 70.82% | Moderate
Secunda Plaza Shops | 2026-02-01 | 4641.05 | 3732.5789 | 124.3% | Expected
Secunda Plaza Shops | 2026-03-01 | 3756 | 3975.4128 | 94.48% | Expected
Secunda Plaza Shops | 2026-04-01 | 3294.1 | 3482.7715 | 94.58% | Expected
Secunda Plaza Shops | 2026-05-01 | 3420.82 | 3528.9727 | 96.94% | Expected
Secunda Plaza Shops | 2026-06-01 | 2882 | 3271.0705 | 88.11% | Moderate
Secunda Plaza choppies | 2026-07-01 | 0 | 18309.9681 | 0% | Poor | NO
Secunda Plaza Shops | 2026-08-01 | 3905 | 3989.982 | 97.87% | Expected | NO
Secunda Plaza Shops | 2026-09-01 | 3972.39 | 4152.8796 | 95.65% | Expected | NO
Secunda Plaza Shops | 2026-10-01 |  | 4165.3416
Secunda Plaza Shops | 2026-11-01 |  | 4124.4272
Secunda Plaza Shops | 2026-12-01 |  | 4312.3503
Secunda Plaza choppies | 2024-01-01 | 14153 | 22834.6221 | 61.98% | Poor
Secunda Plaza choppies | 2024-02-01 | 12255 | 20139.5134 | 60.85% | Poor
Secunda Plaza choppies | 2024-03-01 | 14981 | 21474.6491 | 69.76% | Poor
Secunda Plaza choppies | 2024-04-01 | 12548 | 18626.9888 | 67.36% | Poor
Secunda Plaza choppies | 2024-05-01 | 12499 | 18471.081 | 67.67% | Poor
Secunda Plaza choppies | 2024-06-01 | 10764 | 16943.38 | 63.53% | Poor
Secunda Plaza choppies | 2024-07-01 | 12646 | 18568.846 | 68.1% | Poor
Secunda Plaza choppies | 2024-08-01 | 13284 | 21195.9215 | 62.67% | Poor
Secunda Plaza choppies | 2024-09-01 | 12781 | 22356.5754 | 57.17% | Poor
Secunda Plaza choppies | 2024-10-01 | 16310 | 22494.5329 | 72.51% | Moderate
Secunda Plaza choppies | 2024-11-01 | 16857 | 22152.76 | 76.09% | Moderate
Secunda Plaza choppies | 2024-12-01 | 17902 | 23110.5231 | 77.46% | Moderate
Secunda Plaza choppies | 2025-01-01 | 16357 | 22674.4527 | 72.14% | Moderate
Secunda Plaza choppies | 2025-02-01 | 13076 | 19998.2483 | 65.39% | Poor
Secunda Plaza choppies | 2025-03-01 | 13410 | 21324.4291 | 62.89% | Poor
Secunda Plaza choppies | 2025-04-01 | 11361 | 18496.6889 | 61.42% | Poor
Secunda Plaza choppies | 2025-05-01 | 12073 | 18341.8716 | 65.82% | Poor
Secunda Plaza choppies | 2025-06-01 | 10687.39 | 16824.8573 | 63.52% | Poor
Secunda Plaza choppies | 2025-07-01 | 10449 | 18438.9528 | 56.67% | Poor
Secunda Plaza choppies | 2025-08-01 | 10325 | 21047.6513 | 49.06% | Poor
Secunda Plaza choppies | 2025-09-01 | 9595 | 22200.1861 | 43.22% | Poor
Secunda Plaza choppies | 2025-10-01 | 11068 | 22337.1786 | 49.55% | Poor
Secunda Plaza choppies | 2025-11-01 | 10671 | 21997.7965 | 48.51% | Poor
Secunda Plaza choppies | 2025-12-01 | 1812 | 22948.8598 | 7.896% | Poor
Secunda Plaza choppies | 2026-01-01 | 306 | 22515.8398 | 1.359% | Poor
Secunda Plaza choppies | 2026-02-01 | 522.4446 | 19858.3561 | 2.631% | Poor
Secunda Plaza choppies | 2026-03-01 | 372 | 21175.2599 | 1.757% | Poor
Secunda Plaza choppies | 2026-04-01 | 44.97 | 18367.3003 | 0.2448% | Poor
Secunda Plaza choppies | 2026-05-01 | 0 | 18213.5661 | 0% | Poor
Secunda Plaza choppies | 2026-06-01 |  | 16707.1636
Secunda Plaza Shops | 2026-07-01 | 2926.66 | 3565.9843 | 82.07% | Moderate | NO
Secunda Plaza choppies | 2026-08-01 |  | 20900.4182 |  |  | NO
Secunda Plaza choppies | 2026-09-01 | 0 | 22044.8908 | 0% | Poor | NO
Secunda Plaza choppies | 2026-10-01 |  | 22180.925
Secunda Plaza choppies | 2026-11-01 |  | 21843.9169
Secunda Plaza choppies | 2026-12-01 |  | 22788.3273
Shoprite Dube | 2024-01-01 |  | 23724
Shoprite Dube | 2024-02-01 |  | 20448
Shoprite Dube | 2024-03-01 |  | 19986.3
Shoprite Dube | 2024-04-01 |  | 17181.9
Shoprite Dube | 2024-05-01 |  | 15369.3
Shoprite Dube | 2024-06-01 |  | 13381.2
Shoprite Dube | 2024-07-01 |  | 15023.7
Shoprite Dube | 2024-08-01 |  | 18071.1
Shoprite Dube | 2024-09-01 |  | 20545.2
Shoprite Dube | 2024-10-01 |  | 23411.7
Shoprite Dube | 2024-11-01 |  | 23583.6
Shoprite Dube | 2024-12-01 |  | 24027.3
Shoprite Dube | 2025-01-01 | 10100 | 23724 | 42.57% | Poor
Shoprite Dube | 2025-02-01 | 12001 | 20438.957 | 58.72% | Poor
Shoprite Dube | 2025-03-01 | 13213 | 19966.7061 | 66.18% | Poor
Shoprite Dube | 2025-04-01 | 9636 | 17154.8246 | 56.17% | Poor
Shoprite Dube | 2025-05-01 | 10261 | 15336.2298 | 66.91% | Poor
Shoprite Dube | 2025-06-01 | 11348.4 | 13344.4492 | 85.04% | Moderate
Shoprite Dube | 2025-07-01 | 14705 | 14973.7963 | 98.2% | Expected
Shoprite Dube | 2025-08-01 | 16958 | 18000.3388 | 94.21% | Expected
Shoprite Dube | 2025-09-01 | 17766 | 20452.5534 | 86.86% | Moderate
Shoprite Dube | 2025-10-01 | 22849 | 23292.6841 | 98.1% | Expected
Shoprite Dube | 2025-11-01 | 20014 | 23449.7253 | 85.35% | Moderate
Shoprite Dube | 2025-12-01 | 21334.1162 | 23877.1262 | 89.35% | Moderate
Shoprite Dube | 2026-01-01 | 23434 | 23561.6702 | 99.46% | Expected
Shoprite Dube | 2026-02-01 | 21742.1962 | 20295.9818 | 107.1% | Expected
Shoprite Dube | 2026-03-01 | 18523 | 19827.0344 | 93.42% | Expected
Shoprite Dube | 2026-04-01 | 15379.43 | 17034.8227 | 90.28% | Expected
Shoprite Dube | 2026-05-01 | 15576.52 | 15228.9494 | 102.3% | Expected
Shoprite Dube | 2026-06-01 | 12252.53 | 13251.1018 | 92.46% | Expected
Shoprite Dube | 2026-07-01 | 13658 | 14869.0512 | 91.86% | Expected | NO
Shoprite Dube | 2026-08-01 | 17067.58 | 17874.4223 | 95.49% | Expected | NO
Shoprite Dube | 2026-09-01 | 18587.26 | 20309.4832 | 91.52% | Expected | NO
Shoprite Dube | 2026-10-01 |  | 23129.7465
Shoprite Dube | 2026-11-01 |  | 23285.6892
Shoprite Dube | 2026-12-01 |  | 23710.1003
Shoprite Ekhaya | 2024-01-01 |  | 28380.6
Shoprite Ekhaya | 2024-02-01 |  | 24379.2
Shoprite Ekhaya | 2024-03-01 |  | 23351.4
Shoprite Ekhaya | 2024-04-01 |  | 19887.3
Shoprite Ekhaya | 2024-05-01 |  | 17745.3
Shoprite Ekhaya | 2024-06-01 |  | 15502.5
Shoprite Ekhaya | 2024-07-01 |  | 17358.3
Shoprite Ekhaya | 2024-08-01 |  | 20842.2
Shoprite Ekhaya | 2024-09-01 |  | 23841
Shoprite Ekhaya | 2024-10-01 |  | 27285.3
Shoprite Ekhaya | 2024-11-01 |  | 27841.5
Shoprite Ekhaya | 2024-12-01 |  | 28779.3
Shoprite Ekhaya | 2025-01-01 |  | 28380.6
Shoprite Ekhaya | 2025-02-01 |  | 24379.2
Shoprite Ekhaya | 2025-03-01 |  | 23351.4
Shoprite Ekhaya | 2025-04-01 |  | 19887.3
Shoprite Ekhaya | 2025-05-01 |  | 17745.3
Shoprite Ekhaya | 2025-06-01 |  | 15502.5
Shoprite Ekhaya | 2025-07-01 |  | 17358.3
Shoprite Ekhaya | 2025-08-01 |  | 20842.2
Shoprite Ekhaya | 2025-09-01 |  | 23841
Shoprite Ekhaya | 2025-10-01 |  | 27285.3
Shoprite Ekhaya | 2025-11-01 |  | 27841.5
Shoprite Ekhaya | 2025-12-01 |  | 28779.3
Shoprite Ekhaya | 2026-01-01 |  | 28380.6
Shoprite Ekhaya | 2026-02-01 |  | 24379.2
Shoprite Ekhaya | 2026-03-01 | 10022 | 23345.1134 | 42.93% | Poor
Shoprite Ekhaya | 2026-04-01 | 11511.86 | 19870.0959 | 57.94% | Poor
Shoprite Ekhaya | 2026-05-01 | 14709.43 | 17719.7222 | 83.01% | Moderate
Shoprite Ekhaya | 2026-06-01 | 12264.7 | 15470.9283 | 79.28% | Moderate
Shoprite Ekhaya | 2026-07-01 | 11339.6067 | 17312.957 | 65.5% | Poor | YES
Shoprite Ekhaya | 2026-08-01 | 16951.843 | 20775.3664 | 81.6% | Moderate | YES
Checkrite Inanda | 2026-09-01 | 5791.73 | 6809.7803 | 85.05% | Moderate | NO
Shoprite Ekhaya | 2026-10-01 |  | 27165.9166
Shoprite Ekhaya | 2026-11-01 |  | 27703.1614
Shoprite Ekhaya | 2026-12-01 |  | 28619.7841
Shoprite Hillbrow | 2024-01-01 |  | 20564.65
Shoprite Hillbrow | 2024-02-01 |  | 17491.4
Shoprite Hillbrow | 2024-03-01 |  | 18246.65
Shoprite Hillbrow | 2024-04-01 |  | 15297.85
Shoprite Hillbrow | 2024-05-01 |  | 14953
Shoprite Hillbrow | 2024-06-01 |  | 13275.3
Shoprite Hillbrow | 2024-07-01 |  | 14678.45
Shoprite Hillbrow | 2024-08-01 |  | 17062.95
Shoprite Hillbrow | 2024-09-01 |  | 18937.3
Shoprite Hillbrow | 2024-10-01 |  | 20481.05
Shoprite Hillbrow | 2024-11-01 |  | 20363.3584
Shoprite Hillbrow | 2024-12-01 |  | 21875.2781
Shoprite Hillbrow | 2025-01-01 | 18900 | 20537.7731 | 92.03% | Expected
Shoprite Hillbrow | 2025-02-01 | 13110 | 17458.128 | 75.09% | Moderate
Shoprite Hillbrow | 2025-03-01 | 11124 | 18202.1368 | 61.11% | Poor
Shoprite Hillbrow | 2025-04-01 | 9398 | 15251.4348 | 61.62% | Poor
Shoprite Hillbrow | 2025-05-01 | 10507 | 14899.0323 | 70.52% | Moderate
Shoprite Hillbrow | 2025-06-01 | 8615 | 13219.5036 | 65.17% | Poor
Shoprite Hillbrow | 2025-07-01 | 9297 | 14608.3251 | 63.64% | Poor
Shoprite Hillbrow | 2025-08-01 | 11805 | 16971.312 | 69.56% | Poor
Shoprite Hillbrow | 2025-09-01 | 12829 | 18824.3692 | 68.15% | Poor
Shoprite Hillbrow | 2025-10-01 | 18800 | 20347.17 | 92.4% | Expected
Shoprite Hillbrow | 2025-11-01 | 15186 | 20220.9121 | 75.1% | Moderate
Shoprite Hillbrow | 2025-12-01 | 17488.2707 | 21722.2556 | 80.51% | Moderate
Shoprite Hillbrow | 2026-01-01 | 18755 | 20394.1068 | 91.96% | Expected
Shoprite Hillbrow | 2026-02-01 | 15395.7162 | 17336.0045 | 88.81% | Moderate
Shoprite Hillbrow | 2026-03-01 | 11700 | 18074.8087 | 64.73% | Poor
Shoprite Hillbrow | 2026-04-01 | 8798.96 | 15144.7476 | 58.1% | Poor
Shoprite Hillbrow | 2026-05-01 | 8378.25 | 14794.8102 | 56.63% | Poor
Shoprite Hillbrow | 2026-06-01 | 6213.16 | 13127.0302 | 47.33% | Poor
Shoprite Hillbrow | 2026-07-01 | 6980.78 | 14506.1366 | 48.12% | Poor | NO
Shoprite Hillbrow | 2026-08-01 | 9821.36 | 16852.5938 | 58.28% | Poor | NO
Shoprite Hillbrow | 2026-09-01 | 11626.59 | 18692.6884 | 62.2% | Poor | YES
Shoprite Hillbrow | 2026-10-01 |  | 20204.837
Shoprite Hillbrow | 2026-11-01 |  | 20079.4622
Shoprite Hillbrow | 2026-12-01 |  | 21570.3035
Shoprite Ladybrand | 2024-01-01 |  | 37513.6
Shoprite Ladybrand | 2024-02-01 |  | 31212.25
Shoprite Ladybrand | 2024-03-01 |  | 29700.135
Shoprite Ladybrand | 2024-04-01 |  | 24898.55
Shoprite Ladybrand | 2024-05-01 |  | 21981.1
Shoprite Ladybrand | 2024-06-01 |  | 18982.9
Shoprite Ladybrand | 2024-07-01 |  | 21551.7
Shoprite Ladybrand | 2024-08-01 |  | 26041.4
Shoprite Ladybrand | 2024-09-01 |  | 29888.9
Shoprite Ladybrand | 2024-10-01 |  | 34700.0607
Shoprite Ladybrand | 2024-11-01 |  | 36854.1967
Shoprite Ladybrand | 2024-12-01 |  | 40057.7069
Shoprite Ladybrand | 2025-01-01 | 33100 | 37441.5219 | 88.4% | Moderate
Shoprite Ladybrand | 2025-02-01 | 24950 | 31133.7117 | 80.14% | Moderate
Shoprite Ladybrand | 2025-03-01 | 24126 | 29609.4524 | 81.48% | Moderate
Shoprite Ladybrand | 2025-04-01 | 18837 | 24807.7331 | 75.93% | Moderate
Shoprite Ladybrand | 2025-05-01 | 22373 | 21888.2919 | 102.2% | Expected
Shoprite Ladybrand | 2025-06-01 | 18416.6 | 18891.4843 | 97.49% | Expected
Shoprite Ladybrand | 2025-07-01 | 19123 | 21435.5425 | 89.21% | Moderate
Shoprite Ladybrand | 2025-08-01 | 22404 | 25885.6067 | 86.55% | Moderate
Shoprite Ladybrand | 2025-09-01 | 21900 | 29692.3809 | 73.76% | Moderate
Shoprite Ladybrand | 2025-10-01 | 29612 | 34457.3259 | 85.94% | Moderate
Shoprite Ladybrand | 2025-11-01 | 26751 | 36596.3933 | 73.1% | Moderate
Shoprite Ladybrand | 2025-12-01 | 30623.1004 | 39777.4942 | 76.99% | Moderate
Shoprite Ladybrand | 2026-01-01 | 34009 | 37179.61 | 91.47% | Expected
Shoprite Ladybrand | 2026-02-01 | 24602.8829 | 30915.9243 | 79.58% | Moderate
Shoprite Ladybrand | 2026-03-01 | 23540 | 29402.3276 | 80.06% | Moderate
Shoprite Ladybrand | 2026-04-01 | 18199.29 | 24634.1974 | 73.88% | Moderate
Shoprite Ladybrand | 2026-05-01 | 17860.55 | 21735.1783 | 82.17% | Moderate
Shoprite Ladybrand | 2026-06-01 | 14774.05 | 18759.3341 | 78.76% | Moderate
Shoprite Ladybrand | 2026-07-01 | 17814.88 | 21285.5961 | 83.69% | Moderate | NO
Shoprite Ladybrand | 2026-08-01 | 21703.83 | 25704.531 | 84.44% | Moderate | NO
Shoprite Ladybrand | 2026-09-01 | 20441.04 | 29484.676 | 69.33% | Poor | YES
Shoprite Ladybrand | 2026-10-01 |  | 34216.2892
Shoprite Ladybrand | 2026-11-01 |  | 36340.3933
Shoprite Ladybrand | 2026-12-01 |  | 39499.2416
Shoprite Mini Ganyesa | 2024-01-01 |  | 34074.9
Shoprite Mini Ganyesa | 2024-02-01 |  | 28396.8
Shoprite Mini Ganyesa | 2024-03-01 |  | 28665.9
Shoprite Mini Ganyesa | 2024-04-01 |  | 24411.6
Shoprite Mini Ganyesa | 2024-05-01 |  | 22266.9
Shoprite Mini Ganyesa | 2024-06-01 |  | 19791.9
Shoprite Mini Ganyesa | 2024-07-01 |  | 21774.6
Shoprite Mini Ganyesa | 2024-08-01 | 3670 | 25973.1 | 14.13% | Poor
Shoprite Mini Ganyesa | 2024-09-01 | 24226 | 28981.7129 | 83.59% | Moderate
Shoprite Mini Ganyesa | 2024-10-01 | 29060 | 33036.5545 | 87.96% | Moderate
Shoprite Mini Ganyesa | 2024-11-01 | 28700 | 34322.9051 | 83.62% | Moderate
Shoprite Mini Ganyesa | 2024-12-01 | 32654 | 36253.4033 | 90.07% | Expected
Shoprite Mini Ganyesa | 2025-01-01 | 31900 | 33991.7733 | 93.85% | Expected
Shoprite Mini Ganyesa | 2025-02-01 | 24980 | 28310.6413 | 88.24% | Moderate
Shoprite Mini Ganyesa | 2025-03-01 | 24068 | 28563.5391 | 84.26% | Moderate
Shoprite Mini Ganyesa | 2025-04-01 | 17329 | 24309.9325 | 71.28% | Moderate
Shoprite Mini Ganyesa | 2025-05-01 | 19241 | 22161.3744 | 86.82% | Moderate
Shoprite Mini Ganyesa | 2025-06-01 | 18515.91 | 19686.3632 | 94.05% | Expected
Shoprite Mini Ganyesa | 2025-07-01 | 18781 | 21645.9981 | 86.76% | Moderate
Shoprite Mini Ganyesa | 2025-08-01 | 21235 | 25804.3123 | 82.29% | Moderate
Shoprite Mini Ganyesa | 2025-09-01 | 23085 | 28778.9793 | 80.21% | Moderate
Shoprite Mini Ganyesa | 2025-10-01 | 25611 | 32805.4564 | 78.07% | Moderate
Shoprite Mini Ganyesa | 2025-11-01 | 25276 | 34082.8086 | 74.16% | Moderate
Shoprite Mini Ganyesa | 2025-12-01 | 28457.1296 | 35999.8026 | 79.05% | Moderate
Shoprite Mini Ganyesa | 2026-01-01 | 29092 | 33753.9932 | 86.19% | Moderate
Shoprite Mini Ganyesa | 2026-02-01 | 23486.9398 | 28112.602 | 83.55% | Moderate
Shoprite Mini Ganyesa | 2026-03-01 | 22459 | 28363.7307 | 79.18% | Moderate
Shoprite Mini Ganyesa | 2026-04-01 | 18207.86 | 24139.879 | 75.43% | Moderate
Shoprite Mini Ganyesa | 2026-05-01 | 17848.83 | 22006.3506 | 81.11% | Moderate
Shoprite Mini Ganyesa | 2026-06-01 | 14983.63 | 19548.6526 | 76.65% | Moderate
Shoprite Mini Ganyesa | 2026-07-01 | 18234 | 21494.5794 | 84.83% | Moderate | NO
Shoprite Mini Ganyesa | 2026-08-01 | 20218.59 | 25623.8053 | 78.91% | Moderate | NO
Shoprite Mini Ganyesa | 2026-09-01 | 17902.21 | 28577.6639 | 62.64% | Poor | YES
Shoprite Mini Ganyesa | 2026-10-01 |  | 32575.9748
Shoprite Mini Ganyesa | 2026-11-01 |  | 33844.3917
Shoprite Mini Ganyesa | 2026-12-01 |  | 35747.9758
Shoprite Naledi | 2024-01-01 |  | 20588.4
Shoprite Naledi | 2024-02-01 |  | 17538.3
Shoprite Naledi | 2024-03-01 |  | 17897.4
Shoprite Naledi | 2024-04-01 |  | 14674.5
Shoprite Naledi | 2024-05-01 |  | 13272.3
Shoprite Naledi | 2024-06-01 |  | 11571.3
Shoprite Naledi | 2024-07-01 |  | 12990.6
Shoprite Naledi | 2024-08-01 |  | 15871.5
Shoprite Naledi | 2024-09-01 | 10570 | 18317.7 | 57.7% | Poor
Shoprite Naledi | 2024-10-01 | 18040 | 20111.241 | 89.7% | Moderate
Shoprite Naledi | 2024-11-01 | 18800 | 20550.5592 | 91.48% | Expected
Shoprite Naledi | 2024-12-01 | 20883 | 21893.6366 | 95.38% | Expected
Shoprite Naledi | 2025-01-01 | 20300 | 20541.7293 | 98.82% | Expected
Shoprite Naledi | 2025-02-01 | 13100 | 17488.1138 | 74.91% | Moderate
Shoprite Naledi | 2025-03-01 | 12342 | 17836.5786 | 69.19% | Poor
Shoprite Naledi | 2025-04-01 | 10819 | 14615.9144 | 74.02% | Moderate
Shoprite Naledi | 2025-05-01 | 15169 | 13211.6875 | 114.8% | Expected
Shoprite Naledi | 2025-06-01 | 13081.41 | 11511.5904 | 113.6% | Expected
Shoprite Naledi | 2025-07-01 | 14154 | 12916.1123 | 109.6% | Expected
Shoprite Naledi | 2025-08-01 | 16190 | 15771.0877 | 102.7% | Expected
Shoprite Naledi | 2025-09-01 | 16520 | 18190.9629 | 90.81% | Expected
Shoprite Naledi | 2025-10-01 | 20440 | 19970.5584 | 102.4% | Expected
Shoprite Naledi | 2025-11-01 | 17928 | 20406.8034 | 87.85% | Moderate
Shoprite Naledi | 2025-12-01 | 20527.8823 | 21740.4857 | 94.42% | Expected
Shoprite Naledi | 2026-01-01 | 22071 | 20398.0353 | 108.2% | Expected
Shoprite Naledi | 2026-02-01 | 18965 | 17365.7805 | 109.2% | Expected
Shoprite Naledi | 2026-03-01 | 15865 | 17711.8077 | 89.57% | Moderate
Shoprite Naledi | 2026-04-01 | 13806.89 | 14513.6728 | 95.13% | Expected
Shoprite Naledi | 2026-05-01 | 13506.85 | 13119.2688 | 103% | Expected
Shoprite Naledi | 2026-06-01 | 10711.09 | 11431.0643 | 93.7% | Expected
Shoprite Naledi | 2026-07-01 | 9106.96 | 12825.7612 | 71.01% | Moderate | YES
Shoprite Naledi | 2026-08-01 | 14997.19 | 15660.7654 | 95.76% | Expected | NO
Quintondale | 2026-09-01 | 4995.41 | 5838.9934 | 85.55% | Moderate | NO
Shoprite Naledi | 2026-10-01 |  | 19830.8598
Shoprite Naledi | 2026-11-01 |  | 20264.0532
Shoprite Naledi | 2026-12-01 |  | 21588.4061
Shoprite Newlands | 2024-01-01 |  | 30721.5
Shoprite Newlands | 2024-02-01 |  | 24282.9
Shoprite Newlands | 2024-03-01 |  | 24146.1
Shoprite Newlands | 2024-04-01 |  | 18389.7
Shoprite Newlands | 2024-05-01 |  | 18961.2
Shoprite Newlands | 2024-06-01 |  | 15280.2
Shoprite Newlands | 2024-07-01 |  | 17361.9
Shoprite Newlands | 2024-08-01 |  | 19303.2
Shoprite Newlands | 2024-09-01 |  | 18141.3
Shoprite Newlands | 2024-10-01 |  | 22548.6
Shoprite Newlands | 2024-11-01 |  | 22923.9
Shoprite Newlands | 2024-12-01 |  | 28392.3
Shoprite Newlands | 2025-01-01 |  | 30721.5
Shoprite Newlands | 2025-02-01 |  | 24282.9
Shoprite Newlands | 2025-03-01 |  | 24146.1
Shoprite Newlands | 2025-04-01 |  | 18389.7
Shoprite Newlands | 2025-05-01 |  | 18961.2
Shoprite Newlands | 2025-06-01 |  | 15280.2
Shoprite Newlands | 2025-07-01 |  | 17361.9
Shoprite Newlands | 2025-08-01 |  | 19303.2
Shoprite Newlands | 2025-09-01 |  | 18141.3
Shoprite Newlands | 2025-10-01 |  | 22548.6
Shoprite Newlands | 2025-11-01 |  | 22923.9
Shoprite Newlands | 2025-12-01 | 18509 | 28392.3 | 65.19% | Poor
Shoprite Newlands | 2026-01-01 | 32917 | 30703.1892 | 107.2% | Expected
Shoprite Newlands | 2026-02-01 | 31107 | 24253.9622 | 128.3% | Expected
Shoprite Newlands | 2026-03-01 | 26454 | 24104.3414 | 109.7% | Expected
Shoprite Newlands | 2026-04-01 | 20930.87 | 18346.9548 | 114.1% | Expected
Shoprite Newlands | 2026-05-01 | 20539.96 | 18906.215 | 108.6% | Expected
Shoprite Newlands | 2026-06-01 | 17006.73 | 15226.8084 | 111.7% | Expected
Shoprite Newlands | 2026-07-01 | 17999.1711 | 17291.2552 | 104.1% | Expected | NO
Shoprite Newlands | 2026-08-01 | 22467.354 | 19213.1977 | 116.9% | Expected | NO
Shoprite Newlands | 2026-09-01 | 21057.6623 | 18045.9529 | 116.7% | Expected | NO
Shoprite Newlands | 2026-10-01 |  | 22417.1512
Shoprite Newlands | 2026-11-01 |  | 22776.6798
Shoprite Newlands | 2026-12-01 |  | 28193.6895
Shoprite Thokoza | 2024-01-01 |  | 18584.1
Shoprite Thokoza | 2024-02-01 |  | 16101.9
Shoprite Thokoza | 2024-03-01 |  | 15901.2
Shoprite Thokoza | 2024-04-01 |  | 13660.2
Shoprite Thokoza | 2024-05-01 |  | 12620.7
Shoprite Thokoza | 2024-06-01 |  | 11094.3
Shoprite Thokoza | 2024-07-01 |  | 12367.8
Shoprite Thokoza | 2024-08-01 |  | 14484.6
Shoprite Thokoza | 2024-09-01 |  | 16189.2
Shoprite Thokoza | 2024-10-01 |  | 18663.3
Shoprite Thokoza | 2024-11-01 |  | 18589.5
Shoprite Thokoza | 2024-12-01 |  | 19022.4
Shoprite Thokoza | 2025-01-01 |  | 18584.1
Shoprite Thokoza | 2025-02-01 |  | 16101.9
Shoprite Thokoza | 2025-03-01 |  | 15901.2
Shoprite Thokoza | 2025-04-01 | 4166 | 13660.2 | 30.5% | Poor
Shoprite Thokoza | 2025-05-01 | 5400 | 12613.4203 | 42.81% | Poor
Shoprite Thokoza | 2025-06-01 | 8687.3 | 11081.2921 | 78.4% | Moderate
Shoprite Thokoza | 2025-07-01 | 7090 | 12346.1735 | 57.43% | Poor
Shoprite Thokoza | 2025-08-01 | 10240 | 14450.654 | 70.86% | Moderate
Shoprite Thokoza | 2025-09-01 | 11379 | 16141.6325 | 70.49% | Moderate
Shoprite Thokoza | 2025-10-01 | 16828.7 | 18597.7296 | 90.49% | Expected
Shoprite Thokoza | 2025-11-01 | 15461 | 18513.148 | 83.51% | Moderate
Shoprite Thokoza | 2025-12-01 | 17561 | 18933.3428 | 92.75% | Expected
Shoprite Thokoza | 2026-01-01 | 20127 | 18486.0701 | 108.9% | Expected
Shoprite Thokoza | 2026-02-01 | 16780 | 16007.417 | 104.8% | Expected
Shoprite Thokoza | 2026-03-01 | 14651 | 15799.3843 | 92.73% | Expected
Shoprite Thokoza | 2026-04-01 | 12498.2 | 13564.6438 | 92.14% | Expected
Shoprite Thokoza | 2026-05-01 | 11697.82 | 12525.1866 | 93.39% | Expected
Shoprite Thokoza | 2026-06-01 | 9082.64 | 11003.776 | 82.54% | Moderate
Shoprite Thokoza | 2026-07-01 | 7916.06 | 12259.8092 | 64.57% | Poor | NO
Shoprite Thokoza | 2026-08-01 | 11233.53 | 14349.5684 | 78.28% | Moderate | YES
Saverite Durban | 2026-09-01 | 7731.86 | 8993.978 | 85.97% | Moderate | NO
Shoprite Thokoza | 2026-10-01 |  | 18467.6343
Shoprite Thokoza | 2026-11-01 |  | 18383.6444
Shoprite Thokoza | 2026-12-01 |  | 18800.8998
Spring Glade | 2024-01-01 | 9171 | 16397.2333 | 55.93% | Poor
Spring Glade | 2024-02-01 | 8406 | 14000.4459 | 60.04% | Poor
Spring Glade | 2024-03-01 | 9529 | 14900.4592 | 63.95% | Poor
Spring Glade | 2024-04-01 | 8796 | 12962.963 | 67.85% | Poor
Spring Glade | 2024-05-01 | 10039 | 12598.4667 | 79.68% | Moderate
Spring Glade | 2024-06-01 | 10175 | 11377.5485 | 89.43% | Moderate
Spring Glade | 2024-07-01 | 10629 | 12661.0755 | 83.95% | Moderate
Spring Glade | 2024-08-01 | 10264 | 14561.8573 | 70.49% | Moderate
Spring Glade | 2024-09-01 | 9192 | 15690.2389 | 58.58% | Poor
Spring Glade | 2024-10-01 | 10175 | 16465.4564 | 61.8% | Poor
Spring Glade | 2024-11-01 | 9431 | 16129.4478 | 58.47% | Poor
Spring Glade | 2024-12-01 | 9104 | 17036.3254 | 53.44% | Poor
Spring Glade | 2025-01-01 | 5093 | 16282.2178 | 31.28% | Poor
Spring Glade | 2025-02-01 | 7532 | 13902.2422 | 54.18% | Poor
Spring Glade | 2025-03-01 | 7375 | 14796.2271 | 49.84% | Poor
Spring Glade | 2025-04-01 | 7602 | 12872.2842 | 59.06% | Poor
Spring Glade | 2025-05-01 | 10378 | 12510.3376 | 82.96% | Moderate
Spring Glade | 2025-06-01 | 10510.45 | 11297.96 | 93.03% | Expected
Spring Glade | 2025-07-01 | 9750 | 12572.5084 | 77.55% | Moderate
Spring Glade | 2025-08-01 | 10081 | 14459.9938 | 69.72% | Poor
Spring Glade | 2025-09-01 | 11225 | 15580.4821 | 72.05% | Moderate
Spring Glade | 2025-10-01 | 9885 | 16350.2769 | 60.46% | Poor
Spring Glade | 2025-11-01 | 8679 | 16016.6186 | 54.19% | Poor
Spring Glade | 2025-12-01 | 9967 | 16917.1525 | 58.92% | Poor
Spring Glade | 2026-01-01 | 9751 | 16168.32 | 60.31% | Poor
Spring Glade | 2026-02-01 | 8451 | 13804.9929 | 61.22% | Poor
Spring Glade | 2026-03-01 | 8559 | 14692.7242 | 58.25% | Poor
Spring Glade | 2026-04-01 | 7937.13 | 12782.2396 | 62.09% | Poor
Spring Glade | 2026-05-01 | 10005.8 | 12422.8249 | 80.54% | Moderate
Spring Glade | 2026-06-01 | 9053 | 11218.9282 | 80.69% | Moderate
Spring Glade | 2026-07-01 | 9713.47 | 12484.5609 | 77.8% | Moderate | NO
Spring Glade | 2026-08-01 | 9565 | 14358.8429 | 66.61% | Poor | NO
Spring Glade | 2026-09-01 | 7250.71 | 15471.4931 | 46.86% | Poor | NO
Spring Glade | 2026-10-01 |  | 16235.903
Spring Glade | 2026-11-01 |  | 15904.5788
Spring Glade | 2026-12-01 |  | 16798.8132
TPF Foods | 2024-01-01 | 3404 | 3716.5519 | 91.59% | Expected
TPF Foods | 2024-02-01 | 3408 | 3209.5862 | 106.2% | Expected
TPF Foods | 2024-03-01 | 3131 | 3465.9535 | 90.34% | Expected
TPF Foods | 2024-04-01 | 2829 | 3002.8791 | 94.21% | Expected
TPF Foods | 2024-05-01 | 3129 | 3031.2753 | 103.2% | Expected
TPF Foods | 2024-06-01 | 2591 | 2775.0729 | 93.37% | Expected
TPF Foods | 2024-07-01 | 3122 | 3037.0427 | 102.8% | Expected
TPF Foods | 2024-08-01 | 2990 | 3414.9117 | 87.56% | Moderate
TPF Foods | 2024-09-01 | 2990 | 3639.551 | 82.15% | Moderate
TPF Foods | 2024-10-01 | 4061 | 3809.3379 | 106.6% | Expected
TPF Foods | 2024-11-01 | 3991 | 3644.3635 | 109.5% | Expected
TPF Foods | 2024-12-01 | 3569 | 3918.8157 | 91.07% | Expected
TPF Foods | 2025-01-01 | 3838 | 3690.4828 | 104% | Expected
TPF Foods | 2025-02-01 | 2653 | 3187.0731 | 83.24% | Moderate
TPF Foods | 2025-03-01 | 2925 | 3441.7084 | 84.99% | Moderate
TPF Foods | 2025-04-01 | 2246 | 2981.8733 | 75.32% | Moderate
TPF Foods | 2025-05-01 | 3149 | 3010.0709 | 104.6% | Expected
TPF Foods | 2025-06-01 | 2654.45 | 2755.6606 | 96.33% | Expected
TPF Foods | 2025-07-01 | 2863 | 3015.7979 | 94.93% | Expected
TPF Foods | 2025-08-01 | 3192 | 3391.0236 | 94.13% | Expected
TPF Foods | 2025-09-01 | 3092 | 3614.0915 | 85.55% | Moderate
TPF Foods | 2025-10-01 | 3600 | 3782.6907 | 95.17% | Expected
TPF Foods | 2025-11-01 | 2755 | 3618.8703 | 76.13% | Moderate
TPF Foods | 2025-12-01 | 3248 | 3891.4027 | 83.47% | Moderate
TPF Foods | 2026-01-01 | 3546 | 3664.667 | 96.76% | Expected
TPF Foods | 2026-02-01 | 3398 | 3164.7788 | 107.4% | Expected
TPF Foods | 2026-03-01 | 2638 | 3417.6328 | 77.19% | Moderate
TPF Foods | 2026-04-01 | 2034.35 | 2961.0144 | 68.7% | Poor
TPF Foods | 2026-05-01 | 2231.41 | 2989.0148 | 74.65% | Moderate
TPF Foods | 2026-06-01 | 1788 | 2736.3841 | 65.34% | Poor
SR Morula TF 1 | 2026-07-01 | 2899 | 6049.9371 | 47.92% | Poor | YES
TPF Foods | 2026-08-01 | 3050 | 3367.3026 | 90.58% | Expected | NO
Olievenhoutbosch 1 | 2026-09-01 | 35252.9187 | 40510.7637 | 87.02% | Moderate | NO
TPF Foods | 2026-10-01 |  | 3756.2299
TPF Foods | 2026-11-01 |  | 3593.5555
TPF Foods | 2026-12-01 |  | 3864.1814
Thakadu Industrial | 2024-01-01 |  | 0
Thakadu Industrial | 2024-02-01 |  | 0
Thakadu Industrial | 2024-03-01 |  | 0
Thakadu Industrial | 2024-04-01 |  | 0
Thakadu Industrial | 2024-05-01 |  | 0
Thakadu Industrial | 2024-06-01 |  | 0
Thakadu Industrial | 2024-07-01 |  | 0
Thakadu Industrial | 2024-08-01 |  | 0
Thakadu Industrial | 2024-09-01 |  | 0
Thakadu Industrial | 2024-10-01 |  | 0
Thakadu Industrial | 2024-11-01 |  | 0
Thakadu Industrial | 2024-12-01 |  | 0
Thakadu Industrial | 2025-01-01 |  | 0
Thakadu Industrial | 2025-02-01 |  | 0
Thakadu Industrial | 2025-03-01 |  | 0
Thakadu Industrial | 2025-04-01 |  | 0
Thakadu Industrial | 2025-05-01 |  | 0
Thakadu Industrial | 2025-06-01 |  | 0
Thakadu Industrial | 2025-07-01 |  | 0
Thakadu Industrial | 2025-08-01 |  | 0
Thakadu Industrial | 2025-09-01 |  | 0
Thakadu Industrial | 2025-10-01 |  | 0
Thakadu Industrial | 2025-11-01 |  | 0
Thakadu Industrial | 2025-12-01 |  | 0
Thakadu Industrial | 2026-01-01 |  | 0
Thakadu Industrial | 2026-02-01 |  | 0
Thakadu Industrial | 2026-03-01 |  | 0
Thakadu Industrial | 2026-04-01 |  | 0
Thakadu Industrial | 2026-05-01 |  | 0
Thakadu Industrial | 2026-06-01 |  | 0
SR Morula TF 1 - Shoprite | 2026-07-01 | 10206 | 19065.8449 | 53.53% | Poor | YES
Thakadu Industrial | 2026-08-01 |  | 0 |  |  | NO
Thakadu Industrial | 2026-09-01 |  | 0 |  |  | NO
Thakadu Industrial | 2026-10-01 |  | 0
Thakadu Industrial | 2026-11-01 |  | 0
Thakadu Industrial | 2026-12-01 |  | 0
The Alec | 2024-01-01 | 6142 | 7367.9899 | 83.36% | Moderate
The Alec | 2024-02-01 | 5738 | 6267.3877 | 91.55% | Expected
The Alec | 2024-03-01 | 5912 | 6318.494 | 93.57% | Expected
The Alec | 2024-04-01 | 4354 | 4986.3004 | 87.32% | Moderate
The Alec | 2024-05-01 | 3536 | 4722.3622 | 74.88% | Moderate
The Alec | 2024-06-01 | 2689 | 4226.3271 | 63.62% | Poor
The Alec | 2024-07-01 | 3106 | 4693.6073 | 66.18% | Poor
The Alec | 2024-08-01 | 4461 | 5394.9667 | 82.69% | Moderate
The Alec | 2024-09-01 | 5033 | 6289.0385 | 80.03% | Moderate
The Alec | 2024-10-01 | 6965 | 7181.2893 | 96.99% | Expected
The Alec | 2024-11-01 | 6934 | 7256.2982 | 95.56% | Expected
The Alec | 2024-12-01 | 7000 | 7781.8865 | 89.95% | Moderate
The Alec | 2025-01-01 | 5900 | 7316.3084 | 80.64% | Moderate
The Alec | 2025-02-01 | 4280 | 6223.4262 | 68.77% | Poor
The Alec | 2025-03-01 | 4292 | 6274.2948 | 68.41% | Poor
The Alec | 2025-04-01 | 3097 | 4951.4201 | 62.55% | Poor
The Alec | 2025-05-01 | 3200 | 4689.3282 | 68.24% | Poor
The Alec | 2025-06-01 | 2560.4 | 4196.763 | 61.01% | Poor
The Alec | 2025-07-01 | 2823 | 4660.7745 | 60.57% | Poor
The Alec | 2025-08-01 | 4200 | 5357.2277 | 78.4% | Moderate
The Alec | 2025-09-01 | 4566 | 6245.0453 | 73.11% | Moderate
The Alec | 2025-10-01 | 6195.1 | 7131.0545 | 86.87% | Moderate
The Alec | 2025-11-01 | 5304 | 7205.5388 | 73.61% | Moderate
The Alec | 2025-12-01 | 6296 | 7727.4505 | 81.48% | Moderate
The Alec | 2026-01-01 | 6828 | 7265.1292 | 93.98% | Expected
The Alec | 2026-02-01 | 6062 | 6179.8919 | 98.09% | Expected
The Alec | 2026-03-01 | 4541 | 6230.4046 | 72.88% | Moderate
The Alec | 2026-04-01 | 3743.09 | 4916.7838 | 76.13% | Moderate
The Alec | 2026-05-01 | 3041.11 | 4656.5253 | 65.31% | Poor
The Alec | 2026-06-01 | 2444 | 4167.4057 | 58.65% | Poor
SR Morula TF 2 | 2026-07-01 | 4951 | 6209.7062 | 79.73% | Moderate | YES
The Alec | 2026-08-01 | 3881 | 5319.7527 | 72.95% | Moderate | NO
Engen Kaalfontein | 2026-09-01 | 12896.9249 | 14803.5309 | 87.12% | Moderate | NO
The Alec | 2026-10-01 |  | 7081.1712
The Alec | 2026-11-01 |  | 7155.1344
The Alec | 2026-12-01 |  | 7673.3952
Three Peaks | 2024-01-01 | 3510 | 4218.9729 | 83.2% | Moderate
Three Peaks | 2024-02-01 | 3517 | 3759.2092 | 93.56% | Expected
Three Peaks | 2024-03-01 | 3409 | 3852.4312 | 88.49% | Moderate
Three Peaks | 2024-04-01 | 2977 | 3220.332 | 92.44% | Expected
Three Peaks | 2024-05-01 | 2754 | 2885.4371 | 95.44% | Expected
Three Peaks | 2024-06-01 | 2322 | 2622.702 | 88.53% | Moderate
Three Peaks | 2024-07-01 | 3200 | 2804.5176 | 114.1% | Expected
Three Peaks | 2024-08-01 | 1967.434 | 3182.1869 | 61.83% | Poor
Three Peaks | 2024-09-01 | 2608 | 3269.4503 | 79.77% | Moderate
Three Peaks | 2024-10-01 | 3179 | 3707.4374 | 85.75% | Moderate
Three Peaks | 2024-11-01 | 2499 | 3758.0723 | 66.5% | Poor
Three Peaks | 2024-12-01 | 2419 | 4232.6289 | 57.15% | Poor
Three Peaks | 2025-01-01 | 2940 | 4189.3797 | 70.18% | Moderate
Three Peaks | 2025-02-01 | 2482 | 3732.8409 | 66.49% | Poor
Three Peaks | 2025-03-01 | 2660 | 3825.4826 | 69.53% | Poor
Three Peaks | 2025-04-01 | 3014 | 3197.805 | 94.25% | Expected
Three Peaks | 2025-05-01 | 3259 | 2865.2529 | 113.7% | Expected
Three Peaks | 2025-06-01 | 2701.4 | 2604.3556 | 103.7% | Expected
Three Peaks | 2025-07-01 | 2990 | 2784.8993 | 107.4% | Expected
Three Peaks | 2025-08-01 | 3504 | 3159.9267 | 110.9% | Expected
Three Peaks | 2025-09-01 | 3456 | 3246.5798 | 106.5% | Expected
Three Peaks | 2025-10-01 | 4131 | 3681.5031 | 112.2% | Expected
Three Peaks | 2025-11-01 | 3798 | 3731.7837 | 101.8% | Expected
Three Peaks | 2025-12-01 | 4633 | 4203.0207 | 110.2% | Expected
Three Peaks | 2026-01-01 | 5177 | 4160.074 | 124.4% | Expected
Three Peaks | 2026-02-01 | 3087 | 3706.7288 | 83.28% | Moderate
Three Peaks | 2026-03-01 | 4035 | 3798.7224 | 106.2% | Expected
Three Peaks | 2026-04-01 | 3282.98 | 3175.4356 | 103.4% | Expected
Three Peaks | 2026-05-01 | 3208.4 | 2845.2098 | 112.8% | Expected
Three Peaks | 2026-06-01 | 3015 | 2586.1376 | 116.6% | Expected
Thakadu Industrial | 2026-07-01 | 0 | 0 |  |  | NO
Three Peaks | 2026-08-01 | 3769 | 3137.8223 | 120.1% | Expected | NO
Three Peaks | 2026-09-01 | 3170.27 | 3223.8692 | 98.34% | Expected | NO
Three Peaks | 2026-10-01 |  | 3655.7501
Three Peaks | 2026-11-01 |  | 3705.679
Three Peaks | 2026-12-01 |  | 4173.6196
Trouw Nutrition | 2024-01-01 |  | 13239.8064
Trouw Nutrition | 2024-02-01 | 11561 | 11866.7288 | 97.42% | Expected
Trouw Nutrition | 2024-03-01 | 11738 | 12650.4518 | 92.79% | Expected
Trouw Nutrition | 2024-04-01 | 307 | 11337.9697 | 2.708% | Poor
Trouw Nutrition | 2024-05-01 | 1 | 11581.6766 | 0.008634% | Poor
Trouw Nutrition | 2024-06-01 | 1 | 10821.2254 | 0.009241% | Poor
Trouw Nutrition | 2024-07-01 | 6245 | 11802.0321 | 52.91% | Poor
Trouw Nutrition | 2024-08-01 | 10791 | 13009.7503 | 82.95% | Moderate
Trouw Nutrition | 2024-09-01 | 10127 | 13274.2339 | 76.29% | Moderate
Trouw Nutrition | 2024-10-01 | 12940 | 13643.7592 | 94.84% | Expected
Trouw Nutrition | 2024-11-01 | 12711 | 13227.3749 | 96.1% | Expected
Trouw Nutrition | 2024-12-01 | 12090 | 13930.385 | 86.79% | Moderate
Trouw Nutrition | 2025-01-01 | 10838 | 13146.9381 | 82.44% | Moderate
Trouw Nutrition | 2025-02-01 | 8901 | 11783.4918 | 75.54% | Moderate
Trouw Nutrition | 2025-03-01 | 9398 | 12561.959 | 74.81% | Moderate
Trouw Nutrition | 2025-04-01 | 8195 | 11258.658 | 72.79% | Moderate
Trouw Nutrition | 2025-05-01 | 6021 | 11500.6601 | 52.35% | Poor
Trouw Nutrition | 2025-06-01 | 4341.56 | 10745.5285 | 40.4% | Poor
Trouw Nutrition | 2025-07-01 | 6989 | 11719.4742 | 59.64% | Poor
Trouw Nutrition | 2025-08-01 | 11205 | 12918.7442 | 86.73% | Moderate
Trouw Nutrition | 2025-09-01 | 10024 | 13181.3777 | 76.05% | Moderate
Trouw Nutrition | 2025-10-01 | 13192 | 13548.3181 | 97.37% | Expected
Trouw Nutrition | 2025-11-01 | 10364 | 13134.8464 | 78.9% | Moderate
Trouw Nutrition | 2025-12-01 | 10702 | 13832.9388 | 77.37% | Moderate
Trouw Nutrition | 2026-01-01 | 12710 | 13054.9723 | 97.36% | Expected
Trouw Nutrition | 2026-02-01 | 12261 | 11701.0636 | 104.8% | Expected
Trouw Nutrition | 2026-03-01 | 11049 | 12474.0853 | 88.58% | Moderate
Trouw Nutrition | 2026-04-01 | 9364.19 | 11179.9012 | 83.76% | Moderate
Trouw Nutrition | 2026-05-01 | 10132.34 | 11420.2104 | 88.72% | Moderate
Trouw Nutrition | 2026-06-01 | 8126 | 10670.3611 | 76.15% | Moderate
The Alec | 2026-07-01 | 2690 | 4628.1713 | 58.12% | Poor | NO
Trouw Nutrition | 2026-08-01 | 11112 | 12828.3747 | 86.62% | Moderate | NO
Checkers Silverlakes No Gen | 2026-09-01 | 16232 | 18626.4 | 87.15% | Moderate | NO
Trouw Nutrition | 2026-10-01 |  | 13453.5445
Trouw Nutrition | 2026-11-01 |  | 13042.9652
Trouw Nutrition | 2026-12-01 |  | 13736.1743
U Save Botrivier | 2024-01-01 |  | 7299.9
U Save Botrivier | 2024-02-01 |  | 6223.5
U Save Botrivier | 2024-03-01 |  | 6048.9
U Save Botrivier | 2024-04-01 |  | 5130.9
U Save Botrivier | 2024-05-01 |  | 4621.5
U Save Botrivier | 2024-06-01 |  | 3931.2
U Save Botrivier | 2024-07-01 |  | 4065.3
U Save Botrivier | 2024-08-01 |  | 4723.2
U Save Botrivier | 2024-09-01 |  | 5251.5
U Save Botrivier | 2024-10-01 |  | 6489.9
U Save Botrivier | 2024-11-01 |  | 6813.9
U Save Botrivier | 2024-12-01 |  | 7296.3
U Save Botrivier | 2025-01-01 |  | 7299.9
U Save Botrivier | 2025-02-01 |  | 6223.5
U Save Botrivier | 2025-03-01 |  | 6048.9
U Save Botrivier | 2025-04-01 |  | 5130.9
U Save Botrivier | 2025-05-01 |  | 4621.5
U Save Botrivier | 2025-06-01 |  | 3931.2
U Save Botrivier | 2025-07-01 |  | 4065.3
U Save Botrivier | 2025-08-01 | 3866 | 4722.3825 | 81.87% | Moderate
U Save Botrivier | 2025-09-01 | 4249 | 5247.4616 | 80.97% | Moderate
U Save Botrivier | 2025-10-01 | 5286 | 6481.1688 | 81.56% | Moderate
U Save Botrivier | 2025-11-01 | 5001 | 6800.6771 | 73.54% | Moderate
U Save Botrivier | 2025-12-01 | 6707 | 7277.9406 | 92.16% | Expected
U Save Botrivier | 2026-01-01 | 7171.5 | 7277.1915 | 98.55% | Expected
U Save Botrivier | 2026-02-01 | 4844 | 6200.4422 | 78.12% | Moderate
U Save Botrivier | 2026-03-01 | 5410 | 6023.2446 | 89.82% | Moderate
U Save Botrivier | 2026-04-01 | 2815.5 | 5106.093 | 55.14% | Poor
U Save Botrivier | 2026-05-01 | 2205.5 | 4596.503 | 47.98% | Poor
U Save Botrivier | 2026-06-01 | 1921.8 | 3907.6063 | 49.18% | Poor
Three Peaks | 2026-07-01 | 3037 | 2765.4183 | 109.8% | Expected | NO
U Save Botrivier | 2026-08-01 | 4145 | 4689.3484 | 88.39% | Moderate | NO
Shoprite Ekhaya | 2026-09-01 | 20723.3362 | 23750.386 | 87.25% | Moderate | NO
U Save Botrivier | 2026-10-01 |  | 6435.8315
U Save Botrivier | 2026-11-01 |  | 6753.1048
U Save Botrivier | 2026-12-01 |  | 7227.0297
Watt Place Rotoflo | 2024-01-01 | 17892 | 27902.4846 | 64.12% | Poor
Watt Place Rotoflo | 2024-02-01 | 15929 | 23732.7941 | 67.12% | Poor
Watt Place Rotoflo | 2024-03-01 | 18524 | 24008.6276 | 77.16% | Moderate
Watt Place Rotoflo | 2024-04-01 | 13076 | 19918.4948 | 65.65% | Poor
Watt Place Rotoflo | 2024-05-01 | 17640 | 18892.4367 | 93.37% | Expected
Watt Place Rotoflo | 2024-06-01 | 14642 | 16928.2901 | 86.49% | Moderate
Watt Place Rotoflo | 2024-07-01 | 15002 | 18749.7515 | 80.01% | Moderate
Watt Place Rotoflo | 2024-08-01 | 20792 | 21877.7338 | 95.04% | Expected
Watt Place Rotoflo | 2024-09-01 | 20898 | 24302.8242 | 85.99% | Moderate
Watt Place Rotoflo | 2024-10-01 | 30325 | 26992.0189 | 112.3% | Expected
Watt Place Rotoflo | 2024-11-01 | 27930 | 26696.2399 | 104.6% | Expected
Watt Place Rotoflo | 2024-12-01 | 17653 | 28713.2181 | 61.48% | Poor
Watt Place Rotoflo | 2025-01-01 | 23957 | 27706.7675 | 86.47% | Moderate
Watt Place Rotoflo | 2025-02-01 | 19898 | 23566.3246 | 84.43% | Moderate
Watt Place Rotoflo | 2025-03-01 | 18434 | 23840.6818 | 77.32% | Moderate
Watt Place Rotoflo | 2025-04-01 | 16717 | 19779.1604 | 84.52% | Moderate
Watt Place Rotoflo | 2025-05-01 | 19518 | 18760.2798 | 104% | Expected
Watt Place Rotoflo | 2025-06-01 | 16703.9 | 16809.8728 | 99.37% | Expected
Watt Place Rotoflo | 2025-07-01 | 17442.42 | 18618.5927 | 93.68% | Expected
Watt Place Rotoflo | 2025-08-01 | 21419 | 21724.6941 | 98.59% | Expected
Watt Place Rotoflo | 2025-09-01 | 19487 | 24132.8205 | 80.75% | Moderate
Watt Place Rotoflo | 2025-10-01 | 25859.04 | 26803.2036 | 96.48% | Expected
Watt Place Rotoflo | 2025-11-01 | 23228 | 26509.4937 | 87.62% | Moderate
Watt Place Rotoflo | 2025-12-01 | 13257 | 28512.3627 | 46.5% | Poor
Watt Place Rotoflo | 2026-01-01 | 24628 | 27512.9524 | 89.51% | Moderate
Watt Place Rotoflo | 2026-02-01 | 24848.5 | 23401.4729 | 106.2% | Expected
Watt Place Rotoflo | 2026-03-01 | 20359 | 23673.9109 | 86% | Moderate
Watt Place Rotoflo | 2026-04-01 | 17480.97 | 19640.8007 | 89% | Moderate
Watt Place Rotoflo | 2026-05-01 | 17505.34 | 18629.0475 | 93.97% | Expected
Watt Place Rotoflo | 2026-06-01 | 11655 | 16692.284 | 69.82% | Poor
TPF Foods | 2026-07-01 | 2200.69 | 2994.7017 | 73.49% | Moderate | NO
Watt Place Rotoflo | 2026-08-01 | 18697 | 21572.725 | 86.67% | Moderate | NO
Shoprite Naledi | 2026-09-01 | 15845.86 | 18063.713 | 87.72% | Moderate | NO
Watt Place Rotoflo | 2026-10-01 |  | 26615.7091
Watt Place Rotoflo | 2026-11-01 |  | 26324.0538
Watt Place Rotoflo | 2026-12-01 |  | 28312.9122
Zwartop Golf Course | 2024-01-01
Zwartop Golf Course | 2024-02-01
Zwartop Golf Course | 2024-03-01
Zwartop Golf Course | 2024-04-01
Zwartop Golf Course | 2024-05-01
Zwartop Golf Course | 2024-06-01
Zwartop Golf Course | 2024-07-01
Zwartop Golf Course | 2024-08-01
Zwartop Golf Course | 2024-09-01
Zwartop Golf Course | 2024-10-01
Zwartop Golf Course | 2024-11-01
Zwartop Golf Course | 2024-12-01
Zwartop Golf Course | 2025-01-01
Zwartop Golf Course | 2025-02-01
Zwartop Golf Course | 2025-03-01
Zwartop Golf Course | 2025-04-01
Zwartop Golf Course | 2025-05-01
Zwartop Golf Course | 2025-06-01
Zwartop Golf Course | 2025-07-01
Zwartop Golf Course | 2025-08-01
Zwartop Golf Course | 2025-09-01
Zwartop Golf Course | 2025-10-01
Zwartop Golf Course | 2025-11-01
Zwartop Golf Course | 2025-12-01
Zwartop Golf Course | 2026-01-01
Zwartop Golf Course | 2026-02-01
Zwartop Golf Course | 2026-03-01
Zwartop Golf Course | 2026-04-01
Zwartop Golf Course | 2026-05-01
Zwartop Golf Course | 2026-06-01 | 0
Trouw Nutrition | 2026-07-01 | 9893.59 | 11637.4939 | 85.01% | Moderate | NO
Zwartop Golf Course | 2026-08-01 |  |  |  |  | NO
Zwartop Golf Course | 2026-09-01 |  |  |  |  | NO
Zwartop Golf Course | 2026-10-01
Zwartop Golf Course | 2026-11-01
Zwartop Golf Course | 2026-12-01
Checkers Lichtenburg | 2024-01-01 |  | 26451
Checkers Lichtenburg | 2024-02-01 |  | 23215.5
Checkers Lichtenburg | 2024-03-01 |  | 23034.6
Checkers Lichtenburg | 2024-04-01 |  | 19930.5
Checkers Lichtenburg | 2024-05-01 |  | 18754.2
Checkers Lichtenburg | 2024-06-01 |  | 16767.9
Checkers Lichtenburg | 2024-07-01 |  | 18261
Checkers Lichtenburg | 2024-08-01 |  | 21311.1
Checkers Lichtenburg | 2024-09-01 |  | 23659.2
Checkers Lichtenburg | 2024-10-01 |  | 26865.9
Checkers Lichtenburg | 2024-11-01 |  | 27153.9
Checkers Lichtenburg | 2024-12-01 |  | 27402.3
Checkers Lichtenburg | 2025-01-01 |  | 26451
Checkers Lichtenburg | 2025-02-01 |  | 23215.5
Checkers Lichtenburg | 2025-03-01 |  | 23034.6
Checkers Lichtenburg | 2025-04-01 |  | 19930.5
Checkers Lichtenburg | 2025-05-01 |  | 18754.2
Checkers Lichtenburg | 2025-06-01 |  | 16767.9
Checkers Lichtenburg | 2025-07-01 |  | 18261
Checkers Lichtenburg | 2025-08-01 |  | 21311.1
Checkers Lichtenburg | 2025-09-01 |  | 23659.2
Checkers Lichtenburg | 2025-10-01 |  | 26865.9
Checkers Lichtenburg | 2025-11-01 |  | 27153.9
Checkers Lichtenburg | 2025-12-01 |  | 27402.3
Checkers Lichtenburg | 2026-01-01 |  | 26451
Checkers Lichtenburg | 2026-02-01 |  | 23215.5
Checkers Lichtenburg | 2026-03-01 |  | 23034.6
Checkers Lichtenburg | 2026-04-01 |  | 19930.5
Checkers Lichtenburg | 2026-05-01 | 17630 | 18749.1511 | 94.03% | Expected
Checkers Lichtenburg | 2026-06-01 | 14172 | 16753.3944 | 84.59% | Moderate
U Save Botrivier | 2026-07-01 | 2292.691 | 4038.5707 | 56.77% | Poor | YES
Checkers Lichtenburg | 2026-08-01 | 19960.113 | 21267.6988 | 93.85% | Expected | NO
Mathe Group Company | 2026-09-01 | 43037.19 | 48830.273 | 88.14% | Moderate | NO
Checkers Lichtenburg | 2026-10-01 |  | 26779.7505
Checkers Lichtenburg | 2026-11-01 |  | 27050.6944
Checkers Lichtenburg | 2026-12-01 |  | 27282.4047
Alpine Heath Resort | 2024-01-01 |  | 28877.4
Alpine Heath Resort | 2024-02-01 |  | 25884.9
Alpine Heath Resort | 2024-03-01 |  | 27341.1
Alpine Heath Resort | 2024-04-01 |  | 27823.5
Alpine Heath Resort | 2024-05-01 |  | 29920.5
Alpine Heath Resort | 2024-06-01 |  | 28644.3
Alpine Heath Resort | 2024-07-01 |  | 28051.2
Alpine Heath Resort | 2024-08-01 |  | 31649.4
Alpine Heath Resort | 2024-09-01 |  | 28250.1
Alpine Heath Resort | 2024-10-01 |  | 28466.1
Alpine Heath Resort | 2024-11-01 |  | 28991.7
Alpine Heath Resort | 2024-12-01 |  | 28903.5
Alpine Heath Resort | 2025-01-01 |  | 28877.4
Alpine Heath Resort | 2025-02-01 |  | 25884.9
Alpine Heath Resort | 2025-03-01 |  | 27341.1
Alpine Heath Resort | 2025-04-01 |  | 27823.5
Alpine Heath Resort | 2025-05-01 |  | 29920.5
Alpine Heath Resort | 2025-06-01 |  | 28644.3
Alpine Heath Resort | 2025-07-01 |  | 28051.2
Alpine Heath Resort | 2025-08-01 |  | 31649.4
Alpine Heath Resort | 2025-09-01 |  | 28250.1
Alpine Heath Resort | 2025-10-01 |  | 28466.1
Alpine Heath Resort | 2025-11-01 |  | 28991.7
Alpine Heath Resort | 2025-12-01 |  | 28903.5
Alpine Heath Resort | 2026-01-01 |  | 28877.4
Alpine Heath Resort | 2026-02-01 |  | 25884.9
Alpine Heath Resort | 2026-03-01 |  | 27341.1
Alpine Heath Resort | 2026-04-01 |  | 27823.5
Alpine Heath Resort | 2026-05-01 | 27917.2 | 29918.7737 | 93.31% | Expected
Alpine Heath Resort | 2026-06-01 | 25295 | 28625.5756 | 88.37% | Moderate
Watt Place Rotoflo | 2026-07-01 | 14705 | 18488.3515 | 79.54% | Moderate | NO
Alpine Heath Resort | 2026-08-01 | 29161 | 31591.627 | 92.31% | Expected | NO
Olievenhoutbosch 2 | 2026-09-01 | 9418.8442 | 10685.3856 | 88.15% | Moderate | NO
Alpine Heath Resort | 2026-10-01 |  | 28380.8227
Alpine Heath Resort | 2026-11-01 |  | 28887.6201
Alpine Heath Resort | 2026-12-01 |  | 28783.1249
Engen Kaalfontein | 2024-01-01 |  | 17370.9
Engen Kaalfontein | 2024-02-01 |  | 15077.7
Engen Kaalfontein | 2024-03-01 |  | 14634
Engen Kaalfontein | 2024-04-01 |  | 12420
Engen Kaalfontein | 2024-05-01 |  | 11402.1
Engen Kaalfontein | 2024-06-01 |  | 9989.1
Engen Kaalfontein | 2024-07-01 |  | 10986.3
Engen Kaalfontein | 2024-08-01 |  | 13108.77
Engen Kaalfontein | 2024-09-01 |  | 14833.17
Engen Kaalfontein | 2024-10-01 |  | 17053.2
Engen Kaalfontein | 2024-11-01 |  | 17239.5
Engen Kaalfontein | 2024-12-01 |  | 17465.4
Engen Kaalfontein | 2025-01-01 |  | 17370.9
Engen Kaalfontein | 2025-02-01 |  | 15077.7
Engen Kaalfontein | 2025-03-01 |  | 14634
Engen Kaalfontein | 2025-04-01 |  | 12420
Engen Kaalfontein | 2025-05-01 |  | 11402.1
Engen Kaalfontein | 2025-06-01 |  | 9989.1
Engen Kaalfontein | 2025-07-01 |  | 10986.3
Engen Kaalfontein | 2025-08-01 |  | 13108.77
Engen Kaalfontein | 2025-09-01 |  | 14833.17
Engen Kaalfontein | 2025-10-01 |  | 17053.2
Engen Kaalfontein | 2025-11-01 |  | 17239.5
Engen Kaalfontein | 2025-12-01 |  | 17465.4
Engen Kaalfontein | 2026-01-01 |  | 17370.9
Engen Kaalfontein | 2026-02-01 |  | 15077.7
Engen Kaalfontein | 2026-03-01 |  | 14634
Engen Kaalfontein | 2026-04-01 |  | 12420
Engen Kaalfontein | 2026-05-01 |  | 11402.1
Engen Kaalfontein | 2026-06-01 | 10169 | 9986.7949 | 101.8% | Expected
Zwartop Golf Course | 2026-07-01 | 0
Engen Kaalfontein | 2026-08-01 | 14833.728 | 13090.3787 | 113.3% | Expected | YES
SR Morula TF 1 | 2026-09-01 | 6939.4893 | 7807.3861 | 88.88% | Moderate | NO
Engen Kaalfontein | 2026-10-01 |  | 17009.3082
Engen Kaalfontein | 2026-11-01 |  | 17184.88
Engen Kaalfontein | 2026-12-01 |  | 17400.022
Usave Naboomspruit | 2026-07-01 | 4094.8841 | 4643.203 | 88.19% | Moderate | NO
Usave Naboomspruit | 2026-08-01 | 4246.929 | 5249.1499 | 80.91% | Moderate | NO
Mambha Cash & Carry | 2026-09-01 | 14407.6783 | 16146.8814 | 89.23% | Moderate | NO
Usave Naboomspruit | 2026-10-01 |  | 6018.039
Usave Naboomspruit | 2026-11-01 |  | 5881.6154
Usave Naboomspruit | 2026-12-01 |  | 5969.7197

## Comments
Site Name | Date | Availability | Downtime (days) | Cause of downtime | Technical Events | Energy Impact | Other Comments
21 Melrose | 2024-09-01
21 Melrose | 2024-10-01
21 Melrose | 2024-11-01
21 Melrose | 2024-12-01
21 Melrose | 2025-01-01
21 Melrose | 2025-02-01 | Underperforming Low demand Excessive rain and cloudy weather for approx. 2 weeks -50% less production compared to Feb 2024 Avg load: Feb 2024: 200kW; Feb 2025 150-160kW
21 Melrose | 2025-03-01 | Underperforming due to Low demand System performance is >65% expected production System Performance improved by 9% compared to last month System Performance decreased by 55% compared to march 2024 System Performance affected by rain on some days
21 Melrose | 2025-04-01 | 1. Underperformance due to low demand 2. Production is 63% of expected 3. Production is 45% Compared to April 2024 4. Production is the same compared to last month
21 Melrose | 2025-05-01 | 1. Production is 102% of the expected energy. 2. Production is 16% less compared to May 2024. 3. Production is 39% more compared to last month. 4. There is no downtime on the solar, Eskom, and communication.
21 Melrose | 2025-06-01 | 1. Production is 108% of the expected energy. 2. Production is 6% less compared to June 2024. 3. Production is 6% more compared to last month. 4. There is no downtime on the solar, Eskom, and communication.
21 Melrose | 2025-07-01 | 1. Production is 96% of the expected energy. 2. Production is 10% less compared to Jul 2024. 3. Production is 12% less compared to last month. 4. There is no downtime on the solar, Eskom, and communication.
21 Melrose | 2025-08-01 | 1. Production is 76% of the expected energy. 2. Production is 6% less compared to Aug 2024. 3. Production is 20% less compared to last month. 4. System performed moderately, client loads are slightly low.
21 Melrose | 2025-09-01 | 1. Production is 60% of the expected energy. 2. Production is 146% less compared to Sep 2024. 3. Production is 16% less compared to last month. 4. System performed moderately; client load demand is low.
21 Melrose | 2025-10-01 | 1. Production is 67% of the expected energy. 2. Production is 1% more compared to Oct 2024. 3. Production is 7% more compared to last month. 4. System performed poorly; client load demand is low.
21 Melrose | 2025-11-01 | 1. Production is 61% of the expected energy. 2. Production is 20% less compared to Nov 2024. 3. Production is 3% less compared to last month. 4. System performed poorly; client load demand is low.
21 Melrose | 2025-12-01 | System performed poorly; client load demand is low.
21 Melrose | 2026-01-01 | System performed poorly; client load demand is low.
21 Melrose | 2026-02-01 | System performed poorly; client load demand is low.
21 Melrose | 2026-03-01 | System performed poorly; client load demand is low.
21 Melrose | 2026-04-01 | The system performed poorly due to load demand. The system was on bu pass from the 22nd-30th, there was a phase rotation from city power, the issue is now resolved
21 Melrose | 2026-05-01 | Performend poorly due to load demand
21 Melrose | 2026-06-01
21 Melrose | 2026-07-01 | 31 | 0 | None | None | The System performed as expected | N/A
21 Melrose | 2026-08-01 | 30 days | 0 | None | None | Energy production was limited by load demand | N/A
African Global Plastics | 2024-09-01
African Global Plastics | 2024-10-01
African Global Plastics | 2024-11-01
African Global Plastics | 2024-12-01
African Global Plastics | 2025-01-01
African Global Plastics | 2025-02-01 | Performance decreased by 25% due to rainy weather -36% lower production, compared to Feb 2024 Intermittent comms, IOT sim required
African Global Plastics | 2025-03-01 | Fix Comms - Install IoT simcard
African Global Plastics | 2025-04-01 | Fix Comms - Install IoT simcard
African Global Plastics | 2025-05-01 | 1. Production is 96% of the expected energy. 2. Production is 17% less compared to May 2024. 3. Production is 14% more compared to last month. 4. The system is performing well, monitoring platform was offline for 31 day, to install IoT sim to improve internet stability
African Global Plastics | 2025-06-01 | 1. Production is 82% of the expected energy. 2. Production is 27% less compared to Jun 2024. 3. Production is 14% less compared to last month. 4. The system is performing moderate, monitoring platform was offline for 30 days, to install IoT sim to improve internet stability
African Global Plastics | 2025-07-01 | 1. Production is 20% of the expected energy. 2. Production is 81% less compared to Jul 2024. 3. Production is 62% less compared to last month. 4. The system is performing poor. The reading are incorrect from monitoring. Billing meter is offline.
African Global Plastics | 2025-08-01 | 1. Production is 60% of the expected energy. 2. Production is 18% less compared to Aug 2024. 3. Production is 40% more compared to last month. 4. The system is performing poorly. The reading are incorrect on the billing meter.
African Global Plastics | 2025-09-01 | 1. Production is 56% of the expected energy. 2. Production is 43% less compared to Sep 2024. 3. Production is 4% less compared to last month. 4. The system is performing poorly. The system is offline, and the system needs site attendance
African Global Plastics | 2025-10-01 | 1. Production is 58% of the expected energy. 2. Production is 54% less compared to Oct 2024. 3. Production is 2% more compared to last month. 4. The system is performing poorly. The system is offline, The system was under performing due to faulty controls logger; issue was resoved. System performance should increase next month
African Global Plastics | 2025-11-01 | 1. Production is 51% of the expected energy. 2. Production is 52% less compared to Nov 2024. 3. Production is 7% less compared to last month. 4. System performed poorly. controls system has faulty software. Logger to be replaced
African Global Plastics | 2025-12-01 | System performed poorly. controls system has faulty software. Logger to be replaced
African Global Plastics | 2026-01-01 | Performed poorly due to controls malfunction
African Global Plastics | 2026-02-01 | Performed poorly due to controls' malfunction, to be fixed this month
African Global Plastics | 2026-03-01 | Performed poorly due to load demand
African Global Plastics | 2026-04-01 | Performed poorly due to load demand
African Global Plastics | 2026-05-01 | Performing poorly due to slightly reduced load demand
African Global Plastics | 2026-06-01 | 31 days | 0 | None
African Global Plastics | 2026-07-01 | 31 | 0 | None | None | Energy production was limited by reduced load demand | N/A
African Global Plastics | 2026-08-01 | 30 days | 0 | None | None | Energy production was limited by load demand | N/A
Alpine Heath Residential | 2024-09-01
Alpine Heath Residential | 2024-10-01
Alpine Heath Residential | 2024-11-01
Alpine Heath Residential | 2024-12-01
Alpine Heath Residential | 2025-01-01 | 31 days | None | None | Internet connectivity issues | Energy production was limited by reduced load demand
Alpine Heath Residential | 2025-02-01 | 28 days | None | None | Internet connectivity issues | Energy production was limited by reduced load demand
Alpine Heath Residential | 2025-03-01 | 31 days | None | None | Internet connectivity issues | Energy production was limited by reduced load demand
Alpine Heath Residential | 2025-04-01 | 30 days |  |  | Internet connectivity issues | Energy production was limited by reduced load demand
Alpine Heath Residential | 2025-05-01 | 0 | 30 |  | Internet connectivity issues | Energy production was limited by reduced load demand
Alpine Heath Residential | 2025-06-01 | 26 days | 4 | Inverter was offline | Internet connectivity issues | Energy production was limited by reduced load demand
Alpine Heath Residential | 2025-07-01 | 0 days | 31 days | System shutdown | Technical Fault. Inverter offline due to repairs | No solar production due to technical fault
Alpine Heath Residential | 2025-08-01 | 31 days | 0 |  | None | Energy production was limited by reduced load demand
Alpine Heath Residential | 2025-09-01 | 31 days | 0 |  | None | produced as expected
Alpine Heath Residential | 2025-10-01 | 22 days | 19-27, 9 days | PV Breaker tripped | Faulty AC breakers | Energy production was limited by reduced load demand & technical event
Alpine Heath Residential | 2025-11-01 | 30 days | 0 |  | None | Energy production was limited by reduced load demand
Alpine Heath Residential | 2025-12-01 | 31 days | 0 | None | Internet connectivity issues | Energy production was limited by reduced load demand
Alpine Heath Residential | 2026-01-01 | 31 days | 0 |  | None | Low energy demand reduced production
Alpine Heath Residential | 2026-02-01 | 28 days | 0 |  | None | Energy production was limited by reduced load demand
Alpine Heath Residential | 2026-03-01 | 21 days | 21-31, 10 days | PV Breaker tripped | Faulty DC breakers | Energy production was limited by reduced load demand & technical event
Alpine Heath Residential | 2026-04-01 | 30 days | 28-30, 3 days | PV Breaker tripped | Faulty DC breakers | Energy production was limited by technical event
Alpine Heath Residential | 2026-05-01 | 31 days | 01-18, 18 days | System isolated for maintenance | Faulty DC breakers | Energy production was limited by reduced load demand & technical event
Alpine Heath Residential | 2026-06-01 | 30 days | 0 | None | None | Energy production was limited by reduced load demand | N/A
Alpine Heath Residential | 2026-07-01 | 30 | 1 day, 14th | Power outage | None | Energy production was limited by reduced load demand and weather | N/A
Alpine Heath Residential | 2026-08-01 | 30 days | 0 | None | None | Energy production was limited by load demand | N/A
Alpine Heath Resort | 2026-07-01 | 31 | 0 | None | None | The system performed as expected | N/A
Alpine Heath Resort | 2026-06-01 | 30 days | 0 | None | None | The energy production was limited by load demand & bad weather | N/A
Alpine Heath Resort | 2024-09-01
Alpine Heath Resort | 2024-10-01
Alpine Heath Resort | 2024-11-01
Alpine Heath Resort | 2024-12-01
Alpine Heath Resort | 2025-01-01
Alpine Heath Resort | 2025-02-01
Alpine Heath Resort | 2025-03-01
Alpine Heath Resort | 2025-04-01
Alpine Heath Resort | 2025-05-01
Alpine Heath Resort | 2025-06-01
Alpine Heath Resort | 2025-07-01 | 31 days | N/A | N/A | N/A | N/A | system not commissioned
Alpine Heath Resort | 2025-08-01 | 31 days | N/A | N/A | N/A | N/A | system not commissioned
Alpine Heath Resort | 2025-09-01 | 30 days | N/A | N/A | N/A | N/A | system not commissioned
Alpine Heath Resort | 2025-10-01 | 31 days | N/A | N/A | N/A | N/A | system not commissioned
Alpine Heath Resort | 2025-11-01 | 30 days | N/A | N/A | N/A | N/A | system not commissioned
Alpine Heath Resort | 2025-12-01 | 31 days | N/A | N/A | N/A | N/A | system not commissioned
Alpine Heath Resort | 2026-01-01 | 31 days | N/A | N/A | N/A | N/A | system not commissioned
Alpine Heath Resort | 2026-02-01 | 28 days | N/A | N/A | N/A | N/A | system not commissioned
Alpine Heath Resort | 2026-03-01 | 31 days | N/A | N/A | N/A | N/A | system not commissioned
Alpine Heath Resort | 2026-04-01 | 2 days | 01-28, 28 days | system not commissioned | None | None | N/A
Alpine Heath Resort | 2026-05-01 | 31 days | None | None | None | There system produced as expected | N/A
Alpine Heath Resort | 2026-08-01 | 30 days | 0 | None | None | The system performed as expected | N/A
Bendstore Plaza Shops | 2024-09-01 | Client Load Demand went Lower than Installed Capacity
Bendstore Plaza Shops | 2024-10-01
Bendstore Plaza Shops | 2024-11-01
Bendstore Plaza Shops | 2024-12-01
Bendstore Plaza Shops | 2025-01-01
Bendstore Plaza Shops | 2025-02-01 | Fluctuating loads Load demand lower as of Jan 2024 Production lower than expected simulated production but improved from prior year by 10-15%. Due to increased ramp rate settings. Rainy weather affected Feb performance
Bendstore Plaza Shops | 2025-03-01 | Fluctuating loads Load demand lower as of Jan 2024 System performance is >80% expected production Performance improved by 1% compared to last month Performance Improved by 4,2% compared to march 2024 Performance affected by rain on some days
Bendstore Plaza Shops | 2025-04-01 | 1. Fuctuating load & Reduced 2. Production is 62% of expected energy 3. Production is 7% less Compared to April 2024 4. Production is 20% less compared to last month 5. Loadscheding for three days
Bendstore Plaza Shops | 2025-05-01 | 1. Production is 67% of the expected energy. 2. Production is 7% less compared to May 2024. 3. Production is 5% more compared to last month. 4. Production is in line with historical production, High fluctuating loads and Reduced. There was 3 times comms loss and 1-time grid loss.
Bendstore Plaza Shops | 2025-06-01 | 1. Production is 70% of the expected energy. 2. Production is 6% less compared to Jun 2024. 3. Production is 3% more compared to last month. 4. The system is performing moderate, monitoring platform was offline for 2 days.
Bendstore Plaza Shops | 2025-07-01 | 1. Production is 69% of the expected energy. 2. Production is 7% less compared to Jul 2024. 3. Production is 1% less compared to last month. 4. The system is performing poorly, monitoring platform was offline for 5 days. Days: 8th ,9th ,10th, 30th, 31th
Bendstore Plaza Shops | 2025-08-01 | 1. Production is 70% of the expected energy. 2. Production is 9% more compared to Aug 2024. 3. Production is 1% more compared to last month. 4. The system is performing modaretly. Load demand is modarate.
Bendstore Plaza Shops | 2025-09-01 | 1. Production is 56% of the expected energy. 2. Production is 162% more compared to Sep 2024. 3. Production is 14% less compared to last month. 4. The system is performing poorly. There was no PV production for 5 for 5 days (25th -30th), monitoring is offline
Bendstore Plaza Shops | 2025-10-01 | 1. Production is 61% of the expected energy. 2. Production is 27% less compared to Oct 2024. 3. Production is 5% More compared to last month. 4. The system is performing poorly. There was not producing pv from 1 Oct - 7 Oct due to PV String poor insulation and a fault alarm, that issue has been resolved and the system is working well.
Bendstore Plaza Shops | 2025-11-01 | 1. Production is 71% of the expected energy. 2. Production is 20% less compared to Nov 2024. 3. Production is 10% More compared to last month. 4. The system performed moderately. Client loads are moderate.
Bendstore Plaza Shops | 2025-12-01 | System performed well
Bendstore Plaza Shops | 2026-01-01 | System performed moderatly due to reduced demand
Bendstore Plaza Shops | 2026-02-01 | The system is performing moderately, reduced demand and affected by rainy weather .
Bendstore Plaza Shops | 2026-03-01 | Performed poorly due to load demand
Bendstore Plaza Shops | 2026-04-01 | Performed poorly due to load demand
Bendstore Plaza Shops | 2026-05-01 | Performend poorly due to load demand
Bendstore Plaza Shops | 2026-06-01
Bendstore Plaza Shops | 2026-07-01 | 31 | 0 | None | None | Energy production was limited by reduced load demand | N/A
Bendstore Plaza Shops | 2026-08-01 | 30 days | 0 | None | None | Energy production was limited by load demand | N/A
Bendstore Spar | 2024-09-01
Bendstore Spar | 2024-10-01
Bendstore Spar | 2024-11-01
Bendstore Spar | 2024-12-01
Bendstore Spar | 2025-01-01
Bendstore Spar | 2025-02-01 | Performing well, >90% efficiency Feb 2025 production slightly less than Feb 2024 due to rainy weather
Bendstore Spar | 2025-03-01 | Performing well, >90% efficiency Improved performance by 1,1% compared to last month Performance increased by 11% compared to March 2024 To Install a Monitoring system.
Bendstore Spar | 2025-04-01 | 1. Billing meter was offline for 2 days in April 2. Production is 66% of expected energy 3. Production is 22% less compared to April 2024 4. Production is 28% less compared to last month 5. To install Monitoring platform 6. Power Outage for tree days
Bendstore Spar | 2025-05-01 | 1. Production is 77% of the expected energy. 2. Production is 12% less compared to May 2024. 3. Production is 11% more compared to last month. 4. The no monitoring platform to identify the decreas in energy production. Monitoring platform will be installed during 0&M ,
Bendstore Spar | 2025-06-01 | 1. Production is 73% of the expected energy. 2. Production is 16% less compared to Jun 2024. 3. Production is 4% less compared to last month. 4. The system is performing moderate, The is no monitoring platform (30 days offline). System needs intervansion to improve performance.
Bendstore Spar | 2025-07-01 | 1. Production is 65% of the expected energy. 2. Production is 27% less compared to Jul 2024. 3. Production is 8% less compared to last month. 4. The system is performing moderate, The is no monitoring platform (31 days offline). System needs intervansion to improve performance.
Bendstore Spar | 2025-08-01 | 1. Production is 64% of the expected energy. 2. Production is 20% less compared to Aug 2024. 3. Production is 1% less compared to last month. 4. The system is performing poorly. Monitoring platform is added, comms currently offline due to nertwork issues. Monitoring offline from 21 Aug - 31 Aug.
Bendstore Spar | 2025-09-01 | 1. Production is 91% of the expected energy. 2. Production is 17% more compared to Sep 2024. 3. Production is 27% more compared to last month. 4. System performed as expected.
Bendstore Spar | 2025-10-01 | 1. Production is 114% of the expected energy. 2. Production is 12% more compared to Oct 2024. 3. Production is 23% more compared to last month. 4. System performed more than expected.
Bendstore Spar | 2025-11-01 | 1. Production is 96% of the expected energy. 2. Production is 8% less compared to Nov 2024. 3. Production is 18% less compared to last month. 4. System performed well.
Bendstore Spar | 2025-12-01 | System performed well
Bendstore Spar | 2026-01-01 | The system performed as expected
Bendstore Spar | 2026-02-01 | System performed well
Bendstore Spar | 2026-03-01 | The performed moderately
Bendstore Spar | 2026-04-01 | The performed moderately
Bendstore Spar | 2026-05-01 | There is no monitoring onsite
Bendstore Spar | 2026-06-01
Bendstore Spar | 2026-07-01 | 31 | 0 | None | None | The System performed as expected | N/A
Bendstore Spar | 2026-08-01 | 30 days | 0 | None | None | The system performed as expected | N/A
Beyerskloof | 2024-09-01
Beyerskloof | 2024-10-01
Beyerskloof | 2024-11-01
Beyerskloof | 2024-12-01
Beyerskloof | 2025-01-01
Beyerskloof | 2025-02-01 | Assessment required Improved performance from 2024
Beyerskloof | 2025-03-01 | One Inverter stopped producing from the 13th Feb - 07 March Billing meter reading incorrectly Rain affect Power Cut - 4
Beyerskloof | 2025-04-01 | Billing meter reading incorrectly
Beyerskloof | 2025-05-01 | 1. Production is 57% of the expected energy. 2. Production is 9% less compared to May 2024. 3. Production is 5% more compared to last month. 4. The system is performing poorly, the evening cycling is not yet implemented.
Beyerskloof | 2025-06-01 | 1. Production is 45% of the expected energy. 2. Production is 34% less compared to Jun 2024. 3. Production is 12% less compared to last month. 4. The system is performing poorly, the battery cycling should be set up to increase daily load demand
Beyerskloof | 2025-07-01 | 1. Production is 52% of the expected energy. 2. Production is 31% less compared to Jul 2024. 3. Production is 7% more compared to last month. 4. The system is performing poorly, the battery cycling should be adjusted to increase daily load
Beyerskloof | 2025-08-01 | 1. Production is 77% of the expected energy. 2. Production is 3% less compared to Aug 2024. 3. Production is 25% more compared to last month. 4. The system performed moderately, issues are resolved, More performance improvement expected.
Beyerskloof | 2025-09-01 | 1. Production is 96% of the expected energy. 2. Production is 231% more compared to Sep 2024. 3. Production is 19% more compared to last month. 4. System performed as expected.
Beyerskloof | 2025-10-01 | 1. Production is 94% of the expected energy. 2. Production is 29% more compared to Oct 2024. 3. Production is 2% less compared to last month. 4. System performed as expected.
Beyerskloof | 2025-11-01 | 1. Production is 99% of the expected energy. 2. Production is 88% more compared to Nov 2024. 3. Production is 7% more compared to last month. 4. System performed as expected.
Beyerskloof | 2025-12-01 | System performed well
Beyerskloof | 2026-01-01 | The system performed as expected
Beyerskloof | 2026-02-01 | The system is performing moderately, reduced demand and affected by rainy weather .
Beyerskloof | 2026-03-01 | The system performed as expected
Beyerskloof | 2026-04-01 | Performed as expected
Beyerskloof | 2026-05-01 | Performed as expected
Beyerskloof | 2026-06-01
Beyerskloof | 2026-07-01 | 31 | 0 | None | None | The System performed as expected | N/A
Beyerskloof | 2026-08-01 | 30 days | 0 | None | None | The system performed as expected | N/A
BP Parys | 2024-09-01
BP Parys | 2024-10-01
BP Parys | 2024-11-01
BP Parys | 2024-12-01
BP Parys | 2025-01-01
BP Parys | 2025-02-01 | Low load demand, 15-20kW avg System performing as expected due to low loads
BP Parys | 2025-03-01 | Rain Load Demand Low
BP Parys | 2025-04-01 | Load Demand Low
BP Parys | 2025-05-01 | 1. Production is 65% of the expected energy. 2. Production is 6% more compared to last month. 3. There was a power outage for 1 day, client load is lower than the system installed
BP Parys | 2025-06-01 | 1. Production is 50% of the expected energy. 2. Production is 15% less compared to last month. 4. The system comms went ofline for 8 days, client load demand is lower than the system installed.
BP Parys | 2025-07-01 | 1. Production is 40% of the expected energy. 2. Production is 10% less compared to last month. 4. The system is performing poorly due to low load demand
BP Parys | 2025-08-01 | 1. Production is 15% of the expected energy. 2. Production is 25% less compared to last month. 4. Inverter reading has 10 days (10/08/25-31/08/25) of missing data (actual reading should be higher), the system has been operational regardless of comms being offline on the monitoring, and the comms are online again.
BP Parys | 2025-09-01 | 1. Production is 28% of the expected energy. 2. Production is 13% more compared to last month. 4. The system produced poorly due to reduced load demand
BP Parys | 2025-10-01 | 1. Production is 40% of the expected energy. 2. Production is 12% more compared to last month. 4. The system produced poorly due to reduced load demand
BP Parys | 2025-11-01 | 1. Production is 20% of the expected energy. 2. Production is 20% less compared to last month. 4. The system produced poorly due to reduced load demand
BP Parys | 2025-12-01 | The system produced poorly due to business closure
BP Parys | 2026-01-01 | The system produced poorly due to business closure
BP Parys | 2026-02-01 | The system is performing moderately, reduced demand and affected by rainy weather .
BP Parys | 2026-03-01 | Performed poorly due to load demand
BP Parys | 2026-04-01 | Performed poorly due to load demand
BP Parys | 2026-05-01 | Performend poorly due to load demand
BP Parys | 2026-08-01 | 26 days | 4 days, 8-10, 26th | The inverter went to safe mode | Grid over frequency | Energy production was limited by load demand and downtimes | N/A
BP Parys | 2026-06-01
BP Parys | 2026-07-01 | 31 | 0 | None | None | Energy production was limited by reduced load demand | N/A
Buffalo Rock | 2024-09-01
Buffalo Rock | 2024-10-01
Buffalo Rock | 2024-11-01
Buffalo Rock | 2024-12-01
Buffalo Rock | 2025-01-01
Buffalo Rock | 2025-02-01 | Monitoring offline, need to improve comms, add IOT No performance data
Buffalo Rock | 2025-03-01 | Monitoring offline, need to improve comms, add IOT No performance data
Buffalo Rock | 2025-04-01 | Monitoring offline, need to improve comms, add IOT No performance data
Buffalo Rock | 2025-05-01 | Monitoring offline, need to improve comms, add IOT No performance data
Buffalo Rock | 2025-06-01 | Monitoring offline, need to improve comms, add IOT No performance data
Buffalo Rock | 2025-07-01 | Monitoring offline, need to improve comms, add IOT No performance data
Buffalo Rock | 2025-08-01 | Monitoring offline, need to improve comms, add IOT No performance data
Buffalo Rock | 2025-09-01 | System comms are restored toward the end of the month, monlthy perfomance to evaluted from next month
Buffalo Rock | 2025-10-01 | 1. Production is 58% of the expected energy. 2. Production is 10% more compared to last Oct year 2024. 4. The system produced poorly due to reduced load demand
Buffalo Rock | 2025-11-01 | System went offline
Buffalo Rock | 2025-12-01 | System went offline
Buffalo Rock | 2026-01-01 | System went offline
Buffalo Rock | 2026-02-01 | System went offline
Buffalo Rock | 2026-03-01 | System went offline
Buffalo Rock | 2026-04-01 | System went offline
Buffalo Rock | 2026-05-01 | No Monitoring onsite
Buffalo Rock | 2026-08-01 | 30 days | 0 | None | Battery cell imbalance | Energy production was limited by load demand | N/A
Buffalo Rock | 2026-06-01
Buffalo Rock | 2026-07-01 | 31 | 0 | None | None | Energy production was limited by reduced load demand | N/A
Checkers De Aar | 2024-09-01
Checkers De Aar | 2024-10-01
Checkers De Aar | 2024-11-01
Checkers De Aar | 2024-12-01
Checkers De Aar | 2025-01-01
Checkers De Aar | 2025-02-01 | Performing well Performing 10% higher than expected
Checkers De Aar | 2025-03-01 | Rain Load Reduction
Checkers De Aar | 2025-04-01 | 1. System performing well 2. Production is 98% of expected energy
Checkers De Aar | 2025-05-01 | 1. Production is 113% of the expected energy. 2. Production is 11% more compared to last month. 3. The system is performing as expected. No power outage, no comms loss, PV production loss.
Checkers De Aar | 2025-06-01 | 1. Production is 105% of the expected energy. 2. Production is 21% more compared to Jun 2024. 3. Production is 8% less compared to last month. 4. The system is performing as expected. No power outage, no comms loss, no PV production loss.
Checkers De Aar | 2025-07-01 | 1. Production is 97% of the expected energy. 2. Production is 7% more compared to Jul 2024. 3. Production is 8% less compared to last month. 4. The system is performing as expected. No power outage, no comms loss, no PV production loss.
Checkers De Aar | 2025-08-01 | 1. Production is 99% of the expected energy. 2. Production is 13% less compared to Aug 2024. 3. Production is 4% more compared to last month. 4. The system is performing as expected. No power outage, no comms loss, no PV production loss.
Checkers De Aar | 2025-09-01 | 1. Production is 99% of the expected energy. 2. Production is 8% less compared to Sep 2024. 3. Production is the same compared to last month. 4. The system is performing as expected.
Checkers De Aar | 2025-10-01 | 1. Production is 107% of the expected energy. 2. Production is 8% more compared to Oct 2024. 3. Production is 8% more compared to last month. 4. The system performed more than expected.
Checkers De Aar | 2025-11-01 | 1. Production is 103% of the expected energy. 2. Production is 8% less compared to Nov 2024. 3. Production is 4% less compared to last month. 4. The system performed more than expected.
Checkers De Aar | 2025-12-01 | No PV production on the 14th, System performed well
Checkers De Aar | 2026-01-01 | The system performed as expected
Checkers De Aar | 2026-02-01 | System performed well
Checkers De Aar | 2026-03-01 | System performed well
Checkers De Aar | 2026-04-01 | Performed as expected
Checkers De Aar | 2026-05-01 | Performed as expected
Checkers De Aar | 2026-08-01 | 26 days | 4 days, 1-4th | client contractor tempered with the system | Zero export CT were swapped in the wrong direction | Energy production was limited by technical downtime, and heavily soiled panels | N/A
Checkers De Aar | 2026-06-01
Checkers De Aar | 2026-07-01 | 24 | 7 days, 24-31st | client contractor tempered with the system | Zero export CT were swapped in the wrong direction | Energy production was limited by technical downtime, and heavily soiled panels | N/A
Checkers Lichtenburg | 2026-07-01 | 31 | 0 | None | None | The system performed as expected | N/A
Checkers Lichtenburg | 2026-06-01
Checkers Lichtenburg | 2026-05-01 | Performed as expected
Checkers Lichtenburg | 2026-08-01 | 30 days | 0 | None | None | The system performed as expected | N/A
21 Melrose | 2026-09-01 | 30 | 0 | None | None | Energy production was limited by load demand | N/A
Checkers Lichtenburg | 2026-10-01
Checkers Lichtenburg | 2026-11-01
Checkers Lichtenburg | 2026-12-01
Checkers Silverlakes Gen | 2024-09-01
Checkers Silverlakes Gen | 2024-10-01
Checkers Silverlakes Gen | 2024-11-01
Checkers Silverlakes Gen | 2024-12-01
Checkers Silverlakes Gen | 2025-01-01
Checkers Silverlakes Gen | 2025-02-01 | Commissioned March
Checkers Silverlakes Gen | 2025-03-01 | 1. System performing well 2. Monitoring platform false reporting offline due to communication issue
Checkers Silverlakes Gen | 2025-04-01 | 1. System performing well 2. Monitoring platform false reporting offline due to communication issue 3. Production is 99% expected energy
Checkers Silverlakes Gen | 2025-05-01 | 1. Production is 128% of the expected energy. 2. Production is 29% more compared to last month. 3. The system is performing more than expected. No power outage, no comms loss, PV production loss.
Checkers Silverlakes Gen | 2025-06-01 | 1. Production is 103% of the expected energy. 2. Production is 24% less compared to last month. 3. The system is performing more than expected. No power outage, comms offline for 1 day, PV off for 1 day, grid outage for 1 day.
Checkers Silverlakes Gen | 2025-07-01 | 1. Production is 100% of the expected energy. 2. Production is 3% less compared to last month. 3. The system is performing well.
Checkers Silverlakes Gen | 2025-08-01 | 1. Production is 111% of the expected energy. 2. Production is 11% more compared to last month. 3. The system is performing well.
Checkers Silverlakes Gen | 2025-09-01 | 1. Production is 96% of the expected energy. 2. Production is 7% less compared to last month. 3. The system is performing well.
Checkers Silverlakes Gen | 2025-10-01 | 1. Production is 108% of the expected energy. 2. Production is 12% more compared to last month. 3. The system performed more than expected
Checkers Silverlakes Gen | 2025-11-01 | 1. Production is 84% of the expected energy. 2. Production is 24% less compared to last month. 3. The system performed well. Production reduced to rainy weather
Checkers Silverlakes Gen | 2025-12-01 | System performed well
Checkers Silverlakes Gen | 2026-01-01 | System performed as expected
Checkers Silverlakes Gen | 2026-02-01 | System performed well
Checkers Silverlakes Gen | 2026-03-01 | System performed well
Checkers Silverlakes Gen | 2026-04-01 | Performed as expected
Checkers Silverlakes Gen | 2026-05-01 | Performed as expected
Checkers Silverlakes Gen | 2026-08-01 | 30 days | 0 | None | None | The system performed as expected | N/A
Checkers Silverlakes Gen | 2026-06-01
Checkers Silverlakes Gen | 2026-07-01 | 31 | 0 | None | None | The System performed as expected | N/A
Checkers Silverlakes No Gen | 2024-09-01
Checkers Silverlakes No Gen | 2024-10-01
Checkers Silverlakes No Gen | 2024-11-01
Checkers Silverlakes No Gen | 2024-12-01
Checkers Silverlakes No Gen | 2025-01-01
Checkers Silverlakes No Gen | 2025-02-01 | Commissioned March
Checkers Silverlakes No Gen | 2025-03-01 | 1. System performing well 2. Monitoring platform false reporting offline due communication issue
Checkers Silverlakes No Gen | 2025-04-01 | 1. Sysstem performing well 2. Monitoring platform false reporting offline due to communication issue 3. Production is 87% expected energy
Checkers Silverlakes No Gen | 2025-05-01 | 1. Production is 107% of the expected energy. 2. Production is 20% more compared to last month. 3. The system is performing more than expected. No power outage, no comms loss, PV production loss.
Checkers Silverlakes No Gen | 2025-06-01 | 1. Production is 77% of the expected energy. 2. Production is 30% less compared to last month. 3. The system performed moderately, Load demand reduced compared to last month. Comms off for 3 days, 1 day grid outage, 3 days PV not producing.
Checkers Silverlakes No Gen | 2025-07-01 | 1. Production is 75% of the expected energy. 2. Production is 2% less compared to last month. 3. The system performed moderately, Load demand reduced compared to last month.
Checkers Silverlakes No Gen | 2025-08-01 | 1. Production is 89% of the expected energy. 2. Production is 14% more compared to last month. 3. The system performed well.
Checkers Silverlakes No Gen | 2025-09-01 | 1. Production is 65% of the expected energy. 2. Production is 24% less compared to last month. 3. The system performed poorly due to load demand inconsistency.
Checkers Silverlakes No Gen | 2025-10-01 | 1. Production is 99% of the expected energy. 2. Production is 36% more compared to last month. 3. The system performed as expected
Checkers Silverlakes No Gen | 2025-11-01 | 1. Production is 75% of the expected energy. 2. Production is 24% less compared to last month. 3. The system performed moderately. Client load was reduced on some days, and rainy weather affected performance
Checkers Silverlakes No Gen | 2025-12-01 | No PV production from 11-14th; 16-19th
Checkers Silverlakes No Gen | 2026-01-01 | System performed as expected
Checkers Silverlakes No Gen | 2026-02-01 | System performed well
Checkers Silverlakes No Gen | 2026-03-01 | System performed moderately due to bad weather days
Checkers Silverlakes No Gen | 2026-04-01 | Performed as expected
Checkers Silverlakes No Gen | 2026-05-01 | Performed as expected
Checkers Silverlakes No Gen | 2026-08-01 | 30 days | 0 | None | None | The system performed as expected | N/A
Checkers Silverlakes No Gen | 2026-06-01
Checkers Silverlakes No Gen | 2026-07-01 | 31 | 0 | None | None | The System performed as expected | N/A
Checkrite Inanda | 2024-09-01
Checkrite Inanda | 2024-10-01
Checkrite Inanda | 2024-11-01
Checkrite Inanda | 2024-12-01
Checkrite Inanda | 2025-01-01
Checkrite Inanda | 2025-02-01 | Perfomance reduced significantly to rain and intermittent power outages January performance was as expected
Checkrite Inanda | 2025-03-01 | Load-Reduced by almost half since February. Hence solar production reduced
Checkrite Inanda | 2025-04-01 | Load-Reduced by almost half since February. Hence solar production reduced
Checkrite Inanda | 2025-05-01 | 1. Production is 65% of the expected energy. 2. Production is 13% less compared to last month. 3. The system underperformed due to faulty due to 4 strings not producing because of faulty circuit breakers. The client electrition swapped one Grid CT the wrong way around. The system has been fixed. The was a power outage for 1 day.
Checkrite Inanda | 2025-06-01 | 1. Production is 115% of the expected energy. 2. Production is 50% more compared to last month. 3. System is performing as expected
Checkrite Inanda | 2025-07-01 | 31 days |  |  |  | The System is performed as expected | N/A
Checkrite Inanda | 2025-08-01 | 31 days | 0 | None | None | The System is performed as expected | N/A
Checkrite Inanda | 2025-09-01 | 30 days | 0 | None | None | Energy production was limited by reduced load demand | N/A
Checkrite Inanda | 2025-10-01 | 31 days | 0 | None | None | Energy production was limited by reduced load demand | N/A
Checkrite Inanda | 2025-11-01 | 30 days | 0 | None | None | Energy production was limited by reduced load demand | N/A
Checkrite Inanda | 2025-12-01 | 31 days | 0 | None | None | The System is performed as expected | N/A
Checkrite Inanda | 2026-01-01 | 31 days | 0 | None | None | Energy production was limited by reduced load demand | N/A
Checkrite Inanda | 2026-02-01 | 28 days | 0 | None | 4 strings disconnected | System underperformed due to technical fault experienced onsite. Expected February production corrected due to technical fault. | N/A
Checkrite Inanda | 2026-03-01 | 31 days | 0 | None | 4 strings disconnected | System underperformed due to technical fault experienced onsite. Expected February production corrected due to technical fault. | N/A
Checkrite Inanda | 2026-04-01 | 30 days | 0 | None | None | The System is performed as expected | N/A
Checkrite Inanda | 2026-05-01 | 31 days | 0 | None | None | The System is performed as expected | N/A
Checkrite Inanda | 2026-08-01 | 30 days | 0 | None | None | The system performed as expected | N/A
Checkrite Inanda | 2026-06-01 | 30 days | 0 | None | None | The System is performed as expected | N/A
Checkrite Inanda | 2026-07-01 | 31 | 0 | None | None | The system performed as expected | N/A
Club Houghton | 2024-09-01
Club Houghton | 2024-10-01
Club Houghton | 2024-11-01
Club Houghton | 2024-12-01
Club Houghton | 2025-01-01
Club Houghton | 2025-02-01 | Reduced load demand compared to 2024 Reduced production due to rainy weather Inline with historic performance
Club Houghton | 2025-03-01 | System performance > 65% expected production System production increased by 4.8% compared to last month System production decreased by 8,8% compared to March 2024 Reduced load demand compared to 2024 Reduced production due to rainy weather Inline with historic performance
Club Houghton | 2025-04-01 | 1. Load demand is low 2. Production is 57% of expected energy 3. Production is 33% less compared to April 2024 4. Production is 11% less compared to last month
Club Houghton | 2025-05-01 | 1. Production is 77% of the expected energy. 2. Production is 5% less compared to May 2024. 3. Production is 20% more compared to last month. 4. System production reduced due to load being reduced
Club Houghton | 2025-06-01 | 1. Production is 76% of the expected energy. 2. Production is 9% less compared to May 2024. 3. Production is 1% less compared to last month. 4. System production reduced due to load being reduced
Club Houghton | 2025-07-01 | 1. Production is 65% of the expected energy. 2. Production is 36% less compared to Jul 2024. 3. Productions 11% less compared to last month. 4. System production reduced due to load being reduced
Club Houghton | 2025-08-01 | 1. Production is 47% of the expected energy. 2. Production is 47% less compared to Aug 2024. 3. Productions 18% less compared to last month. 4. System production reduced poorly due to long hours power outages. The system was on bypass: 2025/08/01-2025/08/06 and 2025/08/24 - 2025/08/27
Club Houghton | 2025-09-01 | 1. Production is 50% of the expected energy. 2. Production is 32% less compared to Sep 2024. 3. Productions 3% more compared to last month. 4. The system performed poorly due to load demand
Club Houghton | 2025-10-01 | 1. Production is 53% of the expected energy. 2. Production is 26% less compared to Oct 2024. 3. Productions 3% more compared to last month. 4. The system performed poorly due to load demand
Club Houghton | 2025-11-01 | 1. Production is 42% of the expected energy. 2. Production is 40% less compared to Nov 2024. 3. Productions 11% less compared to last month. 4. The system performed poorly due to load demand. There was grid maintenance sytsem was placed on bypass by onsite maintance technician
Club Houghton | 2025-12-01 | System performed poorly, one inveter is faulty and needs maintanance
Club Houghton | 2026-01-01 | System performed poorly, one inveter is faulty and needs maintanance
Club Houghton | 2026-02-01 | System performed poorly, one inveter is faulty and needs maintanance
Club Houghton | 2026-03-01 | System performed poorly due to low load demand
Club Houghton | 2026-04-01 | The system performed poorly due to load demand. The system was on bu pass from the 24nd - 27th, there was a phase rotation from city power, the issue is now resolved
Club Houghton | 2026-05-01 | Performend poorly due to load demand
Club Houghton | 2026-08-01 | 30 | 0 | None | None | Energy production was limited by load demand | N/A
Club Houghton | 2026-06-01
Club Houghton | 2026-07-01 | 31 | 0 | None | None | The system performed as expected | N/A
Coldstar International | 2024-09-01
Coldstar International | 2024-10-01
Coldstar International | 2024-11-01
Coldstar International | 2024-12-01
Coldstar International | 2025-01-01
Coldstar International | 2025-02-01 | Performance affected by rainy weather Reduced load demand Unable to check export settings as comms are offline Awaiting tech to attend site Requires further investigation
Coldstar International | 2025-03-01 | Performance is > 80% Expected production Performance improved by 6% compared to last month Performance affected by rainy weather Reduced load demand Awaiting tech to attend site (not urgent) Requires further investigation
Coldstar International | 2025-04-01 | 1. Load is reduced, no solar production for 4 days 2. Production is 53% of expected energy 3. Production is 29% less compared to last month 4. Technician to attend site
Coldstar International | 2025-05-01 | 1. Production is 91% of the expected energy 2. Production is 38% more compared to last month 3. System performed well, there is was no grid power loss, PV shutdown, and communication loss.
Coldstar International | 2025-06-01 | 1. Production is 91% of the expected energy. 2. Production is 12% less compared to Jun 2024. 3. Production is the same compared to last month. 4. The system is performing well . No power outage, no comms loss, no PV production loss.
Coldstar International | 2025-07-01 | 1. Production is 108% of the expected energy. 2. Production is 62% less compared to Jul 2024. 3. Production is 17% more compared to last month. 4. The system is performing well . No power outage, no comms loss, no PV production loss.
Coldstar International | 2025-08-01 | 1. Production is 110% of the expected energy. 2. Production is 116% more compared to Aug 2024. 3. Production is 2% more compared to last month. 4. The system is performing well . No power outage, no comms loss, no PV production loss.
Coldstar International | 2025-09-01 | 1. Production is 103% of the expected energy. 2. Production is 31% more compared to Sep 2024. 3. Production is 7% less compared to last month. 4. The system is performing well . No power outage, no comms loss, no PV production loss.
Coldstar International | 2025-10-01 | 1. Production is 103% of the expected energy. 2. Production is 31% more compared to Sep 2024. 3. Production is 16% more compared to last month. 4. The system performed more than expected
Coldstar International | 2025-11-01 | 1. Production is 128% of the expected energy. 2. Production is 42% more compared to Nov 2024. 3. Production is 15% more compared to last month. 4. The system performed more than expected
Coldstar International | 2025-12-01 | System performed well
Coldstar International | 2026-01-01 | The system performed as expected
Coldstar International | 2026-02-01 | System performed well
Coldstar International | 2026-03-01 | System performed well
Coldstar International | 2026-04-01 | Performed as expected
Coldstar International | 2026-05-01 | Performed as expected
Coldstar International | 2026-08-01 | 30 days | 0 | None | None | The system performed as expected | N/A
Coldstar International | 2026-06-01
Coldstar International | 2026-07-01 | 31 | 0 | None | None | The system performed as expected | N/A
Cultura Fresh | 2024-09-01
Cultura Fresh | 2024-10-01
Cultura Fresh | 2024-11-01
Cultura Fresh | 2024-12-01
Cultura Fresh | 2025-01-01
Cultura Fresh | 2025-02-01
Cultura Fresh | 2025-03-01
Cultura Fresh | 2025-04-01
Cultura Fresh | 2025-05-01
Cultura Fresh | 2025-06-01
Cultura Fresh | 2025-07-01
Cultura Fresh | 2025-08-01
Cultura Fresh | 2025-09-01
Cultura Fresh | 2025-10-01
Cultura Fresh | 2025-11-01 | 1. Production is 106% of the expected energy. 2. Production is 5% less compared to last month. 4. The system is performing well.
Cultura Fresh | 2025-12-01 | The system if performing well
Cultura Fresh | 2026-01-01 | The system performed as expected
Cultura Fresh | 2026-02-01 | System performed well
Cultura Fresh | 2026-03-01 | System performed well
Cultura Fresh | 2026-04-01 | No recorded monthly readings
Cultura Fresh | 2026-05-01 | Monitoring system is not working properly
Cultura Fresh | 2026-08-01 | N/A | N/A | N/A | N/A | N/A | Comms issue
Cultura Fresh | 2026-06-01
Cultura Fresh | 2026-07-01 | 31 | 0 | None | Unreliable monitoring platform | N/A | N/A
Demco | 2024-09-01 | Client Demand very low on Friday and weekends, soiling
Demco | 2024-10-01 | Client Demand very low on Friday and weekends, Load reduction genset kit now serving its purpose
Demco | 2024-11-01
Demco | 2024-12-01
Demco | 2025-01-01
Demco | 2025-02-01 | Fluctuating loads, system slightly oversized Closure Friday 12:00 - Sunday, reduce expected utilisation Rainy weather further reduced performance Tariff adjustment required as no expectation of improved performance
Demco | 2025-03-01 | Fluctuating loads, system slightly oversized Rainy weather further reduced performance Tariff adjustment required as no expectation of improved performance
Demco | 2025-04-01 | Fluctuating loads, system slightly oversized Rainy weather further reduced performance Tariff adjustment required as no expectation of improved performance
Demco | 2025-05-01 | 1. Production is 61% of the expected energy. 2. Production is 21% more compared to last month. 3. The system is performing poorly due to Fluctuating loads, system slightly oversized. Tariff adjustment required as no expectation of improved performance
Demco | 2025-06-01 | 1. Production is 69% of the expected energy. 2. Production is 8% more compared to last month. 3. The system is performing poorly maily due to low demand. The system was offline, with no PV Production for 9 days (days: 7, 8, 14, 15, 16, 22, 27, 25, 29).
Demco | 2025-07-01 | 31 days | 0 | None | None | Energy production was limited by reduced load demand | N/A
Demco | 2025-08-01 | 31 days | 0 | None | None | Energy production was limited by reduced load demand | N/A
Demco | 2025-09-01 | 29 days | 0 | None | None | Energy production was limited by reduced load demand | N/A
Demco | 2025-10-01 | 31 days | 0 | None | None | Energy production was limited by reduced load demand | N/A
Demco | 2025-11-01 | 29 days | 0 | None | None | Energy production was limited by reduced load demand, cloudy and rainy weather. | N/A
Demco | 2025-12-01 | 18 days | 13 - 31, 13 days | Company closure | None | Energy production was limited due to load demand | N/A
Demco | 2026-01-01 | 10 days | 21-31, 10 days | Power outages & low load demand | grid failure on low demand | Energy production was limited due to load demand | N/A
Demco | 2026-02-01 | 3 days | 1-3, 3 days | Power outages & low load demand | grid failure on low demand | Performed poorly due to reduced loads,and frequent power cuts during the day, and bad weather | N/A
Demco | 2026-03-01 | 31 days | 0 | None | None | Energy production was limited by reduced load demand | N/A
Demco | 2026-04-01 | 30 days | 0 | None | None | Energy production was limited by reduced load demand | N/A
Demco | 2026-05-01 | 31 days | 0 | None | None | Energy production was limited by reduced load demand | N/A
Demco | 2026-08-01 | 30 days | 0 | None | None | Energy production was limited by load demand | N/A
Demco | 2026-06-01 | 30 days | 0 | None | None | Energy production was limited by reduced load demand | N/A
Demco | 2026-07-01 | 31 | 0 | None | None | Energy production was limited by reduced load demand | N/A
Engen Kaalfontein | 2026-06-01 | 30 days | 0 | N/A | None | None | N/A
Engen Kaalfontein | 2026-07-01 | 18 | 13 days,8-21st | Inverter software | Unknown | Energy production is limited by system unavailability and soiling | N/A
Engen Kaalfontein | 2024-09-01
Engen Kaalfontein | 2024-10-01
Engen Kaalfontein | 2024-11-01
Engen Kaalfontein | 2024-12-01
Engen Kaalfontein | 2025-01-01
Engen Kaalfontein | 2025-02-01
Engen Kaalfontein | 2025-03-01
Engen Kaalfontein | 2025-04-01
Engen Kaalfontein | 2025-05-01
Engen Kaalfontein | 2025-06-01
Engen Kaalfontein | 2025-07-01 | N/A | N/A | N/A | N/A | N/A | system not commissioned
Engen Kaalfontein | 2025-08-01 | N/A | N/A | N/A | N/A | N/A | system not commissioned
Engen Kaalfontein | 2025-09-01 | N/A | N/A | N/A | N/A | N/A | system not commissioned
Engen Kaalfontein | 2025-10-01 | N/A | N/A | N/A | N/A | N/A | system not commissioned
Engen Kaalfontein | 2025-11-01 | N/A | N/A | N/A | N/A | N/A | system not commissioned
Engen Kaalfontein | 2025-12-01 | N/A | N/A | N/A | N/A | N/A | system not commissioned
Engen Kaalfontein | 2026-01-01 | N/A | N/A | N/A | N/A | N/A | system not commissioned
Engen Kaalfontein | 2026-02-01 | N/A | N/A | N/A | N/A | N/A | system not commissioned
Engen Kaalfontein | 2026-03-01 | N/A | N/A | N/A | N/A | N/A | system not commissioned
Engen Kaalfontein | 2026-04-01 | N/A | N/A | N/A | N/A | N/A | system not commissioned
Engen Kaalfontein | 2026-05-01 | 8 days | 1-23, 23 days | system not commissioned | N/A | N/A
Engen Kaalfontein | 2026-08-01 | 30 days | 0 | None | None | The system performed as expected | N/A
Engen Lotus Gardens | 2024-09-01
Engen Lotus Gardens | 2024-10-01
Engen Lotus Gardens | 2024-11-01
Engen Lotus Gardens | 2024-12-01
Engen Lotus Gardens | 2025-01-01
Engen Lotus Gardens | 2025-02-01
Engen Lotus Gardens | 2025-03-01
Engen Lotus Gardens | 2025-04-01
Engen Lotus Gardens | 2025-05-01
Engen Lotus Gardens | 2025-06-01
Engen Lotus Gardens | 2025-07-01 | 31 days | N/A | N/A | N/A | N/A | The system is not commissioned
Engen Lotus Gardens | 2025-08-01 | 31 days | N/A | N/A | N/A | N/A | The system is not commissioned
Engen Lotus Gardens | 2025-09-01 | 30 days | N/A | N/A | N/A | N/A | The system is not commissioned
Engen Lotus Gardens | 2025-10-01 | 31 days | N/A | N/A | N/A | N/A | The system is not commissioned
Engen Lotus Gardens | 2025-11-01 | 30 days | 0 | None | None | The system performed as expected | N/A
Engen Lotus Gardens | 2025-12-01 | 31 days | 0 | None | None | The system performed as expected | N/A
Engen Lotus Gardens | 2026-01-01 | 31 days | 0 | None | None | The system performed as expected | N/A
Engen Lotus Gardens | 2026-02-01 | 28 days | 0 | None | None | The system performed as expected | N/A
Engen Lotus Gardens | 2026-03-01 | 31 days | 0 | None | None | The system performed as expected | N/A
Engen Lotus Gardens | 2026-04-01 | 30 days | 0 | None | None | Performed as expected | N/A
Engen Lotus Gardens | 2026-05-01 | 31 days | 0 | None | None | Performed as expected | N/A
Engen Lotus Gardens | 2026-08-01 | 30 days | 0 | None | None | The system performed as expected | N/A
Engen Lotus Gardens | 2026-06-01 | 30 days | 0 | None | None | The system performed as expected | N/A
Engen Lotus Gardens | 2026-07-01 | 31 | 0 | None | Inverter Internet connectivity | The system performed as expected | N/A
Giba Gorge Main | 2024-09-01
Giba Gorge Main | 2024-10-01
Giba Gorge Main | 2024-11-01
Giba Gorge Main | 2024-12-01
Giba Gorge Main | 2025-01-01
Giba Gorge Main | 2025-02-01 | System was offline from Dec-Feb being repaired, System fully operation as of March 2025
Giba Gorge Main | 2025-03-01 | The system started producing on the 5th of March Load demand is low and inconsistent
Giba Gorge Main | 2025-04-01 | 1. Monitoring platform false reporting 2. Load demand reduced 3. Performance reduced
Giba Gorge Main | 2025-05-01 | 1. Production is 61% of the expected energy. 2. Production is 20% less compared to May 2024. 3. Production is 25% more compared to last month. 4. The system is performing poorly due to a reduced client load demand. The system lost comms for 3 days.
Giba Gorge Main | 2025-06-01 | 1. Production is 60% of the expected energy. 2. Production is 17% less compared to May 2024. 3. Production is 1% less compared to last month. 4. The system is performing poorly due to a reduced client load demand. The system lost comms for 4 days (days: 15,16,17,10)
Giba Gorge Main | 2025-07-01 | 1. Production is 69% of the expected energy. 2. Production is 40% less compared to Jul 2024. 3. Production is 9% more compared to last month. 4. The system is performing poorly due to a reduced client load demand. The system lost comms for 6 days (days: 23-28).
Giba Gorge Main | 2025-08-01 | 1. Production is 72% of the expected energy. 2. Production is 31% less compared to Aug 2024. 3. Production is 3% more compared to last month. 4. The system performed moderately. Loads are slightly low.
Giba Gorge Main | 2025-09-01 | 1. Production is 64% of the expected energy. 2. Production is 18% less compared to Sep 2024. 3. Production is 8% less compared to last month. 4. The system performed poorly. Loads are slightly low.
Giba Gorge Main | 2025-10-01 | 1. Production is 81% of the expected energy. 2. Production is 23% less compared to Oct 2024. 3. Production is 17% more compared to last month. 4. The system performed moderately. Load demand is reduced.
Giba Gorge Main | 2025-11-01 | 1. Production is 76% of the expected energy. 2. Production is 63% more compared to Nov 2024. 3. Production is 5% less compared to last month. 4. The system performed moderately. Load demand is reduced.
Giba Gorge Main | 2025-12-01 | The system performed poorly due to the company closure
Giba Gorge Main | 2026-01-01 | Performed poorly due to reduced loads, client loads aore sometimes zero
Giba Gorge Main | 2026-02-01 | Performed poorly due to reduced loads, client loads aore sometimes zero, EPM might be faulty
Giba Gorge Main | 2026-03-01 | The system performed poorly due to broken inverters
Giba Gorge Main | 2026-04-01 | The system performed poorly due to broken inverters
Giba Gorge Main | 2026-05-01 | The system is broken, the inverter to be replaced
Giba Gorge Main | 2026-08-01 | 30 days | 0 | None | None | Energy production was limited by load demand | N/A
Giba Gorge Main | 2026-06-01
Giba Gorge Main | 2026-07-01 | 31 | 0 | None | Inverter Internet connectivity | Energy production was limited by reduced load demand | N/A
Giba Gorge Storage | 2024-09-01
Giba Gorge Storage | 2024-10-01
Giba Gorge Storage | 2024-11-01
Giba Gorge Storage | 2024-12-01
Giba Gorge Storage | 2025-01-01
Giba Gorge Storage | 2025-02-01 | Performance affected by rainy weather Fluctuating loads Low load demand Inline with historic performance
Giba Gorge Storage | 2025-03-01 | Fluctuating loads Low load demand Inline with historic performance
Giba Gorge Storage | 2025-04-01 | 1. Fluctuating loads 2. Low load demand 3. System underperformed
Giba Gorge Storage | 2025-05-01 | 1. Production is 60% of the expected energy. 2. Production is 25% more compared to May 2024. 3. Production is 24% more compared to last month. 4. The system is performing poorly due to a reduced client load demand.
Giba Gorge Storage | 2025-06-01 | 1. Production is 44% of the expected energy. 2. Production is 1% more compared to May 2024. 3. Production is 16% less compared to last month. 4. The system is performing poorly due to a reduced client load demand. The comms and pv was off for 9 days (Days: 12,13,14,15,16,17,22,28,29)
Giba Gorge Storage | 2025-07-01 | 1. Production is 66% of the expected energy. 2. Production is 5% less compared to Jul 2024. 3. Production is 22% more compared to last month. 4. The system is performing poorly due to a reduced client load demand.
Giba Gorge Storage | 2025-08-01 | 1. Production is 20% of the expected energy. 2. Production is 61% less compared to Aug 2024. 3. Production is 46% more compared to last month. 4. The recorded reading on the sheet is incorrect. The readings from PNP Scada are 3283 kwh + August's new modem recorded data = Correct August reading. I am not sure where the 1766,10 kwh reading is coming from. I will align with the team to fix it
Giba Gorge Storage | 2025-09-01 | 1. Production is 50% of the expected energy. 2. Production is 14% more compared to Sep 2024. 3. Production is 30% more compared to last month. 4. The system performed poorly due to low load demand.
Giba Gorge Storage | 2025-10-01 | 1. Production is 62% of the expected energy. 2. Production is 291% more compared to Oct 2024. 3. Production is 12% more compared to last month. 4. The system performed poorly due to low demand.
Giba Gorge Storage | 2025-11-01 | 1. Production is 62% of the expected energy. 2. Production is 9% more compared to Nov 2024. 3. Production is the same compared to last month. 4. The system performed poorly due to low demand.
Giba Gorge Storage | 2025-12-01 | The system performed poorly due to the company closure
Giba Gorge Storage | 2026-01-01 | Performed poorly due to reduced loads
Giba Gorge Storage | 2026-02-01 | Performed poorly due to reduced loads
Giba Gorge Storage | 2026-03-01 | Performed poorly due to reduced loads
Giba Gorge Storage | 2026-04-01 | Performed poorly due to reduced loads
Giba Gorge Storage | 2026-05-01 | Performend poorly due to load demand
Giba Gorge Storage | 2026-08-01 | 30 days | 0 | None | None | Energy production was limited by load demand | N/A
Giba Gorge Storage | 2026-06-01
Giba Gorge Storage | 2026-07-01 | 31 | 0 | None | Inverter Internet connectivity | Energy production was limited by reduced load demand | N/A
Golden Spot Resort | 2024-09-01 | Load Demand sometimes is very low
Golden Spot Resort | 2024-10-01 | Load Demand sometimes is very low
Golden Spot Resort | 2024-11-01
Golden Spot Resort | 2024-12-01
Golden Spot Resort | 2025-01-01
Golden Spot Resort | 2025-02-01 | Performance affeccted due to rain Fluctuating load Low load demand Affected by power outages in the area
Golden Spot Resort | 2025-03-01 | Fluctuating load Low load demand Billing meter is offline PV was not production from 22/03/2025 - 28/03/2025
Golden Spot Resort | 2025-04-01 | 1. Fluctuating load 2. Low load demand 3. The billing meter is offline
Golden Spot Resort | 2025-05-01 | 1. Production is 78% of the expected energy. 2. Production is 22% more compared to May 2024. 3. Production is 28% more compared to last month. 4. The system is performing moderately due to a reduced client load demand. No power outage, no comms loss, no PV production loss.
Golden Spot Resort | 2025-06-01 | 1. Production is 44% of the expected energy. 2. Production is 26% less compared to Jun 2024. 3. Production is 34% less compared to last month. 4. Wrong readings recorded, system was offline for 12 das (day: 7-19)
Golden Spot Resort | 2025-07-01 | 25 days | 26-31, 6 days | Inverter is offline | internert connection | Energy production was limited by reduced load demand | N/A
Golden Spot Resort | 2025-08-01 | 26 days | 01-05, 5 days | Inverter is offline | internert connection | Energy production was limited by reduced load demand | N/A
Golden Spot Resort | 2025-09-01 | 30 days | None | None | None | Energy production was limited by reduced load demand | N/A
Golden Spot Resort | 2025-10-01 | 15 days | 03-19, 16 days | Inverter is offline | internert connection | Energy production was limited by reduced load demand | N/A
Golden Spot Resort | 2025-11-01 | 30 days | 0 | None | None | Energy production was limited by reduced load demand | N/A
Golden Spot Resort | 2025-12-01 | 30 days | 1 day | Company closure | None | Energy production was limited by reduced load demand | N/A
Golden Spot Resort | 2026-01-01 | 31 days | 0 | None | None | Energy production was limited by reduced load demand | N/A
Golden Spot Resort | 2026-02-01 | 28 days | 0 | None | None | Energy production was limited by reduced load demand | N/A
Golden Spot Resort | 2026-03-01 | 8 days | 01-23, 23 days | Inverter is offline | internert connection | Energy production was limited by reduced load demand | N/A
Golden Spot Resort | 2026-04-01 | 30 days | 0 | None | None | Energy production was limited by reduced load demand
Golden Spot Resort | 2026-05-01 | 0 days | 01-31, 31 days | Inverter is offline | internert connection | The system monitoring is offline
Golden Spot Resort | 2026-08-01 | 30 days | 0 | None | None | Energy production was limited by load demand | N/A
Golden Spot Resort | 2026-06-01 | 30 days | 0 | None | Ineternet connectivity | The energy production was limited by load demand & bad weather | N/A
Golden Spot Resort | 2026-07-01 | 31 | 0 | None | None | Energy production was limited by reduced load demand | Daytime load demand reduced further
Golden Spot Shops | 2024-09-01
Golden Spot Shops | 2024-10-01
Golden Spot Shops | 2024-11-01
Golden Spot Shops | 2024-12-01
Golden Spot Shops | 2025-01-01
Golden Spot Shops | 2025-02-01 | Performance affeccted due to rain Fluctuating load Low load demand Affected by power outages in the area
Golden Spot Shops | 2025-03-01 | System performed well
Golden Spot Shops | 2025-04-01 | System performed well
Golden Spot Shops | 2025-05-01 | 1. Production is 115% of the expected energy. 2. Production is 9% more compared to May 2024. 3. Production is 25% more compared to last month. 4. The system is performing well. No power outage, no comms loss,no PV production loss.
Golden Spot Shops | 2025-06-01 | 1. Production is 112% of the expected energy. 2. Production is 10% more compared to Jun 2024. 3. Production is 3% less compared to last month. 4. The system is performing well. No power outage, no comms loss,no PV production loss.
Golden Spot Shops | 2025-07-01 | 31 days | 0 | None | None | The system performed as expected | N/A
Golden Spot Shops | 2025-08-01 | 26 days | 05-31 days | System is offline | internert connection | There is no energy production for ofline days | N/A
Golden Spot Shops | 2025-09-01 | 30 days | 0 | None | None | The system performed as expected | N/A
Golden Spot Shops | 2025-10-01 | 31 days | 0 | None | None | The system performed as expected | N/A
Golden Spot Shops | 2025-11-01 | 30 days | 0 | None | None | The system performed as expected | N/A
Golden Spot Shops | 2025-12-01 | 31 days | 0 | None | None | The system performed as expected | N/A
Golden Spot Shops | 2026-01-01 | 31 days | 0 | None | None | The system performed as expected | Data needs to be extracted locally onsite, recorded data is missing
Golden Spot Shops | 2026-02-01 | 28 days | 0 | None | None | The system performed as expected | N/A
Golden Spot Shops | 2026-03-01 | 31 days | 0 | None | None | Energy production was limited by reduced load demand | N/A
Golden Spot Shops | 2026-04-01 | 30 days | 0 | None | None | Energy production was limited by reduced load demand | N/A
Golden Spot Shops | 2026-05-01 | 31 days | 0 | None | None | The system performed as expected | N/A
Golden Spot Shops | 2026-08-01 | 0 | 30 | The system is switched off as per client request | None | N/A | N/A
Golden Spot Shops | 2026-07-01 | 17 | 14 days, 8-10,15-17,21-31st | System switched off | None | Energy production was limited by system beign switched off. | Client system switched off as per their requirements
Golden Spot Shops | 2026-06-01 | 30 days | 0 | None | None | The system performed as expected | N/A
Grootpan | 2024-09-01
Grootpan | 2024-10-01
Grootpan | 2024-11-01
Grootpan | 2024-12-01
Grootpan | 2025-01-01
Grootpan | 2025-02-01
Grootpan | 2025-03-01
Grootpan | 2025-04-01
Grootpan | 2025-05-01
Grootpan | 2025-06-01
Grootpan | 2025-07-01
Grootpan | 2025-08-01
Grootpan | 2025-09-01
Grootpan | 2025-10-01
Grootpan | 2025-11-01
Grootpan | 2025-12-01
Grootpan | 2026-01-01
Grootpan | 2026-02-01
Grootpan | 2026-03-01 | First month of commisioning
Grootpan | 2026-04-01 | System performed as expected
Grootpan | 2026-05-01 | Performend poorly due to load demand
Grootpan | 2026-08-01 | 30 days | 0 | None | None | Energy production was limited by load demand | N/A
Grootpan | 2026-06-01
Grootpan | 2026-07-01 | 31 | 0 | None | None | Energy production was limited by reduced load demand | N/A
HB Dunn | 2024-09-01
HB Dunn | 2024-10-01
HB Dunn | 2024-11-01
HB Dunn | 2024-12-01
HB Dunn | 2025-01-01
HB Dunn | 2025-02-01 | Performance affected by rainy weather Performing as expected
HB Dunn | 2025-03-01
HB Dunn | 2025-04-01
HB Dunn | 2025-05-01 | 1. Production is 115% of the expected energy. 2. Production is 21% more compared to last month. 3. The system is performing well.
HB Dunn | 2025-06-01 | 1. Production is 106% of the expected energy. 2. Production is 76% more compared to Jun 2024. 3. Production is 9% less compared to last month. 4. The system is performing well. No power outage, no comms loss,no PV production loss.
HB Dunn | 2025-07-01 | 1. Production is 92% of the expected energy. 2. Production is 10% more compared to Jul 2024. 3. Production is 12% less compared to last month. 4. The system is performing well. No power outage, no comms loss,no PV production loss.
HB Dunn | 2025-08-01 | 1. Production is 94% of the expected energy. 2. Production is 18% more compared to Jul 2024. 3. Production is 2% more compared to last month. 4. The system is performing well. No power outage, no comms loss,no PV production loss.
HB Dunn | 2025-09-01 | 1. Production is 79% of the expected energy. 2. Production is 15% more compared to Sep 2024. 3. Production is 15% more compared to last month. 4. The system is performing moderately; production is affected by load demand
HB Dunn | 2025-10-01 | 1. Production is 90% of the expected energy. 2. Production is 1% more compared to Oct 2024. 3. Production is 11% more compared to last month. 4. The system performed well as expected.
HB Dunn | 2025-11-01 | 1. Production is 69% of the expected energy. 2. Production is 18% less compared to Nov 2024. 3. Production is 21% less compared to last month. 4. The system is performing poorly due to reduced load demand
HB Dunn | 2025-12-01 | System is offline
HB Dunn | 2026-01-01 | System is offline
HB Dunn | 2026-02-01 | System performed well
HB Dunn | 2026-03-01 | The system performed moderately due to slightly reducded loads
HB Dunn | 2026-04-01 | The system performed moderately due to slightly reducded loads
HB Dunn | 2026-05-01 | The system is decommisioned
HB Dunn | 2026-08-01 | 30 days | 0 | None | None | Energy production was limited by load demand | N/A
HB Dunn | 2026-06-01
HB Dunn | 2026-07-01 | 31 | 0 | None | None | Energy production was limited by reduced load demand | N/A
Helderberg Collage | 2024-09-01
Helderberg Collage | 2024-10-01
Helderberg Collage | 2024-11-01
Helderberg Collage | 2024-12-01
Helderberg Collage | 2025-01-01
Helderberg Collage | 2025-02-01 | Performance reduced due to one inverter being oflfine and one currently damaged Damaged inverter awaiting techs to attend to site Offline inverter awaiting action upon feedback from management
Helderberg Collage | 2025-03-01 | 1. Two inverters offline 2. No monitoring
Helderberg Collage | 2025-04-01 | 1. Two inverters offline 2. No monitoring
Helderberg Collage | 2025-05-01 | 1. Production is 49% of the expected energy. 2. Production is 7% less compared to May 2024. 3. Production is 31% less compared to last month. 4. The system is performing poorly. One inverter is switched off. The second inverter was offline for 29 days.
Helderberg Collage | 2025-06-01 | 1. Production is 50% of the expected energy. 2. Production is 21% less compared to May 2024. 3. Production is 1% more compared to last month. 4. The system is performing poorly. One inverter is switched off. Reduced load demand.
Helderberg Collage | 2025-07-01 | 1. Production is 58% of the expected energy. 2. Production is 17% more compared to May 2024. 3. Production is 8% more compared to last month. 4. The system is performing poorly. One inverter is switched off. Reduced load demand.
Helderberg Collage | 2025-08-01 | 1. Production is 64% of the expected energy. 2. Production is 8% less compared to May 2024. 3. Production is 6% less compared to last month. 4. The system is performing poorly. One inverter is switched off. Reduced load demand.
Helderberg Collage | 2025-09-01 | 1. Production is 73% of the expected energy. 2. Production is 4% less compared to Sep 2024. 3. Production is 9% more compared to last month. 4. The system is performing moderately.
Helderberg Collage | 2025-10-01 | 1. Production is 102% of the expected energy. 2. Production is 28% more compared to Oct 2024. 3. Production is 29% more compared to last month. 4. The system is performing well.
Helderberg Collage | 2025-11-01 | 1. Production is 108% of the expected energy. 2. Production is 36% more compared to Nov 2024. 3. Production is 6% more compared to last month. 4. The system is performing well.
Helderberg Collage | 2025-12-01 | System performed well
Helderberg Collage | 2026-01-01 | The system performed as expected
Helderberg Collage | 2026-02-01 | System performed well
Helderberg Collage | 2026-03-01 | System performed well
Helderberg Collage | 2026-04-01 | The system performed moderatly
Helderberg Collage | 2026-05-01 | Performing poorly due to slightly reduced load demand
Helderberg Collage | 2026-08-01 | 30 days | 0 | None | None | The system performed as expected | N/A
Helderberg Collage | 2026-06-01
Helderberg Collage | 2026-07-01 | 31 | 0 | None | None | Energy production was limited by reduced load demand | N/A
Hilston Rotoflo | 2024-09-01
Hilston Rotoflo | 2024-10-01
Hilston Rotoflo | 2024-11-01
Hilston Rotoflo | 2024-12-01
Hilston Rotoflo | 2025-01-01
Hilston Rotoflo | 2025-02-01 | Performance affected by rain 2025 performance improved from 2024 performance Expect better yield with improved weather and regurlar cleaning
Hilston Rotoflo | 2025-03-01 | Performance is > 90% expected production Performance improved by 9% compared to last month Performance improved by 0% compared to march 2024
Hilston Rotoflo | 2025-04-01 | 1. Production affected by 3 days of power outage. 2. Production is 81% of expected energy 3. Production is 13% less compared to April 2024 4. Production is 13% less compared to last month
Hilston Rotoflo | 2025-05-01 | 1. Production is 103% of the expected energy. 2. Production is 11% less compared to May 2024. 3. Production is 14% more compared to last month. 4. The system have improved and performing well.
Hilston Rotoflo | 2025-06-01 | 1. Production is 108% of the expected energy. 2. Production is 67% more compared to Jun 2024. 3. Production is 2% more compared to last month. 4. The system is performing well.
Hilston Rotoflo | 2025-07-01 | 31 days | 0 | None | None | The system performed as expected | N/A
Hilston Rotoflo | 2025-08-01 | 31 days | 0 | None | None | The system performed as expected | N/A
Hilston Rotoflo | 2025-09-01 | 30 days | 0 | None | None | The system performed as expected | N/A
Hilston Rotoflo | 2025-10-01 | 31 days | 0 | None | None | The system performed as expected | N/A
Hilston Rotoflo | 2025-11-01 | 30 days | 0 | None | None | The system performed as expected | N/A
Hilston Rotoflo | 2025-12-01 | 16 days | 16-31, 15 days | Business closure | None | The system production was limited by business closure | N/A
Hilston Rotoflo | 2026-01-01 | 27 days | 01-014, 4 days | Business closure | None | Performed moderately due to slightly reduced load and weather | N/A
Hilston Rotoflo | 2026-02-01 | 28 days | 0 | None | None | The system performed as expected | N/A
Hilston Rotoflo | 2026-03-01 | 31 days | 0 | None | None | The system performed as expected | N/A
Hilston Rotoflo | 2026-04-01 | 30 days | 0 | None | None | Performed moderately due to slightly reduced load and weather | N/A
Hilston Rotoflo | 2026-05-01 | 31 days | 0 | None | None | The system performed as expected | N/A
Hilston Rotoflo | 2026-08-01 | 30 days | 0 | None | None | The system performed as expected | N/A
Hilston Rotoflo | 2026-06-01 | 30 days | 0 | None | None | The energy production was limited by load demand & bad weather | N/A
Hilston Rotoflo | 2026-07-01 | 31 | 0 | None | None | The System performed as expected | N/A
Huis Herfsblaar | 2024-09-01
Huis Herfsblaar | 2024-10-01
Huis Herfsblaar | 2024-11-01
Huis Herfsblaar | 2024-12-01
Huis Herfsblaar | 2025-01-01
Huis Herfsblaar | 2025-02-01 | Fluctuating loads Power outages Rainy weather
Huis Herfsblaar | 2025-03-01 | 1. Grid outage: 31/03/25 2. Fluctuating load
Huis Herfsblaar | 2025-04-01 | 1. System performed well
Huis Herfsblaar | 2025-05-01 | 1. Production is 103% of the expected energy. 2. Production is 23% more compared to last month. 3. The system is performing well. There was no grid loss, comms loss and no PV loss.
Huis Herfsblaar | 2025-06-01 | 1. Production is 89% of the expected energy. 2. Production is 14% less compared to last month. 3. The system is performing well. There system lost comms and PV (days: 6,12,13)
Huis Herfsblaar | 2025-07-01 | 16 days | 15 | Technical Fault on one inverter | Inverter breaker tripped | 50% of the production reduced due to offline inverter | N/A
Huis Herfsblaar | 2025-09-01 | 30 days | 0 | None | None | The system performe well | N/A
Huis Herfsblaar | 2025-10-01 | 31 days | 0 | None | None | The system performe well | N/A
Huis Herfsblaar | 2025-11-01 | 30 days | 0 | None | None | The energy production was limited by load demand & rainy weather | N/A
Huis Herfsblaar | 2025-12-01 | 31 days | 0 | None | None | The system performe well | N/A
Huis Herfsblaar | 2026-01-01 | 31 days | 0 | None | None | The energy production was limited by load demand & bad weather | N/A
Huis Herfsblaar | 2026-02-01 | 28 days | 0 | None | None | The system performe well | N/A
Huis Herfsblaar | 2026-03-01 | 31 days | 0 | None | None | The energy production was limited by load demand & bad weather | N/A
Huis Herfsblaar | 2026-04-01 | 30 days | 0 | None | None | The energy production was limited by load demand | N/A
Huis Herfsblaar | 2026-05-01 | 31 days | 0 | None | None | The system performe well | N/A
Huis Herfsblaar | 2026-08-01 | 30 days | 0 | None | None | Energy production was limited by reduced load demand | N/A
Huis Herfsblaar | 2026-06-01 | 30 days | 0 | None | None | The energy production was limited by load demand & bad weather | N/A
Huis Herfsblaar | 2026-07-01 | 31 | 0 | None | None | The System performed as expected | N/A
IPID - Floor 4 | 2024-09-01
IPID - Floor 4 | 2024-10-01
IPID - Floor 4 | 2024-11-01
IPID - Floor 4 | 2024-12-01
IPID - Floor 4 | 2025-01-01
IPID - Floor 4 | 2025-02-01
IPID - Floor 4 | 2025-03-01
IPID - Floor 4 | 2025-04-01
IPID - Floor 4 | 2025-05-01
IPID - Floor 4 | 2025-06-01
IPID - Floor 4 | 2025-07-01 | N/A | N/A | N/A | N/A | N/A | System not commissioned
IPID - Floor 4 | 2025-08-01 | N/A | N/A | N/A | N/A | N/A | System not commissioned
IPID - Floor 4 | 2025-09-01 | N/A | N/A | N/A | N/A | N/A | System not commissioned
IPID - Floor 4 | 2025-10-01 | 28 days | 01-03, 3 days | System not commissioned | None | None | System not commissioned
IPID - Floor 4 | 2025-11-01 | 30 days | 0 | None | None | None | N/A
IPID - Floor 4 | 2025-12-01 | 31 days | 0 | None | None | System performed as expected | N/A
IPID - Floor 4 | 2026-01-01 | 31 days | 0 | None | None | System performed as expected | N/A
IPID - Floor 4 | 2026-02-01 | 28 days | 0 | None | None | System performed as expected | N/A
IPID - Floor 4 | 2026-03-01 | 31 days | 0 | None | None | System performed as expected | N/A
IPID - Floor 4 | 2026-04-01 | 30 days | 0 | None | None | System performed as expected | N/A
IPID - Floor 4 | 2026-05-01 | 31 days | 0 | None | None | System performed as expected | N/A
IPID - Floor 4 | 2026-08-01 | 30 days | 0 | None | None | The system performed as expected | N/A
IPID - Floor 4 | 2026-06-01 | 30 days | 0 | None | None | The system performed as expected | N/A
IPID - Floor 4 | 2026-07-01 | 31 | 0 | None | None | The System performed as expected | N/A
IPID - Floor 6 | 2024-09-01
IPID - Floor 6 | 2024-10-01
IPID - Floor 6 | 2024-11-01
IPID - Floor 6 | 2024-12-01
IPID - Floor 6 | 2025-01-01
IPID - Floor 6 | 2025-02-01
IPID - Floor 6 | 2025-03-01
IPID - Floor 6 | 2025-04-01
IPID - Floor 6 | 2025-05-01
IPID - Floor 6 | 2025-06-01
IPID - Floor 6 | 2025-07-01 | N/A | N/A | N/A | N/A | N/A | System not commissioned
IPID - Floor 6 | 2025-08-01 | N/A | N/A | N/A | N/A | N/A | System not commissioned
IPID - Floor 6 | 2025-09-01 | N/A | N/A | N/A | N/A | N/A | System not commissioned
IPID - Floor 6 | 2025-10-01 | 28 days | 3-31, 3 days | System not commissioned | None | None | System not commissioned
IPID - Floor 6 | 2025-11-01 | 30 days | 0 | None | None |  | N/A
IPID - Floor 6 | 2025-12-01 | 31 days | 0 | None | None | Performed well | N/A
IPID - Floor 6 | 2026-01-01 | 31 days | 0 | None | None | Energy production was limited by reduced load demand | N/A
IPID - Floor 6 | 2026-02-01 | 28 days | 0 | None | None | Energy production was limited by reduced load demand | N/A
IPID - Floor 6 | 2026-03-01 | 31 days | 0 | None | None | Energy production was limited by reduced load demand | N/A
IPID - Floor 6 | 2026-04-01 | 30 days | 0 | None | None | Energy production was limited by reduced load demand | N/A
IPID - Floor 6 | 2026-05-01 | 31 days | 0 | None | None | Energy production was limited by reduced load demand | N/A
IPID - Floor 6 | 2026-08-01 | 30 days | 0 | None | None | Energy production was limited by reduced load demand | N/A
IPID - Floor 6 | 2026-07-01 | 31 | 0 | None | None | Energy production was limited by reduced load demand | N/A
IPID - Floor 6 | 2026-06-01 | 30 days | 0 | None | None | The energy production was limited by load demand & bad weather | N/A
Kool Village | 2024-09-01
Kool Village | 2024-10-01
Kool Village | 2024-11-01
Kool Village | 2024-12-01
Kool Village | 2025-01-01
Kool Village | 2025-02-01 | System performing well Slight decrease in performance as compared to 2024, mainly due to increased rain in 2025
Kool Village | 2025-03-01 | System performance is >95% expected production System decreased by 1.3% compared to last month System decreased by 16% compared to march 2024 Performance affected by rain and cloudy weather on some days To install Monitoring system
Kool Village | 2025-04-01 | 1. System is producing well 2. Production is 81% of expected energy 3. Production is 19% less compared to April 2024 4. Production is 17% less compared to last month 5. To install monitoring plartform
Kool Village | 2025-05-01 | 1. Production is 92% of the expected energy. 2. Production is 1% less compared to May 2024. 3. Production is 11% more compared to last month. 4. The is no monitoring platform onsite, the system is performing well.
Kool Village | 2025-06-01 | 1. Production is 83% of the expected energy. 2. Production is 3% less compared to May 2024. 3. Production is 24% less compared to last month. 4. The is no monitoring platform onsite, the system is performing well.
Kool Village | 2025-07-01 | 1. Production is 84% of the expected energy. 2. Production is 9% less compared to Jul 2024. 3. Production is 1% more compared to last month. 4. There is no monitoring platform onsite, the system is performing well.
Kool Village | 2025-08-01 | 1. Production is 74% of the expected energy. 2. Production is 16% less compared to Aug 2024. 3. Production is 10% less compared to last month. 4. There is no monitoring platform onsite, the system is performing modarate.
Kool Village | 2025-09-01 | 1. Production is 76% of the expected energy. 2. Production is 11% less compared to Sep 2024. 3. Production is 2% More compared to last month. 4. There is no monitoring platform onsite, the system is performing modarate.
Kool Village | 2025-10-01 | 1. Production is 92% of the expected energy. 2. Production is 16% less compared to Oct 2024. 3. Production is 16% more compared to last month. 4. The system performed well.
Kool Village | 2025-11-01 | 1. Production is 87% of the expected energy. 2. Production is 21% less compared to Nov 2024. 3. Production is 5% less compared to last month. 4. The system performed well.
Kool Village | 2025-12-01 | System performed well
Kool Village | 2026-01-01 | The system performed as expected
Kool Village | 2026-02-01 | The system is performing moderately, reduced demand and affected by rainy weather .
Kool Village | 2026-03-01 | The system is performing moderately, reduced demand and affected by rainy weather .
Kool Village | 2026-04-01 | System performed poorly due to load demand
Kool Village | 2026-05-01 | Performend poorly due to load demand
Kool Village | 2026-08-01 | 30 days | 0 | None | None | N/A | N/A
Kool Village | 2026-06-01
Kool Village | 2026-07-01 | 31 | 0 | None | 2 strings were off due to damaged fuses, No inverter monitoring | Energy production was limited by none operational strings | Installing new monitoring
Mambha Cash & Carry | 2024-09-01
Mambha Cash & Carry | 2024-10-01
Mambha Cash & Carry | 2024-11-01
Mambha Cash & Carry | 2024-12-01
Mambha Cash & Carry | 2025-01-01
Mambha Cash & Carry | 2025-02-01 | System performing as expected Rain in Feb 2025 reduced production Expect system yield to increase with improved weather
Mambha Cash & Carry | 2025-03-01 | System performance is > 90% expected production System performance increased by 13% compared to last month System performance decreased by 3,3% compared to march 2024
Mambha Cash & Carry | 2025-04-01 | 1. System performing well 2. Production is 86% of expected energy 3. Production is 13% less compared to April 2024 4. Production is 6% less compared to lasth month
Mambha Cash & Carry | 2025-05-01 | 1. Production is 119% of the expected energy. 2. Production is 10% more compared to May 2024. 3. Production is 5% more compared to last month. 4. The system is performing well, The monitoring platform is offline.
Mambha Cash & Carry | 2025-06-01 | 1. Production is 119% of the expected energy. 2. Production is 10% more compared to May 2024. 3. Production is 5% more compared to last month. 4. The system is performing well, The monitoring platform is offline.
Mambha Cash & Carry | 2025-07-01 | 1. Production is 79% of the expected energy. 2. Production is 17% less compared to Jul 2024. 3. Production is 31% less compared to last month. 4. The system performed modarate. The monitoring platform is offline.
Mambha Cash & Carry | 2025-08-01 | 1. Production is 90% of the expected energy. 2. Production is 7% less compared to Aug 2024. 3. Production is 10% more compared to last month. 4. The system performed well. The monitoring platform is offline.
Mambha Cash & Carry | 2025-09-01 | 1. Production is 71% of the expected energy. 2. Production is 1% less compared to Sep 2024. 3. Production is 19% more compared to last month. 4. The system performed moderately, in line with historic performance. The monitoring platform is offline.
Mambha Cash & Carry | 2025-10-01 | 1. Production is 87% of the expected energy. 2. Production is 13% less compared to Oct 2024. 3. Production is 16% more compared to last month. 4. The system performed well.
Mambha Cash & Carry | 2025-11-01 | 1. Production is 88% of the expected energy. 2. Production is 9% more compared to Nov 2024. 3. Production is 1% more compared to last month. 4. The system performed well.
Mambha Cash & Carry | 2025-12-01 | System performed well
Mambha Cash & Carry | 2026-01-01 | The system performed as expected
Mambha Cash & Carry | 2026-02-01 | System performed well
Mambha Cash & Carry | 2026-03-01 | The system performed as expected
Mambha Cash & Carry | 2026-04-01 | Performed as expected
Mambha Cash & Carry | 2026-05-01 | Performed as expected
Mambha Cash & Carry | 2026-08-01 | 30 days | 0 | None | None | The system performed as expected | N/A
Mambha Cash & Carry | 2026-06-01
Mambha Cash & Carry | 2026-07-01 | 31 | 0 | None | None | The System performed as expected | N/A
Mathe Group Company | 2024-09-01 | The company had no loads during maintenance in october
Mathe Group Company | 2024-10-01
Mathe Group Company | 2024-11-01
Mathe Group Company | 2024-12-01
Mathe Group Company | 2025-01-01
Mathe Group Company | 2025-02-01 | Performance affected by rainy weather Loads are back to normal Some power outages
Mathe Group Company | 2025-03-01 | System performance is > 85% Expected production System performance increased by 16% compared to last month System performance decreased by 4,1% compared to last year Customer loads are back to normal
Mathe Group Company | 2025-04-01 | 1. The System has under-performed, due to rain 2. Production is 68% of expected energy 3. Production is 28% less compared to April 204 4. Production is 19% less compared to last month
Mathe Group Company | 2025-05-01 | 1. Production is 111% of the expected energy. 2. Production is 7% more compared to May 2024. 3. Production is 21% more compared to last month. 4. There was no grid loss, comms loss and no PV loss. The system is performing well.
Mathe Group Company | 2025-06-01 | 1. Production is 98% of the expected energy. 2. Production is 11% more compared to May 2024. 3. Production is 13% less compared to last month. 4. The system is performing well. System PV was off for 3 days (Day: 10-12)
Mathe Group Company | 2025-07-01 | 1. Production is 98% of the expected energy. 2. Production is 15% less compared to Jul 2024. 3. Production is 2% less compared to last month. 4. The system is performing well.
Mathe Group Company | 2025-08-01 | 1. Production is 88% of the expected energy. 2. Production is 14% less compared to Aug 2024. 3. Production is 8% less compared to last month. 4. The system is performing well.
Mathe Group Company | 2025-09-01 | 1. Production is 81% of the expected energy. 2. Production is 2% less compared to Sep 2024. 3. Production is 7% less compared to last month. 4. The system is performing well.
Mathe Group Company | 2025-10-01 | 1. Production is 85% of the expected energy. 2. Production is 20% more compared to Oct 2024. 3. Production is 4% more compared to last month. 4. The system is performing well.
Mathe Group Company | 2025-11-01 | 1. Production is 94% of the expected energy. 2. Production is 2% less compared to Nov 2024. 3. Production is 8% more compared to last month. 4. The system is performing well.
Mathe Group Company | 2025-12-01 | No PV production from 24-26; 31-31 due to business closure
Mathe Group Company | 2026-01-01 | The system had no production between 1-5th of Jan, system sligtly underperformed
Mathe Group Company | 2026-02-01 | System performed well
Mathe Group Company | 2026-03-01 | System performed well
Mathe Group Company | 2026-04-01 | The system performed moderately due to winter shades
Mathe Group Company | 2026-05-01 | Performed as expected
Mathe Group Company | 2026-08-01 | 30 days | 0 | None | None | The system performed as expected | N/A
Mathe Group Company | 2026-06-01
Mathe Group Company | 2026-07-01 | 31 | 0 | None | None | The System performed as expected | N/A
Mdluli | 2024-09-01
Mdluli | 2024-10-01
Mdluli | 2024-11-01
Mdluli | 2024-12-01
Mdluli | 2025-01-01
Mdluli | 2025-02-01 | Assesment required System offline for a few months Full production restored Feb 2025 Expect production to improve with improved weather
Mdluli | 2025-03-01 | 1. Sustem performing well
Mdluli | 2025-04-01 | 1. System reduced performance compared to last month
Mdluli | 2025-05-01 | 1. The is no comms onsite for monitoring
Mdluli | 2025-06-01 | 1. The is no comms onsite for monitoring
Mdluli | 2025-07-01 | 31 days | 0 | None | Internet connectivity | Energy production was limited by reduced load demand | 1. The is no comms onsite for monitoring
Mdluli | 2025-08-01 | 31 days | 0 | None | Internet connectivity | The system performned as expected | 1. The is no comms onsite for monitoring
Mdluli | 2025-09-01 | 30 days | 0 | None | Internet connectivity | Energy production was limited by reduced load demand | 1. The is no comms onsite for monitoring
Mdluli | 2025-10-01 | 31 days | 0 | None | None | The system performned as expected | N/A
Mdluli | 2025-11-01 | 30 days | 0 | None | None | The system performned as expected | N/A
Mdluli | 2025-12-01 | 31 days | 0 | None | None | The system performned as expected | N/A
Mdluli | 2026-01-01 | 31 days | 0 | None | None | Energy production was limited by reduced load demand | N/A
Mdluli | 2026-02-01 | 28 days | 0 | None | None | System performed well | N/A
Mdluli | 2026-03-01 | 31 days | 0 | None | None | Energy production was limited by reduced load demand | N/A
Mdluli | 2026-04-01 | 30 days | 0 | None | None | Energy production was limited by reduced load demand | N/A
Mdluli | 2026-05-01 | 31 days | 0 | None | None | The system performned as expected | N/A
Mdluli | 2026-08-01 | 30 days | 0 | None | None | The system performed as expected | N/A
Mdluli | 2026-06-01 | 30 days | 0 | None | None | The energy production was limited by load demand & bad weather | N/A
Mdluli | 2026-07-01 | 31 | 0 | None | There is no inverter monitoring | Unknown | N/A
Medipost | 2024-09-01
Medipost | 2024-10-01
Medipost | 2024-11-01
Medipost | 2024-12-01
Medipost | 2025-01-01
Medipost | 2025-02-01
Medipost | 2025-03-01
Medipost | 2025-04-01
Medipost | 2025-05-01
Medipost | 2025-06-01
Medipost | 2025-07-01
Medipost | 2025-08-01
Medipost | 2025-09-01
Medipost | 2025-10-01
Medipost | 2025-11-01
Medipost | 2025-12-01 | PV production is capped to 125kWp
Medipost | 2026-01-01 | PV production is capped to 125kWp
Medipost | 2026-02-01 | System performed well
Medipost | 2026-03-01 | System performed well
Medipost | 2026-04-01 | Performed as expected
Medipost | 2026-05-01 | Performed as expected
Medipost | 2026-08-01 | 30 days | 0 | None | None | The system performed as expected | N/A
Medipost | 2026-06-01 | 31 | 0 | None | None | The System performed as expected | N/A
Medipost | 2026-07-01 | 31 | 0 | None | None | The System performed as expected | N/A
Meredale Heights | 2024-09-01
Meredale Heights | 2024-10-01
Meredale Heights | 2024-11-01
Meredale Heights | 2024-12-01
Meredale Heights | 2025-01-01
Meredale Heights | 2025-02-01 | Fluctuating loads Reduced load demand, assume occupancy issue Residential load pattern affecting system performance Tariff adjustment required as no expectation of improved performance
Meredale Heights | 2025-03-01 | System performance is >50% expected production System performance increased by 3.65% compared to last month System performance decreased by 25% compared to march 2024 Fluctuating loads Reduced load demand, assume occupancy issue Residential load pattern affecting system performance Tariff adjustment required as no expectation of improved performance
Meredale Heights | 2025-04-01 | 1. Load reduced compared to last year, tariff adjustment required as there is no expected improvement 2. Production is 55% of expected energy 3. Production is 30% less compared to April 2024 4. Production is 1% less compared to last month
Meredale Heights | 2025-05-01 | 1. Production is 70% of the expected energy. 2. Production is 18% less compared to May 2024. 3. Production is 15% more compared to last month. 4. Loads have reduced, on of the CTs on the zero export meter is swapped around (arrangements are made for rectification).
Meredale Heights | 2025-06-01 | 1. Production is 97% of the expected energy. 2. Production is 16% more compared to May 2024. 3. Production is 27% more compared to last month. 4. The system is performing well.
Meredale Heights | 2025-07-01 | 31 days | 0 | None | None | The system performed as expected | N/A
Meredale Heights | 2025-08-01 | 31 days | 0 | None | None | The system performed as expected | N/A
Meredale Heights | 2025-09-01 | 30 days | 0 | None | None | The system performed as expected | N/A
Meredale Heights | 2025-10-01 | 31 days | 0 | None | None | The system performed as expected | N/A
Meredale Heights | 2025-11-01 | 30 days | 0 | None | None | The system performed as expected | N/A
Meredale Heights | 2025-12-01 | 31 days | 0 | None | None | The system performed as expected | N/A
Meredale Heights | 2026-01-01 | 31 days | 0 | None | None | The system performed as expected | N/A
Meredale Heights | 2026-02-01 | 28 days | 0 | None | None | The system performed as expected | N/A
Meredale Heights | 2026-03-01 | 31 days | 0 | None | None | The system performed as expected | N/A
Meredale Heights | 2026-04-01 | 30 days | 0 | None | None | The system performed as expected | N/A
Meredale Heights | 2026-05-01 | 31 days | 0 | None | None | The system performed as expected | N/A
Meredale Heights | 2026-08-01 | 30 days | 0 | None | None | The system performed as expected | N/A
Meredale Heights | 2026-06-01 | 30 days | 0 | None | None | The system performed as expected | N/A
Meredale Heights | 2026-07-01 | 31 | 0 | None | None | The System performed as expected | N/A
Monument Park Checkers | 2024-09-01
Monument Park Checkers | 2024-10-01
Monument Park Checkers | 2024-11-01
Monument Park Checkers | 2024-12-01
Monument Park Checkers | 2025-01-01
Monument Park Checkers | 2025-02-01 | System perfoming well Reduced performance in Feb 2025 due to rainy weather
Monument Park Checkers | 2025-03-01 | System perfoming well 90%+ expected production System performance decreased by 1% compared to month System performance decreased by 23% compared to march 2024 System affected by rain on some days
Monument Park Checkers | 2025-04-01 | 1. System is performing well 2. Production is 86% of expected energy 3. Production is 1% more compared to April 2024 4. Production is 4% less compared to last month
Monument Park Checkers | 2025-05-01 | 1. Production is 117% of the expected energy. 2. Production is 18% more compared to May 2024. 3. Production is 3% more compared to last month. 4. The system is performing well as expected
Monument Park Checkers | 2025-06-01 | 1. Production is 114% of the expected energy. 2. Production is 18% more compared to May 2024. 3. Production is 4% less compared to last month. 4. The system is performing well as expected
Monument Park Checkers | 2025-07-01 | 1. Production is 83% of the expected energy. 2. Production is 24% less compared to Jul 2024. 3. Production is 3% less compared to last month. 4. The system is performed well.system monitoring was offline for 6 days,Date: 3th - 8th.
Monument Park Checkers | 2025-08-01 | 1. Production is 104% of the expected energy. 2. Production is 2% more compared to Aug 2024. 3. Production is 21% more compared to last month. 4. The system is performed 4% more than expected.
Monument Park Checkers | 2025-09-01 | 1. Production is 92% of the expected energy. 2. Production is 2% less compared to Sep 2024. 3. Production is 4% less compared to last month. 4. The system is performing well.
Monument Park Checkers | 2025-10-01 | 1. Production is 104% of the expected energy. 2. Production is 10% less compared to Oct 2024. 3. Production is 12% more compared to last month. 4. The system is performing well.
Monument Park Checkers | 2025-11-01 | 1. Production is 112% of the expected energy. 2. Production is 4% less compared to Nov 2024. 3. Production is 8% more compared to last month. 4. The system is performing well.
Monument Park Checkers | 2025-12-01 | System performed well
Monument Park Checkers | 2026-01-01 | The system performed as expected
Monument Park Checkers | 2026-02-01 | System performed well
Monument Park Checkers | 2026-03-01 | System performed well
Monument Park Checkers | 2026-04-01 | The system performed moderately
Monument Park Checkers | 2026-05-01 | Performed as expected
Monument Park Checkers | 2026-08-01 | 30 days | 0 | None | None | The system performed as expected | N/A
Monument Park Checkers | 2026-06-01
Monument Park Checkers | 2026-07-01 | 31 | 0 | None | None | The System performed as expected | N/A
n/ | 2025-08-01 | 31 days | 0 | None | None | The system performe well | N/A
Nkambeni Industrial | 2024-09-01
Nkambeni Industrial | 2024-10-01
Nkambeni Industrial | 2024-11-01
Nkambeni Industrial | 2024-12-01
Nkambeni Industrial | 2025-01-01
Nkambeni Industrial | 2025-02-01 | Expected system performance >90% efficiency Feb 2025 performance reduce due to rainy weather 2024 performance data to be added for comparison
Nkambeni Industrial | 2025-03-01
Nkambeni Industrial | 2025-04-01
Nkambeni Industrial | 2025-05-01 | 1. The comms are offline onsite
Nkambeni Industrial | 2025-06-01 | 1. The comms are offline onsite
Nkambeni Industrial | 2025-07-01 | 1. The comms are offline onsite
Nkambeni Industrial | 2025-08-01 | 1. The comms are offline onsite
Nkambeni Industrial | 2025-09-01 | 1. The comms are offline onsite
Nkambeni Industrial | 2025-10-01 | 1. The comms are offline onsite
Nkambeni Industrial | 2025-11-01 | 1. The comms are offline onsite
Nkambeni Industrial | 2025-12-01 | 1. The comms are offline onsite
Nkambeni Industrial | 2026-01-01 | 1. The comms are offline onsite
Nkambeni Industrial | 2026-02-01 | System performed well
Nkambeni Industrial | 2026-03-01 | No comms onsite, system performed poorly
Nkambeni Industrial | 2026-04-01 | No data recorded
Nkambeni Industrial | 2026-05-01 | There is no monitoring
Nkambeni Industrial | 2026-08-01
Nkambeni Industrial | 2026-06-01
Nkambeni Industrial | 2026-07-01 | 31 | 0 | None | There is no inverter monitoring | Unknown | N/A
Olievenhoutbosch 1 | 2024-09-01
Olievenhoutbosch 1 | 2024-10-01
Olievenhoutbosch 1 | 2024-11-01
Olievenhoutbosch 1 | 2024-12-01
Olievenhoutbosch 1 | 2025-01-01
Olievenhoutbosch 1 | 2025-02-01
Olievenhoutbosch 1 | 2025-03-01
Olievenhoutbosch 1 | 2025-04-01
Olievenhoutbosch 1 | 2025-05-01
Olievenhoutbosch 1 | 2025-06-01
Olievenhoutbosch 1 | 2025-07-01 | N/A | N/A | N/A | N/A | N/A | System not commissioned
Olievenhoutbosch 1 | 2025-08-01 | N/A | N/A | N/A | N/A | N/A | System not commissioned
Olievenhoutbosch 1 | 2025-09-01 | 5 days | 1-25, 25 days | System not commisssioned | None | None | N/A
Olievenhoutbosch 1 | 2025-10-01 | 31 days | 0 | None | None | None | N/A
Olievenhoutbosch 1 | 2025-11-01 | 30 days | 0 | None | None | None | N/A
Olievenhoutbosch 1 | 2025-12-01 | 25 days | 24-29, 6 days | Power outage | None | Reduced production | N/A
Olievenhoutbosch 1 | 2026-01-01 | 31 days | 0 | None | None | The system performed as expected | N/A
Olievenhoutbosch 1 | 2026-02-01 | 28 days | 0 | None | None | The system is performing moderately, reduced demand and affected by rainy weather . | N/A
Olievenhoutbosch 1 | 2026-03-01 | 31 days | 0 | None | None | The system is performing moderately, reduced demand and affected by rainy weather . | N/A
Olievenhoutbosch 1 | 2026-04-01 | 30 days | 0 | None | None | The system is performing moderately, reduced demand and affected by rainy weather . | N/A
Olievenhoutbosch 1 | 2026-05-01 | 31 days | 0 | None | None | Performed as expected | N/A
Olievenhoutbosch 1 | 2026-08-01 | 30 days | 0 | None | None | The system performed as expected | N/A
Olievenhoutbosch 1 | 2026-06-01 | 30 days | 0 | None | None | The energy production was limited by load demand & bad weather | N/A
Olievenhoutbosch 1 | 2026-07-01 | 31 | 0 | None | Offline inverter comms | Energy production was limited by soiling | Inverter comms currently offline
Olievenhoutbosch 2 | 2024-09-01
Olievenhoutbosch 2 | 2024-10-01
Olievenhoutbosch 2 | 2024-11-01
Olievenhoutbosch 2 | 2024-12-01
Olievenhoutbosch 2 | 2025-01-01
Olievenhoutbosch 2 | 2025-02-01
Olievenhoutbosch 2 | 2025-03-01
Olievenhoutbosch 2 | 2025-04-01
Olievenhoutbosch 2 | 2025-05-01
Olievenhoutbosch 2 | 2025-06-01
Olievenhoutbosch 2 | 2025-07-01 | N/A | N/A | N/A | N/A |  | System not commissioned
Olievenhoutbosch 2 | 2025-08-01 | N/A | N/A | N/A | N/A |  | System not commissioned
Olievenhoutbosch 2 | 2025-09-01 | 5 days | 1-25, 25 days | System not commisssioned | None |  | N/A
Olievenhoutbosch 2 | 2025-10-01 | 31 days | 0 | None | None | Produced as expected | N/A
Olievenhoutbosch 2 | 2025-11-01 | 30 days | 0 | None | None | Produced as expected | N/A
Olievenhoutbosch 2 | 2025-12-01 | 25 days | 24-29, 6 days | Power outage | None | Reduced production | N/A
Olievenhoutbosch 2 | 2026-01-01 | 31 days | 0 | None | None | The system performed as expected | N/A
Olievenhoutbosch 2 | 2026-02-01 | 28 days | 0 | None | None | The system is performing moderately, reduced demand and affected by rainy weather . | N/A
Olievenhoutbosch 2 | 2026-03-01 | 31 days | 0 | None | None | The system is performing moderately, reduced demand and affected by rainy weather. | N/A
Olievenhoutbosch 2 | 2026-04-01 | 30 days | 0 | None | None | The system is performing moderately, reduced demand and affected by rainy weather . | N/A
Olievenhoutbosch 2 | 2026-05-01 | 31 days | 0 | None | None | Performed as expected | N/A
Olievenhoutbosch 2 | 2026-08-01 | 30 days | 0 | None | None | The system performed as expected | N/A
Olievenhoutbosch 2 | 2026-06-01 | 30 days | 0 | None | None | The energy production was limited by load demand & bad weather | N/A
Olievenhoutbosch 2 | 2026-07-01 | 31 | 0 | None | Offline inverter comms | Energy production was limited by soiling | N/A
Opal Students | 2024-09-01
Opal Students | 2024-10-01
Opal Students | 2024-11-01
Opal Students | 2024-12-01
Opal Students | 2025-01-01
Opal Students | 2025-02-01 | Fluctuating loads Performance as expected when occupied due to university oeprational months Frequent power outages in the area
Opal Students | 2025-03-01 | System performing well Comms offline
Opal Students | 2025-04-01 | 1. System is performing well 2. Production is 81% of expected energy 3. Production is 26% less compared to April 2024 4. Production is 8% lesss compred to last month
Opal Students | 2025-05-01 | 1. Production is 109% of the expected energy. 2. Production is 5% more compared to May 2024. 3. Production is 28% more compared to last month. 4. The system is performing well.
Opal Students | 2025-06-01 | 1. Production is 104% of the expected energy. 2. Production is 20% more compared to May 2024. 3. Production is 5% less compared to last month. 4. The system is performing well.
Opal Students | 2025-07-01 | 31 days | 0 | None | None | The system performed as expected | N/A
Opal Students | 2025-08-01 | 31 days | 0 | None | None | The system performed as expected | N/A
Opal Students | 2025-09-01 | 30 days | 0 | None | None | The system performed as expected | N/A
Opal Students | 2025-10-01 | 31 days | 0 | None | None | The system performed as expected | N/A
Opal Students | 2025-11-01 | 30 days | 0 | None | None | Energy production was limited by reduced load demand | N/A
Opal Students | 2025-12-01 | 31 days | 0 | None | None | Energy production was limited by reduced load demand | N/A
Opal Students | 2026-01-01 | 31 days | 0 | None | None | System performed poorly due to no occupation | N/A
Opal Students | 2026-02-01 | 28 days | 0 | None | None | The system performed as expected | N/A
Opal Students | 2026-03-01 | 31 days | 0 | None | None | The system performed as expected | N/A
Opal Students | 2026-04-01 | 30 days | 0 | None | None | The system performed as expected | N/A
Opal Students | 2026-05-01 | 31 days | 0 | None | None | The system performed as expected | N/A
Opal Students | 2026-08-01 | 30 days | 0 | None | None | The system performed as expected | N/A
Opal Students | 2026-06-01 | 30 days | 0 | None | None | The energy production was limited by load demand & bad weather | N/A
Opal Students | 2026-07-01 | 31 | 0 | None | None | The System performed as expected | N/A
Orthochem Bethlehem | 2024-09-01
Orthochem Bethlehem | 2024-10-01
Orthochem Bethlehem | 2024-11-01
Orthochem Bethlehem | 2024-12-01
Orthochem Bethlehem | 2025-01-01
Orthochem Bethlehem | 2025-02-01 | Performing well, efficicieny >90% Performance affected by rainy weather and power outages
Orthochem Bethlehem | 2025-03-01 | System performed well
Orthochem Bethlehem | 2025-04-01 | 1. System affected by weather & load reduced on some days
Orthochem Bethlehem | 2025-05-01 | 1. Production is 82% of the expected energy. 2. Production is 9% more compared to May 2024. 3. Production is 12% more compared to last month. 4. The system is performing moderately. No power outage, no comms loss, no PV production loss.
Orthochem Bethlehem | 2025-06-01 | 1. Production is 77% of the expected energy. 2. Production is 10% more compared to May 2024. 3. Production is 5% less compared to last month. 4. The system is performing moderately. Reduced load demand for 6 days (days: 7,8,9,14,15,16)
Orthochem Bethlehem | 2025-07-01 | 1. Production is 74% of the expected energy. 2. Production is 4% less compared to Jul 2024. 3. Production is 3% less compared to last month. 4. The system is performing moderately.
Orthochem Bethlehem | 2025-08-01 | 1. Production is 73% of the expected energy. 2. Production is 4% less compared to Aug 2024. 3. Production is 1% more compared to last month. 4. The system is performing moderately. Billing reading are incorrect, use inverter readings instead - Inv Reading 30529kWh not 23016 not kwh.
Orthochem Bethlehem | 2025-09-01 | 1. Production is 80% of the expected energy. 2. Production is 20% more compared to Sep 2024. 3. Production is 7% more compared to last month. 4. The system is performing well. Performance affected by weather
Orthochem Bethlehem | 2025-10-01 | 1. Production is 98% of the expected energy. 2. Production is 5% less compared to Oct 2024. 3. Production is 18% more compared to last month. 4. The system is performing well.
Orthochem Bethlehem | 2025-11-01 | 1. Production is 92% of the expected energy. 2. Production is 9% less compared to Nov 2024. 3. Production is 6% less compared to last month. 4. The system is performing well.
Orthochem Bethlehem | 2025-12-01 | No PV production from 20-31 due to business closure
Orthochem Bethlehem | 2026-01-01 | The system performed as expected
Orthochem Bethlehem | 2026-02-01 | System performed well
Orthochem Bethlehem | 2026-03-01 | System performed well
Orthochem Bethlehem | 2026-04-01 | The system performed moderately due to load demand
Orthochem Bethlehem | 2026-05-01 | Performing poorly due to slightly reduced load demand
Orthochem Bethlehem | 2026-08-01 | 30 days | 0 | None | None | Energy production was limited by reduced load demand | N/A
Orthochem Bethlehem | 2026-06-01
Orthochem Bethlehem | 2026-07-01 | 31 |  | None | None | The system production was limited by soiling | possible heavy soiling to confirm during O&M on the 27th august
Plastiplate | 2024-09-01
Plastiplate | 2024-10-01
Plastiplate | 2024-11-01
Plastiplate | 2024-12-01
Plastiplate | 2025-01-01
Plastiplate | 2025-02-01 | The system is performance is affected by the weather Load demand fluctuation An increase in the PV ramp rate will be done to improve performance
Plastiplate | 2025-03-01 | System performance is >65% expected production System performance increased by 0.23% compared to last month System performace decreased by 21% compared to march 2024 Load demand fluctuation An increase in the PV ramp rate will be done to improve performance
Plastiplate | 2025-04-01 | 1. Load demand fluctuating 2. Production is 67% of expected energy 3. Production is 2% less compared to April 2024
Plastiplate | 2025-05-01 | 1. Production is 96% of the expected energy. 2. Production is 9% less compared to May 2024. 3. Production is 37% compared to last month. 4. The system is performing well.
Plastiplate | 2025-06-01 | 1. Production is 98% of the expected energy. 2. Production is 4% more compared to May 2024. 3. Production is 2% more compared to last month. 4. The system is performing well.
Plastiplate | 2025-07-01 | 31 days | 0 | None | None | Energy production was limited by reduced load demand | N/A
Plastiplate | 2025-08-01 | 31 days | 0 | None | None | Energy production was limited by reduced load demand | N/A
Plastiplate | 2025-09-01 | 30 days | 0 | None | None | Energy production was limited by reduced load demand | N/A
Plastiplate | 2025-10-01 | 31 days | 0 | None | None | Energy production was limited by reduced load demand | N/A
Plastiplate | 2025-11-01 | 30 days | 0 | None | None | Energy production was limited by reduced load demand | N/A
Plastiplate | 2025-12-01 | 31 days | 0 | None | None | Energy production was limited by reduced load demand due to business closure | N/A
Plastiplate | 2026-01-01 | 31 days | 0 | None | None | Energy production was limited by reduced load demand due to business closure | N/A
Plastiplate | 2026-02-01 | 28 days | 0 | None | None | System performed well | N/A
Plastiplate | 2026-03-01 | 31 days | 0 | None | None | System performed well | N/A
Plastiplate | 2026-04-01 | 30 days | 0 | None | None | Energy production was limited by reduced load demand | N/A
Plastiplate | 2026-05-01 | 31 days | 0 | None | None | Energy production was limited by reduced load demand | N/A
Plastiplate | 2026-08-01 | 30 days | 0 | None | None | Energy production was limited by reduced load demand | N/A
Plastiplate | 2026-07-01 | 31 | 0 | None | None | The System performed as expected | N/A
Plastiplate | 2026-06-01 | 30 days | 0 | None | None | The system performed as expected | N/A
PNB Unlimited | 2024-09-01
PNB Unlimited | 2024-10-01
PNB Unlimited | 2024-11-01
PNB Unlimited | 2024-12-01
PNB Unlimited | 2025-01-01
PNB Unlimited | 2025-02-01 | Monitoring comms Intermittent System performance reduced in Feb 2025 due to rainy weather
PNB Unlimited | 2025-03-01 | System performing well Comms offline
PNB Unlimited | 2025-04-01 | System performing well Comms offline
PNB Unlimited | 2025-05-01 | 1. Production is 108% of the expected energy. 2. Production is 17% more compared to May 2024. 3. Production is 20% more compared to last month. 4. The system is performing well. Monitoring platform offline for 31 days due to internet instability.
PNB Unlimited | 2025-06-01 | 1. Production is 99% of the expected energy. 2. Production is 16% less compared to May 2024. 3. Production is 9% less compared to last month. 4. The system is performing well. Monitoring platform offline for 31 days due to internet instability.
PNB Unlimited | 2025-07-01 | 1. Production is 96% of the expected energy. 2. Production is 9% less compared to May 2024. 3. Production is 3% less compared to last month. 4. The system is performing well. Monitoring platform offline for 31 days due to internet instability.
PNB Unlimited | 2025-08-01 | 1. Production is 55% of the expected energy. 2. Production is 39% less compared to aug 2024. 3. Production is 41% less compared to last month. 4. The system is performing poorly. Monitoring platform offline for 31 days due to internet instability.
PNB Unlimited | 2025-09-01 | 1. Production is 68% of the expected energy. 2. Production is 11% less compared to Sep 2024. 3. Production is 13% more compared to last month. 4. The system is performing poorly.
PNB Unlimited | 2025-10-01 | 1. Production is 71% of the expected energy. 2. Production is 37% less compared to Oct 2024. 3. Production is 2% more compared to last month. 4. The system is performing moderately. The system is offline. system was under performing due to faulty controls logger; issue was resoved. System performance will increase next month
PNB Unlimited | 2025-11-01 | 1. Production is 20% of the expected energy. 2. Production is 79% less compared to Nov 2024. 3. Production is 51% less compared to last month. 4. The system is performing poorly. The system is offline. system was under performing due to faulty controls logger; issue was resoved. System performance will increase next month
PNB Unlimited | 2025-12-01 | System performed poorly due business closure
PNB Unlimited | 2026-01-01 | The system performed moderately, due to demand
PNB Unlimited | 2026-02-01 | Performed moderatlry due to controls malfunction, system controll has been fixed and production is increasing
PNB Unlimited | 2026-03-01 | The system performed poorly due to load inconsistent load demand
PNB Unlimited | 2026-04-01 | The system performed poorly due to load inconsistent load demand
PNB Unlimited | 2026-05-01 | The system perfomance is affected by load shedding
PNB Unlimited | 2026-08-01 | 28 days | 2 days, 14-15th | None | None | Energy production was limited by reduced load demand and unavailability du to power outage | N/A
PNB Unlimited | 2026-06-01
PNB Unlimited | 2026-07-01 | 31 | 0 | None | None | The system performance was limited by fluctuating load demand | N/A
Q-lity Meat | 2024-09-01
Q-lity Meat | 2024-10-01
Q-lity Meat | 2024-11-01
Q-lity Meat | 2024-12-01
Q-lity Meat | 2025-01-01
Q-lity Meat | 2025-02-01 | Rain
Q-lity Meat | 2025-03-01 | 1. System perfoming well
Q-lity Meat | 2025-04-01 | 1. System perfoming well
Q-lity Meat | 2025-05-01 | 1. Production is 105% of the expected energy. 2. Production is the same compared to May 2024. 3. Production is 20% more compared to last month. 4. The system is performing well. No power outage, no comms loss, no PV production loss.
Q-lity Meat | 2025-06-01 | 1. Production is 96% of the expected energy. 2. Production is 6% less compared to May 2024. 3. Production is 0% less compared to last month. 4. The system is performing well. No power outage, no comms loss, no PV production loss.
Q-lity Meat | 2025-07-01
Q-lity Meat | 2025-08-01 | 1. Production is 96% of the expected energy. 2. Production is 16% less compared to Aug 2024. 3. Production is 12% more compared to last month. 4. The system is performing well. No power outage, no comms loss, no PV production loss.
Q-lity Meat | 2025-09-01 | 1. Production is 90% of the expected energy. 2. Production is 16% more compared to Sep 2024. 3. Production is 6% less compared to last month. 4. The system is performing well. No power outage, no comms loss, no PV production loss.
Q-lity Meat | 2025-10-01 | 1. Production is 98% of the expected energy. 2. Production is 10% less compared to Oct 2024. 3. Production is 8% more compared to last month. 4. The system is performing well.
Q-lity Meat | 2025-11-01 | 1. Production is 86% of the expected energy. 2. Production is 24% less compared to Nov 2024. 3. Production is 12% less compared to last month. 4. The system is performing well.
Q-lity Meat | 2025-12-01 | System performed well
Q-lity Meat | 2026-01-01 | The system performed as expected
Q-lity Meat | 2026-02-01 | System performed well
Q-lity Meat | 2026-03-01 | Performed moderately due to slightly reduced load
Q-lity Meat | 2026-04-01 | The system was offline, energy reading to be retrieved on site
Q-lity Meat | 2026-05-01 | The shop has shutdown, the system is not producing
Q-lity Meat | 2026-08-01 | N/A | N/A | N/A | N/A | N/A | Business has shut down
Q-lity Meat | 2026-06-01
Q-lity Meat | 2026-07-01 | N/A | N/A | Business Shutdown | N/A | N/A | N/A
Quintondale | 2024-09-01
Quintondale | 2024-10-01
Quintondale | 2024-11-01
Quintondale | 2024-12-01
Quintondale | 2025-01-01
Quintondale | 2025-02-01
Quintondale | 2025-03-01
Quintondale | 2025-04-01
Quintondale | 2025-05-01
Quintondale | 2025-06-01
Quintondale | 2025-07-01
Quintondale | 2025-08-01
Quintondale | 2025-09-01
Quintondale | 2025-10-01 | 1. Production is 93% of the expected energy. 2. Production is 10% less compared to Oct 2024. 3. Production is 11% more compared to last month. 4. The system is performing well.
Quintondale | 2025-11-01 | 1. Production is 93% of the expected energy. 2. Production is 10% less compared to Oct 2024. 3. Production is 11% more compared to last month. 4. The system is performing well.
Quintondale | 2025-12-01 | The system performed well
Quintondale | 2026-01-01 | The system performed as expected
Quintondale | 2026-02-01 | System performed well
Quintondale | 2026-03-01 | System performed well
Quintondale | 2026-04-01 | Performed moderately due to slightly reduced load
Quintondale | 2026-05-01 | Performing poorly due to slightly reduced load demand
Quintondale | 2026-08-01 | 30 days | 0 | None | None | Energy production was limited by reduced load demand | N/A
Quintondale | 2026-06-01
Quintondale | 2026-07-01 | 31 | 0 | None | None | Energy production was limited by reduced load demand | N/A
Riverside Lodge | 2024-09-01
Riverside Lodge | 2024-10-01 | 10 strings producing instead of 18 string , possible soiling or shading
Riverside Lodge | 2024-11-01
Riverside Lodge | 2024-12-01
Riverside Lodge | 2025-01-01
Riverside Lodge | 2025-02-01 | Monitoring platform offline, One string was down, Rain
Riverside Lodge | 2025-03-01 | System performance is >70% expected production System performance increased by 17% compared to last month System performance decreased by 0.77% compared to march 2024
Riverside Lodge | 2025-04-01 | 1. System performing well 2. Production is 93% of expected energy 3. Production is 3% more compared to April 2024 4. Production is 20% more compared to last month
Riverside Lodge | 2025-05-01 | 1. Production is 118% of the expected energy. 2. Production is 19% more compared to May 2024. 3. Production is 25% more compared to last month. 4. The system is performing well
Riverside Lodge | 2025-06-01 | 1. Production is 114% of the expected energy. 2. Production is 31% more compared to May 2024. 3. Production is 4% less compared to last month. 4. The system is performing well
Riverside Lodge | 2025-07-01 | 31 days | 0 | None | None | The system performed as expected | N/A
Riverside Lodge | 2025-08-01 | 31 days | 0 | None | None | The system performed as expected | N/A
Riverside Lodge | 2025-09-01 | 30 days | 0 | None | None | The system performed as expected | N/A
Riverside Lodge | 2025-10-01 | 31 days | 0 | None | None | The system performed as expected | N/A
Riverside Lodge | 2025-11-01 | 30 days | 0 | None | None | Energy production was limited by reduced load demand | N/A
Riverside Lodge | 2025-12-01 | 31 days | 0 | None | None | Energy production was limited by reduced load demand | N/A
Riverside Lodge | 2026-01-01 | 31 days | 0 | None | None | Energy production was limited by reduced load demand | N/A
Riverside Lodge | 2026-02-01 | 28 days | 0 | None | None | The system performed as expected | N/A
Riverside Lodge | 2026-03-01 | 31 days | 0 | None | None | The system performed as expected | N/A
Riverside Lodge | 2026-04-01 | 30 days | 0 | None | None | The system performed as expected | N/A
Riverside Lodge | 2026-05-01 | 31 days | 0 | None | None | The system performed as expected | N/A
Riverside Lodge | 2026-08-01 | 30 days | 0 | None | None | The system performed as expected | N/A
Riverside Lodge | 2026-06-01 | 30 days | 0 | None | None | The system performed as expected | N/A
Riverside Lodge | 2026-07-01 | 31 | 0 | None | None | The System performed as expected | N/A
Roan Foods | 2024-09-01
Roan Foods | 2024-10-01
Roan Foods | 2024-11-01
Roan Foods | 2024-12-01
Roan Foods | 2025-01-01
Roan Foods | 2025-02-01
Roan Foods | 2025-03-01
Roan Foods | 2025-04-01
Roan Foods | 2025-05-01
Roan Foods | 2025-06-01
Roan Foods | 2025-07-01
Roan Foods | 2025-08-01
Roan Foods | 2025-09-01
Roan Foods | 2025-10-01
Roan Foods | 2025-11-01
Roan Foods | 2025-12-01
Roan Foods | 2026-01-01
Roan Foods | 2026-02-01
Roan Foods | 2026-03-01
Roan Foods | 2026-04-01 | First month of commissioning
Roan Foods | 2026-05-01 | Performend poorly due to load demand
Roan Foods | 2026-08-01 | 30 days | 0 | None | None | Energy production was limited by reduced load demand | N/A
Roan Foods | 2026-06-01
Roan Foods | 2026-07-01 | 31 | 0 | None | None | Energy production was limited by reduced load demand | N/A
Sakhumnotho | 2024-09-01
Sakhumnotho | 2024-10-01
Sakhumnotho | 2024-11-01
Sakhumnotho | 2024-12-01
Sakhumnotho | 2025-01-01
Sakhumnotho | 2025-02-01 | Rain, Load demand reduced,
Sakhumnotho | 2025-03-01 | 1. System underperforming due to load demand 2. System decresd performance by 21% compared to April 2024
Sakhumnotho | 2025-04-01 | 1. System underperforming due to load demand 2. System increased performance by 8% compared to April 2024
Sakhumnotho | 2025-05-01 | 1. Production is 53% of the expected energy. 2. Production is 47% more compared to May 2024. 3. Production is 19% more compared to last month. 4. The system is performing poorly due to reduced load. No power outage, no comms loss, no PV production loss.
Sakhumnotho | 2025-06-01 | 1. Production is 58% of the expected energy. 2. Production is 120% more compared to May 2024. 3. Production is 4% less compared to last month. 4. The system is performing poorly due to reduced load. No power outage, no comms loss, no PV production loss.
Sakhumnotho | 2025-07-01 | 1. Production is 58% of the expected energy. 2. Production is 3% more compared to Jul 2024. 3. Production is the same compared to last month. 4. The system is performing poorly due to reduced load. No power outage, no comms loss, no PV production loss.
Sakhumnotho | 2025-08-01 | 1. Production is 52% of the expected energy. 2. Production is 239% more compared to Aug 2024. 3. Production is 6 less compared to last month. 4. The system is performing poorly due to reduced load. No power outage, no comms loss, no PV production loss.
Sakhumnotho | 2025-09-01 | 1. Production is 28% of the expected energy. 2. Production is 18% less compared to Sep 2024. 3. Production is 24% less compared to last month. 4. The system is performing poorly due to reduced load. No power outage, no comms loss, no PV production loss.
Sakhumnotho | 2025-10-01 | 1. Production is 7% of the expected energy. 2. Production is 81% less compared to Oct 2024. 3. Production is 21% less compared to last month. 4. System has been decommissioned and removed
Sakhumnotho | 2025-11-01 | Decomissioned
Sakhumnotho | 2025-12-01 | Decomissioned
Sakhumnotho | 2026-01-01 | Decomissioned
Sakhumnotho | 2026-02-01 | Decomissioned
Sakhumnotho | 2026-03-01 | Decomissioned
Sakhumnotho | 2026-04-01 | Decomissioned
Sakhumnotho | 2026-05-01 | System is decommissioned
Sakhumnotho | 2026-06-01
Sakhumnotho | 2026-07-01 | N/A | N/A | Business shutdown | N/A | N/A | N/A
Sakhumnotho | 2026-08-01 | N/A | N/A | N/A | N/A | N/A | Business has shut down
SaveMore Alldays - Store | 2024-09-01 | Low Demand, Panels Theft, 2x Inverter damage
SaveMore Alldays - Store | 2024-10-01
SaveMore Alldays - Store | 2024-11-01
SaveMore Alldays - Store | 2024-12-01
SaveMore Alldays - Store | 2025-01-01
SaveMore Alldays - Store | 2025-02-01 | Rain, Power Outages, Inconsistent loads, IoT siom
SaveMore Alldays - Store | 2025-03-01 | 1. System underperformed due to reduced load demand, 2. One inverter is offline
SaveMore Alldays - Store | 2025-04-01 | 1. System underperformed due to reduced load demand, 2. One inverter comms are offline 3. Requires a technician onsite to install a compatible data logger with the newly installed inverter 4. Cliet should sort out unstable grid problem with power supplier
SaveMore Alldays - Store | 2025-05-01 | 1. Production is 58% of the expected energy. 2. Production is 12% less compared to May 2024. 3. Production is 19% more compared to last month. 4. The system is performing poorly, due to reduced load. Comms are offline for 31 due existing comms device being incompatible with the new replacement inverter.
SaveMore Alldays - Store | 2025-06-01 | 1. Production is 53% of the expected energy. 2. Production is 14% less compared to May 2024. 3. Production is 5% less compared to last month. 4. The system is performing poorly, due to reduced load. Comms are offline for 31 due existing comms device being incompatible with the new replacement inverter.
SaveMore Alldays - Store | 2025-07-01 | 1. Production is 47% of the expected energy. 2. Production is 6% less compared to Jul 2024. 3. Production is 5% less compared to last month. 4. The system is performing poorly, due to reduced load. Comms are offline for 31 due existing comms device being incompatible with the new replacement inverter.
SaveMore Alldays - Store | 2025-08-01 | 1. Production is 68% of the expected energy. 2. Production is 23% more compared to Aug 2024. 3. Production is 21% more compared to last month. 4. The system is performing poorly, due to reduced load.
SaveMore Alldays - Store | 2025-09-01 | 1. Production is 66% of the expected energy. 2. Production is 15% more compared to Sep 2024. 3. Production is 22% less compared to last month. 4. The system is performing poorly, due to reduced load.
SaveMore Alldays - Store | 2025-10-01 | 1. Production is 78% of the expected energy. 2. Production is 63% more compared to Oct 2024. 3. Production is 12% more compared to last month. 4. The system performed moderately due to reduced load.
SaveMore Alldays - Store | 2025-11-01 | 1. Production is 65% of the expected energy. 2. Production is 146% less compared to Nov 2024. 3. Production is 13% less compared to last month. 4. The system performed moderately due to reduced load.
SaveMore Alldays - Store | 2025-12-01 | System performed poorly. System was isolated due to maitenance from 15 - 22st
SaveMore Alldays - Store | 2026-01-01 | System performed poorly, due to demand
SaveMore Alldays - Store | 2026-02-01 | The system is performing moderately, reduced demand and affected by rainy weather .
SaveMore Alldays - Store | 2026-03-01 | System performed poorly, due to demand
SaveMore Alldays - Store | 2026-04-01 | System performed poorly, due to demand
SaveMore Alldays - Store | 2026-05-01 | Performend poorly due to load demand
SaveMore Alldays - Store | 2026-06-01
SaveMore Alldays - Store | 2026-07-01 | 31 | 0 | None | Offline inverter comms | Energy production was limited by reduced load demand | N/A
SaveMore Alldays - Store | 2026-08-01 | 30 days | 0 | None | None | Energy production was limited by reduced load demand | N/A
Savemore Liquor Alldays | 2024-09-01 | Low Demand, Panels Theft
Savemore Liquor Alldays | 2024-10-01
Savemore Liquor Alldays | 2024-11-01
Savemore Liquor Alldays | 2024-12-01
Savemore Liquor Alldays | 2025-01-01
Savemore Liquor Alldays | 2025-02-01 | 1. Load reduced load
Savemore Liquor Alldays | 2025-03-01 | 1. Load reduced load
Savemore Liquor Alldays | 2025-04-01 | 1. Load reduced load
Savemore Liquor Alldays | 2025-05-01 | 1. Production is 20% of the expected energy. 2. Production is 32% less compared to last year. 3. Production is 3% less compared to last month. 4. The system is performing poorly due to reduced loads.
Savemore Liquor Alldays | 2025-06-01 | 1. Production is 17% of the expected energy. 2. Production is 59% less compared to last year. 3. Production is 3% less compared to last month. 4. The system is performing poorly due to reduced loads.
Savemore Liquor Alldays | 2025-07-01 | 1. Production is 20% of the expected energy. 2. Production is 53% less compared to 2024 Jul year. 3. Production is 3% less compared to last month. 4. The system is performing poorly due to reduced loads.
Savemore Liquor Alldays | 2025-08-01 | 1. Production is 43% of the expected energy. 2. Production is 43% more compared to 2024 Aug last year. 3. Production is 21% more compared to last month. 4. The system is performing poorly due to reduced loads.
Savemore Liquor Alldays | 2025-09-01 | 1. Production is 39% of the expected energy. 2. Production is 3% more compared to 2024 Sep last year. 3. Production is 4% less compared to last month. 4. The system is performing poorly due to reduced loads.
Savemore Liquor Alldays | 2025-10-01 | 1. Production is 51% of the expected energy. 2. Production is 16% more compared to 2024 Oct last year. 3. Production is 11% less compared to last month. 4. The system is performing poorly due to reduced loads.
Savemore Liquor Alldays | 2025-11-01 | 1. Production is 46% of the expected energy. 2. Production is 15% less compared to 2024 Nov last year. 3. Production is 5% less compared to last month. 4. The system is performing poorly due to reduced loads.
Savemore Liquor Alldays | 2025-12-01 | The system is performing poorly due to reduced loads.
Savemore Liquor Alldays | 2026-01-01 | The system is performing poorly due to reduced loads.
Savemore Liquor Alldays | 2026-02-01 | The system is performing poorly due to reduced loads.
Savemore Liquor Alldays | 2026-03-01 | System performed poorly, due to demand
Savemore Liquor Alldays | 2026-04-01 | System performed poorly, due to demand
Savemore Liquor Alldays | 2026-05-01 | Performend poorly due to load demand
Savemore Liquor Alldays | 2026-06-01
Savemore Liquor Alldays | 2026-07-01 | 31 | 0 | None | Offline inverter comms | Energy production was limited by reduced load demand | N/A
Savemore Liquor Alldays | 2026-08-01 | 30 days | 0 | None | None | Energy production was limited by reduced load demand | N/A
Saverite Durban | 2024-09-01
Saverite Durban | 2024-10-01 | Insufficient Information from Monitoring platform to identify
Saverite Durban | 2024-11-01
Saverite Durban | 2024-12-01
Saverite Durban | 2025-01-01
Saverite Durban | 2025-02-01 | No Monitoring Platform
Saverite Durban | 2025-03-01 | No Monitoring Platform
Saverite Durban | 2025-04-01 | 1. System performing well, no monitoring 2. Production is 79% of expected energy 3. Production is 3% more compared to April 2024 4. Production is 4% more compared to last month
Saverite Durban | 2025-05-01 | 1. Production is 100% of the expected energy. 2. Production is 13% more compared to last year. 3. Production is 21% more compared to last month. 4. There is no monitoring onsite, the system is performing well.
Saverite Durban | 2025-06-01 | 1. Production is 104% of the expected energy. 2. Production is 35% more compared to last year. 3. Production is 4% more compared to last month. 4. There is no monitoring onsite, the system is performing well.
Saverite Durban | 2025-07-01 | 1. Production is 101% of the expected energy. 2. Production is 13% more compared to Jul 2024. 3. Production is 3% less compared to last month. 4. There is no monitoring onsite, the system is performing well.
Saverite Durban | 2025-08-01 | 1. Production is 62% of the expected energy. 2. Production is 22% less compared to Aug 2024. 3. Production is 37% less compared to last month. 4. There is no monitoring onsite, the billing meter was offline from 2025/08/21 - 2025/08/31
Saverite Durban | 2025-09-01 | 1. Production is 76% of the expected energy. 2. Production is 29% more compared to Sep 2024. 3. Production is 18% less compared to last month. 4. The system performed mordaratly
Saverite Durban | 2025-10-01 | 1. Production is 90% of the expected energy. 2. Production is 21% more compared to Oct 2024. 3. Production is 14% more compared to last month. 4. The system performed well
Saverite Durban | 2025-11-01 | 1. Production is 99% of the expected energy. 2. Production is 42% more compared to Nov 2024. 3. Production is 9% more compared to last month. 4. The system performed well
Saverite Durban | 2025-12-01 | The system performed well
Saverite Durban | 2026-01-01 | The system performed as expected
Saverite Durban | 2026-02-01 | System performed well
Saverite Durban | 2026-03-01 | System performed well
Saverite Durban | 2026-04-01 | Performed as expected
Saverite Durban | 2026-05-01 | Performed as expected
Saverite Durban | 2026-06-01
Saverite Durban | 2026-07-01 | 31 | 0 | None | None | The System performed as expected | N/A
Saverite Durban | 2026-08-01 | 30 days | 0 | None | None | The system performed as expected | N/A
Saverite PMB | 2024-09-01
Saverite PMB | 2024-10-01
Saverite PMB | 2024-11-01
Saverite PMB | 2024-12-01
Saverite PMB | 2025-01-01
Saverite PMB | 2025-02-01 | Monitoring Platform offline - Rain
Saverite PMB | 2025-03-01 | 1. Monitoring Platform offline 2. System performing well
Saverite PMB | 2025-04-01 | 1. Monitoring Platform offline 2. System performing well
Saverite PMB | 2025-05-01 | 1. Production is 86% of the expected energy. 2. Production is 6% more compared to May 2024. 3. Production is 16% more compared to last month. 4. The system is performing well, The remote monitoring platform is offline for 31 days.
Saverite PMB | 2025-06-01 | 1. Production is 84% of the expected energy. 2. Production is 6% more compared to May 2024. 3. Production is 2% less compared to last month. 4. The system is performing well, The remote monitoring platform is offline for 31 days.
Saverite PMB | 2025-07-01 | 1. Production is 89% of the expected energy. 2. Production is 10% less compared to Jul 2024. 3. Production is 5% more compared to last month. 4. The system is performing well, The remote monitoring platform is offline for 31 days.
Saverite PMB | 2025-08-01 | 1. Production is 87% of the expected energy. 2. Production is 6% less compared to Aug 2024. 3. Production is 6% less compared to last month. 4. The system is performing well.
Saverite PMB | 2025-09-01 | 1. Production is 71% of the expected energy. 2. Production is 9% less compared to Sep 2024. 3. Production is 16% less compared to last month. 4. The system is performing moderately.
Saverite PMB | 2025-10-01 | 1. Production is 88% of the expected energy. 2. Production is 10% less compared to Oct 2024. 3. Production is 17% more compared to last month. 4. The system is performing well.
Saverite PMB | 2025-11-01 | 1. Production is 87% of the expected energy. 2. Production is 3% more compared to Nov 2024. 3. Production is 1% less compared to last month. 4. The system is performing well.
Saverite PMB | 2025-12-01 | The system performed well
Saverite PMB | 2026-01-01 | The syetem had controls malfunction, sofware updated and working well
Saverite PMB | 2026-02-01 | The syetem had controls malfunction, sofware updated and working well
Saverite PMB | 2026-03-01 | System performed moderately; new controls installed, system performance should increase
Saverite PMB | 2026-04-01 | The system performed moderately due to the load demand
Saverite PMB | 2026-05-01 | Performing poorly due to slightly reduced load demand
Saverite PMB | 2026-06-01
Saverite PMB | 2026-07-01 | 31 | 0 | None | Offline inverter comms | Energy production was limited by reduced load demand | N/A
Saverite PMB | 2026-08-01 | 30 days | 0 | None | None | The system performed as expected | N/A
Secunda Plaza choppies | 2026-07-01 | 0 | 31 | Business grid supply disconnected | None | No production from the solar system | Client running on generator
Secunda Plaza choppies | 2026-06-01
Secunda Plaza choppies | 2024-09-01
Secunda Plaza choppies | 2024-10-01 | Load demand Low, at 80kW or slightly low
Secunda Plaza choppies | 2024-11-01
Secunda Plaza choppies | 2024-12-01
Secunda Plaza choppies | 2025-01-01
Secunda Plaza choppies | 2025-02-01 | Reduced Load, Rain
Secunda Plaza choppies | 2025-03-01 | 1. Load reduced load 2. System is underperforming but in line with hestoric production
Secunda Plaza choppies | 2025-04-01 | 1. Load reduced load 2. System is underperforming but in line with hestoric production
Secunda Plaza choppies | 2025-05-01 | 1. Production is 65% of the expected energy. 2. Production is 3% less compared to May 2024. 3. Production is 5% more compared to last month. 4. The system is performing poorly due to reduced loads (Inline with historical data). The client experienced a power outage for 2 days during the day.
Secunda Plaza choppies | 2025-06-01 | 1. Production is 62% of the expected energy. 2. Production is 1% less compared to May 2024. 3. Production is 3% less compared to last month. 4. The system is performing poorly due to reduced loads (Inline with historical data).
Secunda Plaza choppies | 2025-07-01 | 1. Production is 56% of the expected energy. 2. Production is 17% less compared to July 2024. 3. Production is 6% less compared to last month. 4. The system is performing poorly due to reduced loads (Inline with historical data).
Secunda Plaza choppies | 2025-08-01 | 1. Production is 48% of the expected energy. 2. Production is 44% less compared to Aug 2024. 3. Production is 8% less compared to last month. 4. The system is performing poorly due to reduced loads.
Secunda Plaza choppies | 2025-09-01 | 1. Production is 42% of the expected energy. 2. Production is 25% less compared to Sep 2024. 3. Production is 6% less compared to last month. 4. The system is performing poorly due to reduced loads.
Secunda Plaza choppies | 2025-10-01 | 1. Production is 48% of the expected energy. 2. Production is 32% less compared to Oct 2024. 3. Production is 8% more compared to last month. 4. The system is performing poorly due to reduced loads.
Secunda Plaza choppies | 2025-11-01 | 1. Production is 48% of the expected energy. 2. Production is 37% less compared to Nov 2024. 3. Production is 1% less compared to last month. 4. The system is performing poorly due to reduced loads.
Secunda Plaza choppies | 2025-12-01 | There was no PV production from the 6 - 31 due to business closure
Secunda Plaza choppies | 2026-01-01 | The shop has been shut down, no load demand
Secunda Plaza choppies | 2026-02-01 | The shop has been shut down, no load demand
Secunda Plaza choppies | 2026-03-01 | The client is running on generator, that is no genset, the PV is not producing
Secunda Plaza choppies | 2026-04-01 | The client is running on generator, that is no genset, the PV is not producing
Secunda Plaza choppies | 2026-05-01 | There is no grid on-site, the system is not producing
Secunda Plaza choppies | 2026-08-01 | N/A | N/A | N/A | N/A | N/A | Grid unavailable
Secunda Plaza Shops | 2024-09-01
Secunda Plaza Shops | 2024-10-01
Secunda Plaza Shops | 2024-11-01
Secunda Plaza Shops | 2024-12-01
Secunda Plaza Shops | 2025-01-01
Secunda Plaza Shops | 2025-02-01 | System is performing well
Secunda Plaza Shops | 2025-03-01 | System is performing well
Secunda Plaza Shops | 2025-04-01 | System is performing well
Secunda Plaza Shops | 2025-05-01 | 1. Production is 100% of the expected energy. 2. Production is 4% less compared to May 2024. 3. Production is 6% more compared to last month. 4. The system is performing well, Client experienced power outage for 2 days.
Secunda Plaza Shops | 2025-06-01 | 1. Production is 95% of the expected energy. 2. Production is 1% less compared to May 2024. 3. Production is 5% more compared to last month. 4. The system is performing well.
Secunda Plaza Shops | 2025-07-01 | 1. Production is 90% of the expected energy. 2. Production is 14% less compared to Jul 2024. 3. Production is 5% more compared to last month. 4. The system is performing well.
Secunda Plaza Shops | 2025-08-01 | 1. Production is 95% of the expected energy. 2. Production is 1% less compared to Aug 2024. 3. Production is 5% more compared to last month. 4. The system is performing well.
Secunda Plaza Shops | 2025-09-01 | 1. Production is 95% of the expected energy. 2. Production is 8% more compared to Sep 2024. 3. Production is same compared to last month. 4. The system is performing well.
Secunda Plaza Shops | 2025-10-01 | 1. Production is 107% of the expected energy. 2. Production is 34% more compared to Oct 2024. 3. Production 12% more compared to last month. 4. The system performed more that expected.
Secunda Plaza Shops | 2025-11-01 | 1. Production is 87% of the expected energy. 2. Production is 20% less compared to Nov 2024. 3. Production 20% more compared to last month. 4. The system performed well.
Secunda Plaza Shops | 2025-12-01 | There was no PV production from the 9 - 31 due to business closure
Secunda Plaza Shops | 2026-01-01 | Performed poorly due to reduced demand
Secunda Plaza Shops | 2026-02-01 | System performed well
Secunda Plaza Shops | 2026-03-01 | System performed well
Secunda Plaza Shops | 2026-04-01 | Performed as expected
Secunda Plaza Shops | 2026-05-01 | Performed as expected
Secunda Plaza Shops | 2026-08-01 | 30 days | 0 | None | None | The system performed as expected | N/A
Secunda Plaza Shops | 2026-06-01
Secunda Plaza Shops | 2026-07-01 | 31 | 0 | None | None | Energy production was limited by reduced load demand | N/A
Shoprite Dube | 2024-09-01
Shoprite Dube | 2024-10-01
Shoprite Dube | 2024-11-01
Shoprite Dube | 2024-12-01
Shoprite Dube | 2025-01-01
Shoprite Dube | 2025-02-01 | The system system was offline for 4 days due to power outage, Rain
Shoprite Dube | 2025-03-01 | 1. System underperformed due to inefficient controls
Shoprite Dube | 2025-04-01 | 1. System underperformed due to inefficient controls
Shoprite Dube | 2025-05-01 | 1. Production is 67% of the expected energy. 2. Production is 11% more compared to last month. 3. The system is performing poorly. The is a huge possibility of the stringing done wrong to be checked. The was power outage for one day.
Shoprite Dube | 2025-06-01 | 1. Production is 85% of the expected energy. 2. Production is 18% more compared to last month. 3. The system is performing well. Comms went offline for 2 days
Shoprite Dube | 2025-07-01 | 1. Production is 98% of the expected energy. 2. Production is 13% more compared to last month. 3. The system is performing well. Monitoring was offline from the 27th - 31st , due to internet connectivity. Incorrect readings data should be accounted for for next month billing
Shoprite Dube | 2025-08-01 | 1. Production is 94% of the expected energy. 2. Production is 4% more compared to last month. 3. The system is performing well. Monitoring was offline from the 1st August.
Shoprite Dube | 2025-09-01 | 1. Production is 86% of the expected energy. 2. Production is 8% less compared to last month. 3. The system is performing well.
Shoprite Dube | 2025-10-01 | 1. Production is 98% of the expected energy. 2. Production is 12% more compared to last month. 3. The system is performing well.
Shoprite Dube | 2025-11-01 | 1. Production is 85% of the expected energy. 2. Production is 13% less compared to last month. 3. The system is performing well.
Shoprite Dube | 2025-12-01 | The system performed well
Shoprite Dube | 2026-01-01 | The system performed as expected
Shoprite Dube | 2026-02-01 | System performed well
Shoprite Dube | 2026-03-01 | System performed well
Shoprite Dube | 2026-04-01 | System performed well
Shoprite Dube | 2026-05-01 | Performed as expected
Shoprite Dube | 2026-06-01
Shoprite Dube | 2026-07-01 | 31 | 0 | None | None | The System performed as expected | N/A
Shoprite Dube | 2026-08-01 | 30 days | 0 | None | None | Energy production was limited by reduced load demand | N/A
Shoprite Ekhaya | 2024-09-01
Shoprite Ekhaya | 2024-10-01
Shoprite Ekhaya | 2024-11-01
Shoprite Ekhaya | 2024-12-01
Shoprite Ekhaya | 2025-01-01
Shoprite Ekhaya | 2025-02-01
Shoprite Ekhaya | 2025-03-01
Shoprite Ekhaya | 2025-04-01
Shoprite Ekhaya | 2025-05-01
Shoprite Ekhaya | 2025-06-01
Shoprite Ekhaya | 2025-07-01
Shoprite Ekhaya | 2025-08-01
Shoprite Ekhaya | 2025-09-01
Shoprite Ekhaya | 2025-10-01
Shoprite Ekhaya | 2025-11-01
Shoprite Ekhaya | 2025-12-01
Shoprite Ekhaya | 2026-01-01
Shoprite Ekhaya | 2026-02-01
Shoprite Ekhaya | 2026-03-01
Shoprite Ekhaya | 2026-04-01 | First month of commisioning
Shoprite Ekhaya | 2026-05-01 | The system performed poorly due to 8 strings being offline. The issue is resolved
Shoprite Ekhaya | 2026-06-01
Shoprite Ekhaya | 2026-07-01 | 31 | 0 | None | None | Energy production was possibly limited by heavy soiling, to be confirmed during site visit | N/A
Shoprite Ekhaya | 2026-08-01
Shoprite Hillbrow | 2024-09-01
Shoprite Hillbrow | 2024-10-01
Shoprite Hillbrow | 2024-11-01
Shoprite Hillbrow | 2024-12-01
Shoprite Hillbrow | 2025-01-01
Shoprite Hillbrow | 2025-02-01
Shoprite Hillbrow | 2025-03-01
Shoprite Hillbrow | 2025-04-01
Shoprite Hillbrow | 2025-05-01
Shoprite Hillbrow | 2025-06-01
Shoprite Hillbrow | 2025-07-01 | 1. Production is 63% of the expected energy. 2. Production is 2% more to last month. 4. The system ispporly due to shadding by nearby buildings.
Shoprite Hillbrow | 2025-08-01 | 1. Production is 69% of the expected energy. 2. Production is 6% more to last month. 4. The system is performing poorly due to shading; the system is expected to improve during the summer season
Shoprite Hillbrow | 2025-09-01 | 1. Production is 68% of the expected energy. 2. Production is 1% less to last month. 4. The system is performing poorly due to shading.
Shoprite Hillbrow | 2025-10-01 | 1. Production is 92% of the expected energy. 2. Production is 24% less than last month. 3. The system is performing well.
Shoprite Hillbrow | 2025-11-01 | 1. Production is 75% of the expected energy. 2. Production is 24% less compared to Nov 2024. 3. Production is 17% less compared to last month. 4. The system is performing moderately, due to rainy weather and shading.
Shoprite Hillbrow | 2025-12-01 | The system is performing well
Shoprite Hillbrow | 2026-01-01 | The system performed as expected
Shoprite Hillbrow | 2026-02-01 | The system is performing moderately, reduced demand and affected by rainy weather .
Shoprite Hillbrow | 2026-03-01 | The system performed poorly due to modules mismatch from shading
Shoprite Hillbrow | 2026-04-01 | The system performed poorly due to modules mismatch from shading
Shoprite Hillbrow | 2026-05-01 | System perfomed poorly due to winter shading
Shoprite Hillbrow | 2026-06-01
Shoprite Hillbrow | 2026-07-01 | 31 | 0 | None | None | The system production was limited by heavy shading | N/A
Shoprite Hillbrow | 2026-08-01 | 30 days | 0 | None | None | The system production was limited by heavy shading | N/A
Shoprite Ladybrand | 2024-09-01
Shoprite Ladybrand | 2024-10-01 | Customer Load demand sometime lower that usual, 2 under performing MPPTs need to be checked
Shoprite Ladybrand | 2024-11-01
Shoprite Ladybrand | 2024-12-01
Shoprite Ladybrand | 2025-01-01
Shoprite Ladybrand | 2025-02-01 | Rain, Load demand reduced on other days
Shoprite Ladybrand | 2025-03-01 | System performing well
Shoprite Ladybrand | 2025-04-01 | 1. System performing well
Shoprite Ladybrand | 2025-05-01 | 1. Production is 102% of the expected energy. 2. Production is 26% more compared to last month. 3. The system is performing well.No power outage, no comms loss, no PV production loss.
Shoprite Ladybrand | 2025-06-01 | 1. Production is 97% of the expected energy. 2. Production is 4% less compared to last month. 3. The system is performing well.No power outage, no comms loss, no PV production loss.
Shoprite Ladybrand | 2025-07-01 | 1. Production is 89% of the expected energy. 2. Production is 8% less compared to last month. 3. The system is performing well. Monitoring was offline from the 16-29 due to internet connectivity
Shoprite Ladybrand | 2025-08-01 | 1. Production is 86% of the expected energy. 2. Production is 3% less compared to last month. 3. The system is performing well.
Shoprite Ladybrand | 2025-09-01 | 1. Production is 73% of the expected energy. 2. Production is 13% less compared to last month. 3. The system is performing moderately. System is affected by the weather
Shoprite Ladybrand | 2025-10-01 | 1. Production is 85% of the expected energy. 2. Production is 7% less compared to Oct 2024. 3. Production is 12% more compared to last month. 4. The system is performing well.
Shoprite Ladybrand | 2025-11-01 | 1. Production is 73% of the expected energy. 2. Production is 16% less compared to Nov 2024. 3. Production is 12% less compared to last month. 4. The system is performing moderately, reduced demand and affected by rainy weather .
Shoprite Ladybrand | 2025-12-01 | The system is performing moderately, reduced demand and affected by rainy weather .
Shoprite Ladybrand | 2026-01-01 | The system performed as expected
Shoprite Ladybrand | 2026-02-01 | System performed moderately due to load demand, one string is disconnected
Shoprite Ladybrand | 2026-03-01 | System performance will increase, damaged strings were repaired
Shoprite Ladybrand | 2026-04-01 | System performance moderately
Shoprite Ladybrand | 2026-05-01 | Performing poorly due to slightly reduced load demand
Shoprite Ladybrand | 2026-06-01
Shoprite Ladybrand | 2026-07-01 | 31 | 0 | None | None | The Energy production was limited by due O&M to be made by the end of August | N/A
Shoprite Ladybrand | 2026-08-01 | 30 days | 0 | None | None | Energy production was limited by reduced load demand | N/A
Shoprite Mini Ganyesa | 2024-09-01
Shoprite Mini Ganyesa | 2024-10-01 | Load demand is low at 150kW
Shoprite Mini Ganyesa | 2024-11-01
Shoprite Mini Ganyesa | 2024-12-01
Shoprite Mini Ganyesa | 2025-01-01
Shoprite Mini Ganyesa | 2025-02-01 | Rain
Shoprite Mini Ganyesa | 2025-03-01 | System performing well
Shoprite Mini Ganyesa | 2025-04-01
Shoprite Mini Ganyesa | 2025-05-01 | 1. Production is 86% of the expected energy. 2. Production is 15% more compared to last month. 3. The system is performing well. The was power outage and PV loss for 2 days .
Shoprite Mini Ganyesa | 2025-06-01 | 1. Production is 94% of the expected energy. 2. Production is 8% more compared to last month. 3. The system is performing well.
Shoprite Mini Ganyesa | 2025-07-01 | 1. Production is 86% of the expected energy. 2. Production is 8% less compared to last month. 3. The system is performing well.
Shoprite Mini Ganyesa | 2025-08-01 | 1. Production is 82% of the expected energy. 2. Production is 4% less compared to last month. 3. The system is performing well.
Shoprite Mini Ganyesa | 2025-09-01 | 1. Production is 80% of the expected energy. 2. Production is 5% more compared to Sep 2024. 3. Production is 2% less compared to last month. 4. The system is performing well.
Shoprite Mini Ganyesa | 2025-10-01 | 1. Production is 77% of the expected energy. 2. Production is 12% less compared to Oct 2024. 3. Production is 3% less compared to last month. 4. The system is performing moderately. Load demand reduced.
Shoprite Mini Ganyesa | 2025-11-01 | 1. Production is 74% of the expected energy. 2. Production is 12% less compared to Nov 2024. 3. Production is 3% less compared to last month. 4. The system is performing moderately. Load demand reduced, affected by weather.
Shoprite Mini Ganyesa | 2025-12-01 | The system is performing moderately, reduced demand and affected by rainy weather .
Shoprite Mini Ganyesa | 2026-01-01 | The system is performing moderately, reduced demand and affected by rainy weather .
Shoprite Mini Ganyesa | 2026-02-01 | The system is performing moderately, reduced demand and affected by rainy weather .
Shoprite Mini Ganyesa | 2026-03-01 | The system is performing moderately, reduced demand and affected by rainy weather .
Shoprite Mini Ganyesa | 2026-04-01 | The system is performing moderately, reduced demand and affected by rainy weather .
Shoprite Mini Ganyesa | 2026-05-01 | Performing poorly due to slightly reduced load demand
Shoprite Mini Ganyesa | 2026-06-01
Shoprite Mini Ganyesa | 2026-07-01 | 31 | 0 | None | None | The Energy production was limited by due O&M to be made by the end of August | N/A
Shoprite Mini Ganyesa | 2026-08-01 | 30 days | 0 | None | None | Energy production was limited by reduced load demand | N/A
Shoprite Naledi | 2024-09-01
Shoprite Naledi | 2024-10-01 | Power cuts, slightly low demand on some other days
Shoprite Naledi | 2024-11-01
Shoprite Naledi | 2024-12-01
Shoprite Naledi | 2025-01-01
Shoprite Naledi | 2025-02-01 | Power cuts, slightly low demand on some other days
Shoprite Naledi | 2025-03-01 | 1. System perfoming modarate, system is slightly oversized
Shoprite Naledi | 2025-04-01 | 1. System perfoming modarate, system is slightly oversized
Shoprite Naledi | 2025-05-01 | 1. Production is 114% of the expected energy. 2. Production is 40% more compared to last month. 3. The system is performing well. Client load demand increased. No power outage, no comms loss, no PV production loss.
Shoprite Naledi | 2025-06-01 | 1. Production is 113% of the expected energy. 2. Production is 1% less compared to last month. 3. The system is performing well. Client load demand increased. No power outage, no comms loss, no PV production loss.
Shoprite Naledi | 2025-07-01 | 1. Production is 109% of the expected energy. 2. Production is 4% less compared to last month. 3. The system is performing well. The system was offline on the 6th
Shoprite Naledi | 2025-08-01 | 1. Production is 102% of the expected energy. 2. Production is 7% less compared to last month. 3. The system is performing well.
Shoprite Naledi | 2025-09-01 | 1. Production is 90% of the expected energy. 2. Production is 56% more compared to Sep 2024. 3. Production is 12% less compared to last month. 4. The system is performing well.
Shoprite Naledi | 2025-10-01 | 1. Production is 102% of the expected energy. 2. Production is 13% more compared to Oct 2024. 3. Production is 12% more compared to last month. 4. The system performed more than expected.
Shoprite Naledi | 2025-11-01 | 1. Production is 87% of the expected energy. 2. Production is 5% less compared to Nov 2024. 3. Production is 11% less compared to last month. 4. The system performed as expected
Shoprite Naledi | 2025-12-01 | The system performed well
Shoprite Naledi | 2026-01-01 | The system performed as expected
Shoprite Naledi | 2026-02-01 | System performed well
Shoprite Naledi | 2026-03-01 | System performed well
Shoprite Naledi | 2026-04-01 | Performed as expected
Shoprite Naledi | 2026-05-01 | Performed as expected
Shoprite Naledi | 2026-06-01
Shoprite Naledi | 2026-07-01 | 31 | 0 | None | Inverter comms offline | The energy production was affected by heavy soiling | N/A
Shoprite Naledi | 2026-08-01 | 30 days | 0 | None | None | The system performed as expected | N/A
Shoprite Newlands | 2024-09-01
Shoprite Newlands | 2024-10-01
Shoprite Newlands | 2024-11-01
Shoprite Newlands | 2024-12-01
Shoprite Newlands | 2025-01-01
Shoprite Newlands | 2025-02-01
Shoprite Newlands | 2025-03-01
Shoprite Newlands | 2025-04-01
Shoprite Newlands | 2025-05-01
Shoprite Newlands | 2025-06-01
Shoprite Newlands | 2025-07-01
Shoprite Newlands | 2025-08-01
Shoprite Newlands | 2025-09-01
Shoprite Newlands | 2025-10-01
Shoprite Newlands | 2025-11-01
Shoprite Newlands | 2025-12-01 | Performed well
Shoprite Newlands | 2026-01-01 | The system performed as expected
Shoprite Newlands | 2026-02-01 | System performed well
Shoprite Newlands | 2026-03-01 | System performed well
Shoprite Newlands | 2026-04-01 | Performed as expected
Shoprite Newlands | 2026-05-01 | Performed as expected
Shoprite Newlands | 2026-06-01
Shoprite Newlands | 2026-07-01 | 31 | 0 | None | None | The System performed as expected | N/A
Shoprite Newlands | 2026-08-01 | 30 days | 0 | None | None | The system performed as expected | N/A
Shoprite Thokoza | 2024-09-01
Shoprite Thokoza | 2024-10-01
Shoprite Thokoza | 2024-11-01
Shoprite Thokoza | 2024-12-01
Shoprite Thokoza | 2025-01-01
Shoprite Thokoza | 2025-02-01
Shoprite Thokoza | 2025-03-01
Shoprite Thokoza | 2025-04-01
Shoprite Thokoza | 2025-05-01
Shoprite Thokoza | 2025-06-01
Shoprite Thokoza | 2025-07-01 | 1. Production is 57% of the expected energy. 2. Production is 21% less compared to last month. 4. The system performed poorly. Recorded readings are incorrect should be accounted for next month billing. The system was offline from 10-17th
Shoprite Thokoza | 2025-08-01 | 1. Production is 71% of the expected energy. 2. Production is 14% more compared to last month. 4. The system performed moderately. Solar panels to be tilted to improve performance.
Shoprite Thokoza | 2025-09-01 | 1. Production is 70% of the expected energy. 2. Production is 1% less compared to last month. 4. The system performed moderately.
Shoprite Thokoza | 2025-10-01 | 1. Production is 90% of the expected energy. 2. Production is 20% more compared to last month. 3. The system performed moderately.
Shoprite Thokoza | 2025-11-01 | 1. Production is 83% of the expected energy. 2. Production is 7% less compared to last month. 3. The system performed well.
Shoprite Thokoza | 2025-12-01 | The system produced poorly due to business closure from 16-31
Shoprite Thokoza | 2026-01-01 | The system performed as expected
Shoprite Thokoza | 2026-02-01 | System performed well
Shoprite Thokoza | 2026-03-01 | System performed well
Shoprite Thokoza | 2026-04-01 | Performed as expected
Shoprite Thokoza | 2026-05-01 | Performed as expected
Shoprite Thokoza | 2026-06-01
Shoprite Thokoza | 2026-07-01 | 31 | 0 | None | Inverter comms offline | The energy production was affected by heavy soiling | N/A
Shoprite Thokoza | 2026-08-01 | 30 days | 0 | None | None | The energy production was affected by heavy soiling | N/A
Spring Glade | 2024-09-01 | load reduction, inconsistant load
Spring Glade | 2024-10-01
Spring Glade | 2024-11-01
Spring Glade | 2024-12-01
Spring Glade | 2025-01-01
Spring Glade | 2025-02-01 | Rain, Load demand reduced to half the installed capacity
Spring Glade | 2025-03-01 | Load demand reduced to half the installed capacity
Spring Glade | 2025-04-01 | Load demand reduced to half the installed capacity
Spring Glade | 2025-05-01 | 1. Production is 81% of the expected energy. 2. Production is 3% more compared to May 2024. 3. Production is 23% more compared to last month. 4. The system performed well, client load increased. No power outage, no comms loss, no PV production loss.
Spring Glade | 2025-06-01 | 1. Production is 91% of the expected energy. 2. Production is 3% more compared to May 2024. 3. Production is 10% more compared to last month. 4. The system performed well, client load increased. No power outage, no comms loss, no PV production loss.
Spring Glade | 2025-07-01 | 1. Production is 76% of the expected energy. 2. Production is 8% less compared to Jul 2024. 3. Production is 16% less compared to last month. 4. The system performed modarately, client load reduced. No power outage, there was no comms on the 6th.
Spring Glade | 2025-08-01 | 1. Production is 68% of the expected energy. 2. Production is 2% less compared to Aug 2024. 3. Production is 8% less compared to last month. 4. The system performed poorly, client load reduced. No power outage, there was no comms on the 24th and 25th.
Spring Glade | 2025-09-01 | 1. Production is 70% of the expected energy. 2. Production is 22% less compared to Sep 2024. 3. Production is 2% more compared to last month. 4. The system performed moderately, and client load was reduced. No power outage, there was no comms on the 24th and 25th.
Spring Glade | 2025-10-01 | 1. Production is 59% of the expected energy. 2. Production is 3% less compared to Oct 2024. 3. Production is 11% less compared to last month. 4. The system performed poorely, and client load was reduced.
Spring Glade | 2025-11-01 | 1. Production is 53% of the expected energy. 2. Production is 8% less compared to Nov 2024. 3. Production is 6% less compared to last month. 4. The system performed poorely, and client load was reduced. System affected by rainy weather
Spring Glade | 2025-12-01 | The system performed poorely, and client load was reduced. System affected by rainy weather
Spring Glade | 2026-01-01 | The system performed poorely, and client load was reduced. System affected by rainy weather
Spring Glade | 2026-02-01 | The system performed poorely, and client load was reduced. System affected by rainy weather
Spring Glade | 2026-03-01 | The system performed poorely, and client load was reduced.
Spring Glade | 2026-04-01 | The system performed poorely, and client load was reduced.
Spring Glade | 2026-05-01 | Performing poorly due to slightly reduced load demand
Spring Glade | 2026-06-01
Spring Glade | 2026-07-01 | 31 | 0 | None | None | Energy production was limited by reduced load demand | N/A
Spring Glade | 2026-08-01 | 30 days | 0 | None | None | Energy production was limited by reduced load demand | N/A
SR Morula TF 1 | 2024-09-01
SR Morula TF 1 | 2024-10-01
SR Morula TF 1 | 2024-11-01
SR Morula TF 1 | 2024-12-01
SR Morula TF 1 | 2025-01-01
SR Morula TF 1 | 2025-02-01
SR Morula TF 1 | 2025-03-01
SR Morula TF 1 | 2025-04-01
SR Morula TF 1 | 2025-05-01
SR Morula TF 1 | 2025-06-01
SR Morula TF 1 | 2025-07-01
SR Morula TF 1 | 2025-08-01 | 11 days | 01-20, 20 days | The system was not commissioned | None | None | N/A
SR Morula TF 1 | 2025-09-01 | 30 days | 0 | None | None | The system performed as expected | N/A
SR Morula TF 1 | 2025-10-01 | 31 days | 0 | None | None | The system performed as expected | N/A
SR Morula TF 1 | 2025-11-01 | 30 days | 0 | None | None | The system performed as expected | N/A
SR Morula TF 1 | 2025-12-01 | 31 days | 0 | None | None | The system performed as expected | N/A
SR Morula TF 1 | 2026-01-01 | 31 days | 0 | None | None | The system performed as expected | N/A
SR Morula TF 1 | 2026-02-01 | 28 days | 0 | None | None | The system performed as expected | N/A
SR Morula TF 1 | 2026-03-01 | 31 days | 0 | None | None | The system performed moderately due to rainy weather | N/A
SR Morula TF 1 | 2026-04-01 | 30 days | 0 | None | None | The system performed moderately due to rainy weather | N/A
SR Morula TF 1 | 2026-05-01 | 31 days | 0 | None | None | The system performed as expected | N/A
SR Morula TF 1 | 2026-08-01 | 30 days | 0 | None | None | The system performed as expected | N/A
SR Morula TF 1 | 2026-06-01 | 30 days | 0 | None | None | The system performed as expected | N/A
SR Morula TF 1 | 2026-07-01 | 20 | 11 days, 16-27th | Client Transformer was getting serviced | None | The energy production was affected by system unavailability and heavy soiling | CT has been swapped around after transformer maintenance
SR Morula TF 1 - Shoprite | 2024-09-01
SR Morula TF 1 - Shoprite | 2024-10-01
SR Morula TF 1 - Shoprite | 2024-11-01
SR Morula TF 1 - Shoprite | 2024-12-01
SR Morula TF 1 - Shoprite | 2025-01-01
SR Morula TF 1 - Shoprite | 2025-02-01
SR Morula TF 1 - Shoprite | 2025-03-01
SR Morula TF 1 - Shoprite | 2025-04-01
SR Morula TF 1 - Shoprite | 2025-05-01
SR Morula TF 1 - Shoprite | 2025-06-01
SR Morula TF 1 - Shoprite | 2025-07-01
SR Morula TF 1 - Shoprite | 2025-08-01
SR Morula TF 1 - Shoprite | 2025-09-01 | 1. Production is 86% of the expected energy. 2. Production is 28% less than last month. 4. The system is performing well.
SR Morula TF 1 - Shoprite | 2025-10-01 | 1. Production is 94% of the expected energy. 2. Production is 8% more than last month. 3. The system is performing well.
SR Morula TF 1 - Shoprite | 2025-11-01 | 1. Production is 81% of the expected energy. 2. Production is 13% less than last month. 3. The system is performing well. System is affected by weather.
SR Morula TF 1 - Shoprite | 2025-12-01 | System performed well
SR Morula TF 1 - Shoprite | 2026-01-01 | The system performed as expected
SR Morula TF 1 - Shoprite | 2026-02-01 | System performed well
SR Morula TF 1 - Shoprite | 2026-03-01 | The system performed moderately due to rainy weather
SR Morula TF 1 - Shoprite | 2026-04-01 | The system performed moderately due to rainy weather
SR Morula TF 1 - Shoprite | 2026-05-01 | Performed as expected
SR Morula TF 1 - Shoprite | 2026-08-01 | 28 days | 2 days, 11-12th | Power outage | None | Energy production was limited by reduced load demand and grid unavailability | N/A
SR Morula TF 1 - Shoprite | 2026-06-01
SR Morula TF 1 - Shoprite | 2026-07-01 | 20 | 11 days, 16-27th | Client Transformer was getting serviced | None | The energy production was affected by system unavailability and heavy soiling | N/A
SR Morula TF 2 | 2024-09-01
SR Morula TF 2 | 2024-10-01
SR Morula TF 2 | 2024-11-01
SR Morula TF 2 | 2024-12-01
SR Morula TF 2 | 2025-01-01
SR Morula TF 2 | 2025-02-01
SR Morula TF 2 | 2025-03-01
SR Morula TF 2 | 2025-04-01
SR Morula TF 2 | 2025-05-01
SR Morula TF 2 | 2025-06-01
SR Morula TF 2 | 2025-07-01
SR Morula TF 2 | 2025-08-01 | 11 days | 01-20, 20 days | The system was not commissioned | None | None | N/A
SR Morula TF 2 | 2025-09-01 | 30 days | 0 | None | None | The system performed as expected | N/A
SR Morula TF 2 | 2025-10-01 | 31 days | 0 | None | None | The system performed as expected | N/A
SR Morula TF 2 | 2025-11-01 | 30 days | 0 | None | None | The system performed as expected | N/A
SR Morula TF 2 | 2025-12-01 | 31 days | 0 | None | None | The system performed as expected | N/A
SR Morula TF 2 | 2026-01-01 | 31 days | 0 | None | None | The system performed as expected | N/A
SR Morula TF 2 | 2026-02-01 | 28 days | 0 | None | None | The system performed as expected | N/A
SR Morula TF 2 | 2026-03-01 | 31 days | 0 | None | None | The system performed moderately due to rainy weather | N/A
SR Morula TF 2 | 2026-04-01 | 30 days | 0 | None | None | The system performed moderately due to rainy weather | N/A
SR Morula TF 2 | 2026-05-01 | 31 days | 0 | None | None | The system performed as expected | N/A
SR Morula TF 2 | 2026-08-01 | 11 days | 19 days, 1-19th | Power outage | transfomer repairs | Energy production was limited by unavailability due to power outage due to transformer repairs | N/A
SR Morula TF 2 | 2026-06-01 | 30 days | 0 | None | None | The system performed as expected | N/A
SR Morula TF 2 | 2026-07-01 | 31 | 0 | None | None | The energy production was affected by heavy soiling | N/A
Thakadu Industrial | 2024-09-01
Thakadu Industrial | 2024-10-01
Thakadu Industrial | 2024-11-01
Thakadu Industrial | 2024-12-01
Thakadu Industrial | 2025-01-01
Thakadu Industrial | 2025-02-01
Thakadu Industrial | 2025-03-01
Thakadu Industrial | 2025-04-01
Thakadu Industrial | 2025-05-01
Thakadu Industrial | 2025-06-01
Thakadu Industrial | 2025-07-01
Thakadu Industrial | 2025-08-01
Thakadu Industrial | 2025-09-01
Thakadu Industrial | 2025-10-01
Thakadu Industrial | 2025-11-01
Thakadu Industrial | 2025-12-01
Thakadu Industrial | 2026-01-01
Thakadu Industrial | 2026-02-01
Thakadu Industrial | 2026-03-01
Thakadu Industrial | 2026-04-01
Thakadu Industrial | 2026-05-01 | No monitoring onsite
Thakadu Industrial | 2026-08-01
Thakadu Industrial | 2026-06-01
Thakadu Industrial | 2026-07-01 | N/A | N/A | N/A | The system comms are offline | N/A | N/A
The Alec | 2024-09-01
The Alec | 2024-10-01
The Alec | 2024-11-01
The Alec | 2024-12-01
The Alec | 2025-01-01
The Alec | 2025-02-01 | Rain, Power outages, Inconsistent Load demand, Increase Ramp rate
The Alec | 2025-03-01 | System performance is >65% expected production System performance increased by 0,4% compared to last month System performance decreased by 27% compared to march 2024 Inconsistent Load demand, Increase Ramp rate to improve perfomance
The Alec | 2025-04-01 | 1. System affected by weather, Fuctuating loads 2. Production is 62% of expected energy 3. Production is 29% less compared to April 2024 4. Production is 6% less compared to last month
The Alec | 2025-05-01 | 1. Production is 67% of the expected energy. 2. Production is 10% less compared to May 2024. 3. Production is 5% more compared to last month. 4. They experienced grid outages 3 times and caused loss of PV three times, Load are not consistently higher that install PV.
The Alec | 2025-06-01 | 1. Production is 60% of the expected energy. 2. Production is 5% less compared to May 2024. 3. Production is 7% less compared to last month. 4.System poorely due to inconsistant load reduction. The experience loss of Comma and PV 4 days (days: 7,8,14,15)
The Alec | 2025-07-01 | 31 days | 0 | None | None | Energy production was limited by reduced load demand | N/A
The Alec | 2025-08-01 | 31 days | 0 | None | None | Energy production was limited by reduced load demand | N/A
The Alec | 2025-09-01 | 30 days | 0 | None | None | Energy production was limited by reduced load demand | N/A
The Alec | 2025-10-01 | 31 days | 0 | None | None | Energy production was limited by reduced load demand | N/A
The Alec | 2025-11-01 | 30 days | 0 | None | None | Energy production was limited by reduced load demand | N/A
The Alec | 2025-12-01 | 31 days | 0 | None | None | The system performed as expected | N/A
The Alec | 2026-01-01 | 31 days | 0 | None | None | The system performed as expected | N/A
The Alec | 2026-02-01 | 28 days | 0 | None | None | The system performed as expected | N/A
The Alec | 2026-03-01 | 31 days | 0 | None | None | Energy production was limited by reduced load demand | N/A
The Alec | 2026-04-01 | 30 days | 0 | None | None | Energy production was limited by reduced load demand | N/A
The Alec | 2026-05-01 | 31 days | 0 | None | None | Energy production was limited by reduced load demand | N/A
The Alec | 2026-08-01 | 30 days | 0 | None | None | Energy production was limited by reduced load demand | N/A
The Alec | 2026-07-01 | 28 | 3 days; 8th, 23rd,28th | Grid power outage | None | The system energy production has been affected by grid unavailability and reduced load demand | N/A
The Alec | 2026-06-01 | 30 days | 0 | None | None | The energy production was limited by load demand & bad weather | N/A
Three Peaks | 2024-09-01
Three Peaks | 2024-10-01
Three Peaks | 2024-11-01
Three Peaks | 2024-12-01
Three Peaks | 2025-01-01
Three Peaks | 2025-02-01 | Rain, Power Outage, Inconsistent Loads
Three Peaks | 2025-03-01 | System performance is >65% expected production System performance increased by 3% compared to last month System performance decreased by 22% compared to march 2024 Inconsistent Load demand, Increase Ramp rate to improve perfomances
Three Peaks | 2025-04-01 | 1. The system is performing well 2. Production is 92% of expected production 3. Production is 24% more compared to last month
Three Peaks | 2025-05-01 | 1. Production is 111% of the expected energy. 2. Production is 18% more compared to May 2024. 3. Production is 19% more compared to last month. 4. The system is performing well, Billing meter comms to be rebooted and restored
Three Peaks | 2025-06-01 | 1. Production is 101% of the expected energy. 2. Production is 16% more compared to Jul 2024. 3. Production is 10% less compared to last month. 4. The system is performing well.
Three Peaks | 2025-07-01 | 1. Production is 105% of the expected energy. 2. Production is 7% less compared to May 2024. 3. Production is 4% more compared to last month. 4. The system is performing well.
Three Peaks | 2025-08-01 | 1. Production is 108% of the expected energy. 2. Production is 78% more compared to Aug 2024. 3. Production is 3% more compared to last month. 4. The system is performing well.
Three Peaks | 2025-09-01 | 1. Production is 104% of the expected energy. 2. Production is 33% more compared to Sep 2024. 3. Production is 4% less compared to last month. 4. The system is performing well.
Three Peaks | 2025-10-01 | 1. Production is 109% of the expected energy. 2. Production is 30% more compared to Oct 2024. 3. Production is 5% more compared to last month. 4. The system performed more than expected.
Three Peaks | 2025-11-01 | 1. Production is 99% of the expected energy. 2. Production is 55% more compared to Nov 2024. 3. Production is 10% less compared to last month. 4. The system performed well.
Three Peaks | 2025-12-01 | The system performed well
Three Peaks | 2026-01-01 | The system performed as expected
Three Peaks | 2026-02-01 | System performed well
Three Peaks | 2026-03-01 | System performed well
Three Peaks | 2026-04-01 | Performed as expected
Three Peaks | 2026-05-01 | Performed as expected
Three Peaks | 2026-08-01 | 30 days | 0 | None | None | The system performed as expected | N/A
Three Peaks | 2026-06-01
Three Peaks | 2026-07-01 | 31 | 0 | None | None | The System performed as expected | N/A
TPF Foods | 2024-09-01
TPF Foods | 2024-10-01
TPF Foods | 2024-11-01
TPF Foods | 2024-12-01
TPF Foods | 2025-01-01
TPF Foods | 2025-02-01 | The system is performed well in January February performance reduced due rainy weather
TPF Foods | 2025-03-01 | System performing well
TPF Foods | 2025-04-01 | System modaratly perfomed, load reduced slignificantly on some days
TPF Foods | 2025-05-01 | 1. Production is 102% of the expected energy. 2. Production is 1% more compared to May 2024. 3. Production is 29% more compared to last month. 4. The system is performing well. Client load slightly increased.
TPF Foods | 2025-06-01 | 1. Production is 94% of the expected energy. 2. Production is 2% more compared to Jun 2024. 3. Production is 8% less compared to last month. 4. The system is performing well. Client load slightly increased.
TPF Foods | 2025-07-01 | 1. Production is 92% of the expected energy. 2. Production is 8% less compared to Jul 2024. 3. Production is 2% less compared to last month. 4. The system is performing well. Client load slightly increased.
TPF Foods | 2025-08-01 | 1. Production is 91% of the expected energy. 2. Production is 7% more compared to Aug 2024. 3. Production is 1% less compared to last month. 4. The system is performing well.
TPF Foods | 2025-09-01 | 1. Production is 83% of the expected energy. 2. Production is 3% more compared to Aug 2024. 3. Production is 8% more compared to last month. 4. The system is performing well.
TPF Foods | 2025-10-01 | 1. Production is 92% of the expected energy. 2. Production is 11% less compared to Oct 2024. 3. Production is 9% more compared to last month. 4. The system is performing well.
TPF Foods | 2025-11-01 | 1. Production is 74% of the expected energy. 2. Production is 31% less compared to Nov 2024. 3. Production is 18% less compared to last month. 4. The system is performing moderately, load reduced, system affected by weather.
TPF Foods | 2025-12-01 | The system performed well
TPF Foods | 2026-01-01 | The system performed as expected
TPF Foods | 2026-02-01 | System performed well
TPF Foods | 2026-03-01 | The system performed moderately due to reduced load
TPF Foods | 2026-04-01 | The system performed poorely, and client load was reduced.
TPF Foods | 2026-05-01 | Performing poorly due to slightly reduced load demand
TPF Foods | 2026-08-01 | 30 days | 0 | None | None | Energy production was limited by reduced load demand | N/A
TPF Foods | 2026-06-01
TPF Foods | 2026-07-01 | 31 | 0 | None | None | Energy production was limited by reduced load demand | N/A
Trouw Nutrition | 2024-09-01
Trouw Nutrition | 2024-10-01
Trouw Nutrition | 2024-11-01
Trouw Nutrition | 2024-12-01
Trouw Nutrition | 2025-01-01
Trouw Nutrition | 2025-02-01 | The system performance is affected by rainy weather System affected by inconsistent load demand
Trouw Nutrition | 2025-03-01 | System performed well
Trouw Nutrition | 2025-04-01 | System modaratly perfomed, Monitoring plartform is offline
Trouw Nutrition | 2025-05-01 | 1. Production is 51% of the expected energy. 2. Production is 20% less compared to last month. 3. The system is performed poorly due to the Wattmon controls kit repair. The system monitoring, PV was offline for 14 days.
Trouw Nutrition | 2025-06-01 | 1. Production is 39% of the expected energy. 2. Production is 12% less compared to last month. 3. The system is performed poorly . The system monitoring, PV was offline 19 days (1-11,16-17,19-20,24-26,28-30)
Trouw Nutrition | 2025-07-01 | 1. Production is 58% of the expected energy. 2. Production is 19% more compared to last month. 3. The system is performed poorly . The system monitoring, PV was offline 11 days (01st - 11th) , the issuse is of swapped CTs's is resolved and th e performance is recovering
Trouw Nutrition | 2025-08-01 | 1. Production is 84% of the expected energy. 2. Production is 4% more compared to Aug 2024. 3. Production is 26% more compared to last month. 4. The system is performing well, issues resolved, and system performance is expected to improve more
Trouw Nutrition | 2025-09-01 | 1. Production is 74% of the expected energy. 2. Production is 1% less compared to Sep 2024. 3. Production is 10% less compared to last month. 4. The system is performing moderately.
Trouw Nutrition | 2025-10-01 | 1. Production is 95% of the expected energy. 2. Production is 2% more compared to Oct 2024. 3. Production is 21% more compared to last month. 4. The system is performing well.
Trouw Nutrition | 2025-11-01 | 1. Production is 77% of the expected energy. 2. Production is 8% less compared to Nov 2024. 3. Production is 18% less compared to last month. 4. The system performed moderately, system affected by rainy weather.
Trouw Nutrition | 2025-12-01 | 4. The system performed moderately, system affected by busined closure
Trouw Nutrition | 2026-01-01 | The system performed as expected
Trouw Nutrition | 2026-02-01 | System performed well
Trouw Nutrition | 2026-03-01 | The system performed moderately due to bad weather
Trouw Nutrition | 2026-04-01 | The system performed moderately due to the load demand
Trouw Nutrition | 2026-05-01 | Performing poorly due to slightly reduced load demand
Trouw Nutrition | 2026-08-01 | 30 days | 0 | None | None | Energy production was limited by reduced load demand | N/A
Trouw Nutrition | 2026-06-01
Trouw Nutrition | 2026-07-01 | 31 | 0 | None | None | Energy production was limited by reduced load demand | N/A
U Save Botrivier | 2024-09-01
U Save Botrivier | 2024-10-01
U Save Botrivier | 2024-11-01
U Save Botrivier | 2024-12-01
U Save Botrivier | 2025-01-01
U Save Botrivier | 2025-02-01
U Save Botrivier | 2025-03-01
U Save Botrivier | 2025-04-01
U Save Botrivier | 2025-05-01
U Save Botrivier | 2025-06-01
U Save Botrivier | 2025-07-01
U Save Botrivier | 2025-08-01
U Save Botrivier | 2025-09-01 | 1. Production is 81% of the expected energy. 2. Production is 1% less than last month. 4. The system is performing well. Load demand is low.
U Save Botrivier | 2025-10-01 | 1. Production is 81% of the expected energy. 2. Production is the same as last month. 3. The system is performing well. Load demand is low.
U Save Botrivier | 2025-11-01 | 1. Production is 73% of the expected energy. 2. Production is 8% less compared to last month. 3. The system is performed moderate.
U Save Botrivier | 2025-12-01 | No PV production on the 17th due to power outage
U Save Botrivier | 2026-01-01 | The system performed as expected
U Save Botrivier | 2026-02-01 | System performed moderately due to load demand
U Save Botrivier | 2026-03-01 | The system performed well
U Save Botrivier | 2026-04-01 | The is missing data fron 22-30 on the monitoring platform, data will be retrieved
U Save Botrivier | 2026-05-01 | Performend poorly due to load demand
U Save Botrivier | 2026-08-01 | 30 days | 0 | None | None | Energy production was limited by reduced load demand | N/A
U Save Botrivier | 2026-06-01
U Save Botrivier | 2026-07-01 | 23 | 8 days;5-9th,27-31st | Unknown | None | Energy production was limited by system unavailability | N/A
Usave Naboomspruit | 2026-07-01 | 31 | 0 | None | None | The energy production was limited by load demand | N/A
Watt Place Rotoflo | 2024-09-01
Watt Place Rotoflo | 2024-10-01
Watt Place Rotoflo | 2024-11-01
Watt Place Rotoflo | 2024-12-01
Watt Place Rotoflo | 2025-01-01
Watt Place Rotoflo | 2025-02-01 | The system is affected by the rainy weather Load demand is fluctuating on some days Power outages affected performance The system performance for Jan and Much is better than last year
Watt Place Rotoflo | 2025-03-01 | System performance is >70% expected production System performance decreased by 7% compared to last month System performance decreased by 0,48% compared to march 2024 Load demand is fluctuating on some days Power outages affected performance The system performance for Jan and Feb production was better than 2024
Watt Place Rotoflo | 2025-04-01 | 1. The system is performing well 2. Production is 83% of the expected energy 3. Production is 28% more compared to April 2024 4. Production is 7% more compared to last month
Watt Place Rotoflo | 2025-05-01 | 1. Production is 103% of the expected energy. 2. Production is 11% more compared to May 2024. 3. Production is 20% more compared to last month. 4. The system is perfoming well.
Watt Place Rotoflo | 2025-06-01 | 1. Production is 98% of the expected energy. 2. Production is 14% more compared to May 2024. 3. Production is 5% less compared to last month. 4. The system is perfoming well.
Watt Place Rotoflo | 2025-07-01 | 31 days | 0 | None | None | There system produced as expected | N/A
Watt Place Rotoflo | 2025-08-01 | 31 days | 0 | None | None | There system produced as expected | N/A
Watt Place Rotoflo | 2025-09-01 | 30 days | 0 | None | Internet connectivity issues | There system produced as expected | N/A
Watt Place Rotoflo | 2025-10-01 | 31 days | 0 | None | None | Energy production was limited by reduced load demand | N/A
Watt Place Rotoflo | 2025-11-01 | 30 days | 0 | None | None | There system produced as expected | N/A
Watt Place Rotoflo | 2025-12-01 | 17 days | 17-31, 14 days | Company closure | None | Energy production was limited by reduced load demand | N/A
Watt Place Rotoflo | 2026-01-01 | 28 days | 01-04, 4 days | Company closure | None | Energy production was limited by reduced load demand | N/A
Watt Place Rotoflo | 2026-02-01 | 28 days | 0 | None | None | There system produced as expected | N/A
Watt Place Rotoflo | 2026-03-01 | 31 days | 0 | None | None | Energy production was limited by reduced load demand | N/A
Watt Place Rotoflo | 2026-04-01 | 30 days | 0 | None | None | Energy production was limited by reduced load demand | N/A
Watt Place Rotoflo | 2026-05-01 | 31 days | 0 | None | None | There system produced as expected | N/A
Watt Place Rotoflo | 2026-08-01 | 30 days | 0 | None | None | Energy production was limited by reduced load demand | N/A
Watt Place Rotoflo | 2026-06-01 | 30 days | 0 | None | None | There system produced as expected | N/A
Watt Place Rotoflo | 2026-07-01 | 31 | 0 | None | None | Energy production was limited by reduced load demand | N/A
Zwartop Golf Course | 2024-09-01
Zwartop Golf Course | 2024-10-01
Zwartop Golf Course | 2024-11-01
Zwartop Golf Course | 2024-12-01
Zwartop Golf Course | 2025-01-01
Zwartop Golf Course | 2025-02-01 | Comms offline, No Billing meter
Zwartop Golf Course | 2025-03-01 | Comms offline, No Billing meter
Zwartop Golf Course | 2025-04-01 | Comms offline, No Billing meter
Zwartop Golf Course | 2025-05-01 | Comms offline, No Billing meter
Zwartop Golf Course | 2025-06-01 | Comms offline, No Billing meter
Zwartop Golf Course | 2025-07-01 | Comms offline, No Billing meter
Zwartop Golf Course | 2025-08-01
Zwartop Golf Course | 2025-09-01
Zwartop Golf Course | 2025-10-01
Zwartop Golf Course | 2025-11-01
Zwartop Golf Course | 2025-12-01
Zwartop Golf Course | 2026-01-01
Zwartop Golf Course | 2026-02-01
Zwartop Golf Course | 2026-03-01 | N/A
Zwartop Golf Course | 2026-04-01 | N/A
Zwartop Golf Course | 2026-05-01 | The system monitoring is offline
Zwartop Golf Course | 2026-08-01 | N/A | N/A | N/A | N/A | N/A | N/A
Zwartop Golf Course | 2026-06-01 | N/A | N/A | N/A | N/A | N/A | N/A
Zwartop Golf Course | 2026-07-01 | N/A | N/A | N/A | N/A | N/A | N/A
African Global Plastics | 2026-09-01 | 30 | 0 | None | None | Energy production was limited by load demand | N/A
Alpine Heath Residential | 2026-09-01 | 30 | 0 | None | None | Energy production was limited by load demand | N/A
Alpine Heath Resort | 2026-09-01 | 30 | 0 | None | None | The system performed poorly due to the load demand reduction, rainy and cloudy weather | N/A
Bendstore Plaza Shops | 2026-09-01 | 30 | 0 | None | None | Energy production was limited by load demand | N/A
Bendstore Spar | 2026-09-01 | 30 | 0 | None | None | The system performed poorly due to rainy and cloudy weather | N/A
Beyerskloof | 2026-09-01 | 30 | 0 | None | None | The system performed as expected | N/A
BP Parys | 2026-09-01 | 30 | 0 | None | None | The system performed poorly due to the load demand reduction, rainy and cloudy weather | N/A
Buffalo Rock | 2026-09-01 | 30 | 0 | None | None | The system performed poorly due to the load demand reduction | N/A
Checkers De Aar | 2026-09-01 | 30 | 0 | None | None | The system performed poorly due to the load demand reduction, rainy and cloudy weather | N/A
Checkers Lichtenburg | 2026-09-01 | 30 | 0 | None | None | The system performed poorly due to the load demand reduction, rainy and cloudy weather | N/A
Checkers Silverlakes Gen | 2026-09-01 | 30 | 0 | None | None | The system performed as expected | N/A
Checkers Silverlakes No Gen | 2026-09-01 | 30 | 0 | None | None | The system performed poorly due to rainy and cloudy weather | N/A
Checkrite Inanda | 2026-09-01 | 30 | 0 | None | None | The system performed poorly due to the load demand reduction, rainy and cloudy weather | N/A
Club Houghton | 2026-09-01 | 30 | 0 | None | None | Energy production was limited by load demand | N/A
Coldstar International | 2026-09-01 | 30 | 0 | None | None | The system performed as expected | N/A
Cultura Fresh | 2026-09-01 | 30 | 0 | None | None | The system performed poorly due to the load demand reduction, rainy and cloudy weather | N/A
Demco | 2026-09-01 | 30 | 0 | None | None | Energy production was limited by load demand | N/A
Engen Kaalfontein | 2026-09-01 | 30 | 0 | None | None | The system performed poorly due to the load demand reduction, rainy and cloudy weather | N/A
Engen Lotus Gardens | 2026-09-01 | 30 | 0 | None | None | The system performed as expected | N/A
Giba Gorge Main | 2026-09-01 | 30 | 0 | None | None | Energy production was limited by load demand | N/A
Giba Gorge Storage | 2026-09-01 | 30 | 0 | None | None | Energy production was limited by load demand | N/A
Golden Spot Resort | 2026-09-01 | 22 | 8 days,19th-27th | None | Internet connectivity issues | Missing data from 19th - 27th due to offline comms (per Sep kWh registration) | N/A
Golden Spot Shops | 2026-09-01 | 0 | 30 | System switched off | None | System switched off - client requested the system to be shut down (per Sep kWh registration) | N/A
Grootpan | 2026-09-01 | 30 | 0 | None | None | Energy production was limited by load demand | N/A
HB Dunn | 2026-09-01 | 30 | 0 | None | None | Energy production was limited by load demand | N/A
Helderberg Collage | 2026-09-01 | 30 | 0 | None | None | The system performed as expected | N/A
Hilston Rotoflo | 2026-09-01 | 30 | 0 | None | None | The system performed as expected | N/A
Huis Herfsblaar | 2026-09-01 | 30 | 2 day, 29-30th | Internet connectivity | None | The system performed poorly due to the load demand reduction, offline days, rainy and cloudy weather | N/A
IPID - Floor 4 | 2026-09-01 | 30 | 0 | None | None | The system performed as expected | N/A
IPID - Floor 6 | 2026-09-01 | 30 | 0 | None | None | Energy production was limited by load demand | N/A
Kool Village | 2026-09-01 | 30 | 0 | None | None | Energy production was limited by load demand | N/A
Makalali | 2026-09-01 | 30 | 0 | None | None | N/A | N/A
Mambha Cash & Carry | 2026-09-01 | 30 | 0 | None | None | The system performed poorly due to the load demand reduction, rainy and cloudy weather | N/A
Mathe Group Company | 2026-09-01 | 30 | 0 | None | None | The system performed poorly due to rainy and cloudy weather | N/A
Mdluli | 2026-09-01 | 30 | 0 | None | monitoring comms offline | Energy production was limited by load demand | N/A
Medipost | 2026-09-01 | 30 | 0 | None | None | The system performed as expected | N/A
Meredale Heights | 2026-09-01 | 30 | 0 | None | None | The system performed as expected | N/A
Monument Park Checkers | 2026-09-01 | 30 | 0 | None | None | The system performed as expected | N/A
Nkambeni Industrial | 2026-09-01 | N/A | N/A | N/A | N/A | N/A | N/A
Olievenhoutbosch 1 | 2026-09-01 | 30 | 0 | None | None | The system performed poorly due to rainy and cloudy weather | N/A
Olievenhoutbosch 2 | 2026-09-01 | 30 | 0 | None | None | The system performed poorly due to rainy and cloudy weather | N/A
Opal Students | 2026-09-01 | 30 | 0 | None | None | The system performed as expected | kWh based on inverter readings (per Sep kWh registration)
Orthochem Bethlehem | 2026-09-01 | 30 | 0 | None | None | Energy production was limited by load demand | N/A
Plastiplate | 2026-09-01 | 30 | 0 | None | None | Energy production was limited by load demand | N/A
PNB Unlimited | 2026-09-01 | 30 | 0 | None | None | Energy production was limited by load demand | N/A
Q-lity Meat | 2026-09-01 | 0 | 30 | System switched off | None | System off due to business closure (per Sep kWh registration) | N/A
Quintondale | 2026-09-01 | 30 | 0 | None | None | Energy production was limited by load demand | N/A
Riverside Lodge | 2026-09-01 | 30 | 0 | None | None | The system performed as expected | N/A
Roan Foods | 2026-09-01 | 30 | 0 | None | None | Energy production was limited by load demand | N/A
Sakhumnotho | 2026-09-01 | N/A | N/A | N/A | N/A | N/A | N/A
SaveMore Alldays - Store | 2026-09-01 | 30 | 0 | None | None | Energy production was limited by load demand | N/A
Savemore Liquor Alldays | 2026-09-01 | 30 | 0 | None | None | Energy production was limited by load demand | N/A
Saverite Durban | 2026-09-01 | 30 | 0 | None | None | The system performed poorly due to the load demand reduction, rainy and cloudy weather | N/A
Saverite PMB | 2026-09-01 | 30 | 0 | None | None | The system performed poorly due to the load demand reduction, rainy and cloudy weather | N/A
Secunda Plaza choppies | 2026-09-01 | 0 | 30 | Grid unavailable | N/A | System off due to grid unavailability (per Sep kWh registration) | N/A
Secunda Plaza Shops | 2026-09-01 | 30 | 0 | None | None | The system performed as expected | N/A
Shoprite Dube | 2026-09-01 | 30 | 0 | None | None | The system performed as expected | N/A
Shoprite Ekhaya | 2026-09-01 | 30 | 0 | None | None | The system performed poorly due to rainy and cloudy weather | N/A
Shoprite Hillbrow | 2026-09-01 | 30 | 0 | None | None | The system performed poorly due to morning shading from the 1st to the 19th | N/A
Shoprite Ladybrand | 2026-09-01 | 30 | 0 | None | None | The system performed poorly due to the load demand reduction, rainy and cloudy weather | N/A
Shoprite Mayfair | 2026-09-01 | 30 | 0 | None | None | The system performed poorly due to the load demand reduction, rainy and cloudy weather | N/A
Shoprite Mini Ganyesa | 2026-09-01 | 30 | 0 | None | None | The system performed poorly due to the load demand reduction | N/A
Shoprite Naledi | 2026-09-01 | 30 | 0 | None | None | The system performed poorly due to rainy and cloudy weather | N/A
Shoprite Newlands | 2026-09-01 | 30 | 0 | None | None | The system performed as expected | N/A
Shoprite SRH Bizana | 2026-09-01 | 30 | 0 | None | None | The system performed poorly due to the load demand reduction, rainy and cloudy weather | N/A
Shoprite Thokoza | 2026-09-01 | 30 | 0 | None | None | The system performed poorly due to the load demand reduction, rainy and cloudy weather | N/A
Spring Glade | 2026-09-01 | 30 | 0 | None | None | Energy production was limited by load demand | N/A
SR Morula TF 1 | 2026-09-01 | 30 | 0 | None | None | The system performed poorly due to the load demand reduction, rainy and cloudy weather | N/A
SR Morula TF 1 - Shoprite | 2026-09-01 | 30 | 0 | None | None | The system performed poorly due to rainy and cloudy weather | N/A
SR Morula TF 2 | 2026-09-01 | 30 | 0 | None | None | The system performed poorly due to the load demand reduction, rainy and cloudy weather | N/A
Thakadu Industrial | 2026-09-01 | N/A | N/A | N/A | N/A | N/A | N/A
The Alec | 2026-09-01 | 30 | 0 | None | None | The system performed poorly due to the load demand reduction, rainy and cloudy weather | N/A
Three Peaks | 2026-09-01 | 30 | 0 | None | None | The system performed as expected | N/A
Tlou Integrated Tech |  | 30 | 0 | None | None | The system performed poorly due to the load demand reduction, rainy and cloudy weather | N/A
TPF Foods | 2026-09-01 | 30 | 0 | None | None | The system performed poorly due to the load demand reduction, rainy and cloudy weather | N/A
Trouw Nutrition | 2026-09-01 | 2 | 28 days | client roof maintanance | None | PV system isolated from the 2nd - 30th due to client roof leakage maintenance; energy production estimated from Sep 2025 readings (per Sep kWh registration) | N/A
U Save Botrivier | 2026-09-01 | 30 | 0 | None | None | Energy production was limited by load demand | N/A
Usave Naboomspruit | 2026-09-01 | 30 | 0 | None | None | Energy production was limited by load demand | N/A
Watt Place Rotoflo | 2026-09-01 | 30 | 0 | None | None | The system performed poorly due to the load demand reduction, rainy and cloudy weather | N/A
Zwartop Golf Course | 2026-09-01 | N/A | N/A | N/A | N/A | N/A | N/A

## CountryList (hidden)
Algeria
Angola
Benin
Botswana
Burkina Faso
Burundi
Cabo Verde
Cameroon
Central African Republic
Chad
Comoros
Democratic Republic of the Congo
Republic of the Congo
Djibouti
Egypt
Equatorial Guinea
Eritrea
Eswatini
Ethiopia
Gabon
Gambia
Ghana
Guinea
Guinea-Bissau
Ivory Coast
Kenya
Lesotho
Liberia
Libya
Madagascar
Malawi
Mali
Mauritania
Mauritius
Morocco
Mozambique
Namibia
Niger
Nigeria
Rwanda
Sao Tome and Principe
Senegal
Seychelles
Sierra Leone
Somalia
South Africa
South Sudan
Sudan
Tanzania
Togo
Tunisia
Uganda
Zambia
Zimbabwe