## Cables Sizes
|  |  | PROJECT NAME AC POWER CABLE SCHEDULE | [11 empty] | Project Name | [5 empty] | Date
[15 empty] | Project Number | [5 empty] | Revision |  | 00
[15 empty] | Document Number | [5 empty] | Designed
[15 empty] | Address | [5 empty] | Checked
[15 empty] | Coordinates | [5 empty] | Approved
[15 empty] | Client | [5 empty] | Rev. Description
AC CABLES – SIZING TO SANS 10142-1 / IEC 60364-5-52
| AC Cable Inputs | [13 empty] | Calculated Outputs (SANS 10142-1) | [11 empty] | Calculation helpers – do not edit
# | Design Current Ib (A) | Termination Point A | Termination Point B | Installation Method | Cable Distance (m) | System Voltage (V) | Cable Protection | Conductor Insulation | Conductor (Cu/Al) | Cores | Other Derating Ca (ambient/soil) (blank = default) | Spacing between runs (blank = touching) | Fault Level Ik (kA) (blank = not checked) | Fault Clearing Time t (s) (blank = device default) | Cables in Parallel | Recommended Size (mm2) | Grouping Factor Cg (runs) | Cable CCC – total (A) | Voltage Drop (V) | Voltage Drop (%) | Circuit Breaker Size (A) | Breaker Type | Trip Setting Ir (A) | Earth Conductor (mm2) | Cable SC Withstand per run (kA) | Status | Inputs OK | Ref Method | Loaded | CCC col | Insul fac | Cu/Al fac | Ca used | Breaker raw | Req base CCC | mV col | Al mV fac | Max base mV | Runs needed | Size by CCC | Size by VD | Rec size | Grp key | Runs by CCC | Runs by VD | Cg used | k | t used | Min S for SC | Size by SC | Single-core | CCC key | Input issue
1 | 2000 | A | B | On Tray/Ladder | 200 | 400 | Armoured | XLPE | Copper | Single-core (3ph trefoil) |  |  |  |  | 5 | 630 | 0.75 | 4104 | 11.6 | 2.9% | 2500 | ACB | 2500 | 400 | Not checked | OK | TRUE | F | 3 | 10 | 1.28 | 1 | 1 | 2500 | 1953.125 | 4 | 1 | 0.03 | 5 | 300 | 630 | 630 | AIR-TRAY¦Touching | 3 | 5 | 0.75 | 143 | 0.4 |  | 0 | TRUE | F¦3
2
3
4
5
6
7
8
9
10
Notes / Assumptions:
• Ratings from 'Cable Data': PVC multicore ≤ 300 mm² per SANS 10142-1 / IEC 60364-5-52 (XLPE and Al via factors on 'SANS Data'); Rubber = H07RN-F (EN 50525-2-21) manufacturer data, 60°C, 1.5–630 mm². VERIFY all values.
• Protection per IEC 60364-4-43 cl. 433.1 / SANS 10142-1: Ib × SF ≤ Ir ≤ In and Ir ≤ Iz. Safety factor SF (default 1.25) on 'SANS Data' X52. Frame In = smallest standard rating ≥ Ib × SF (6–6300 A). Trip setting Ir (col X) = smallest setting ≥ Ib × SF (MCB fixed; MCCB 0.7–1.0 In; ACB 0.4–1.0 In); cable sized to Ir. Ranges editable on 'SANS Data' W47:Z50.
• Phase from cores: 2-core = single-phase (use 230 V); 3/4-core = three-phase (use 400 V). Status shows CHECK if the voltage doesn't suit the cores.
• Derating: Iz = It × Ca × Cg. Cg for parallel runs is applied automatically (IEC 60364-5-52 B.52.17–B.52.19) from installation method + spacing (col M). Column L = other factors only (ambient/soil temperature, grouping with OTHER circuits).
• Parallel runs (IEC 60364-5-52 cl. 523.7): same conductor, size, length and route. Practical max runs and max size per run set on 'SANS Data'. Output size, earth and SC withstand are per run; CCC is the total for the set.
• Earth conductor per IEC 60364-5-54 Table 54.2 (same material): S ≤ 16 → S; 16–35 → 16; > 35 → S/2. Per run. Armour may serve as earth if verified by adiabatic check.
• Status: FAIL = invalid inputs, out of range, volt drop over limit, breaker < Ib, CCC < breaker, or cable SC withstand < fault level.
• Short circuit (IEC 60364-4-43 cl. 434.5.2): S ≥ Ik·√t / k, full prospective Ik on each run (conservative). k from Table 43A. Default t by device (MCB/MCCB 0.1 s, ACB 0.4 s short-time delay). For current-limiting MCB/MCCB the device I²t let-through gives a smaller, more accurate result.
• Large currents (design up to 2500 A, breaker up to 3200 A with SF 1.25): select 'Single-core (3ph trefoil)' in free air, on tray/ladder, clipped or surface – PVC/XLPE (IEC 60364-5-52 B.52.10) or H07RN-F rubber, up to 630 mm², max 6 per phase. Single-core is not offered in conduit or buried (use multicore, or busbar trunking for large buried/enclosed feeders). H07RN-F 3ph ratings derived (Fac_Trefoil) – verify.
• Spacing options: in air – Touching or 2 cable dia (Cg = 1); buried direct – Touching/1 cable dia/0.125/0.25/0.5 m; in ducts – Touching/0.25/0.5/1.0 m.
• Rubber flex (H07RN-F) is copper only and not rated in conduit or buried – Status shows the reason. For buried large feeders use armoured PVC/XLPE (add single-core tables) or busbar. Single-core parallel sets: use the multicore grouping factors (conservative); earth shown is per run – a common CPC sized by adiabatic check may be used.

## DC Cable Sizes
|  |  | PROJECT NAME DC POWER CABLE SCHEDULE | [6 empty] | Project Name |  |  |  |  | Date
[10 empty] | Project Number |  |  |  |  | Revision |  | 00
[10 empty] | Document Number |  |  |  |  | Designed
[10 empty] | Address |  |  |  |  | Checked
[10 empty] | Coordinates |  |  |  |  | Approved
[10 empty] | Client |  |  |  |  | Rev. Description
DC / PV CABLES – SIZING
| DC Cable Inputs | [8 empty] | Calculated Outputs (DC / PV)
# | Circuit Type | Current Input (A) – Isc per string for PV | Strings in Parallel (PV Array) | Installation Method | Cable Distance one-way (m) | Modules per String (PV) | Module Voltage Vmp (V) | System Voltage (V DC) – if no modules entered | Derating (blank = default) | Total System Voltage (V DC) | Design Current Ib (A) | Cables in Parallel | Recommended Size (mm2) | Cable CCC – total (A) | Voltage Drop (V) | Voltage Drop (%) | DC MCB/ Fuse Size (A) | Status | Inputs OK | Strings used | Ib mult | Min In mult | VD limit | Method col | Derate used | Ib | I for VD | Min In | Prot raw | Req CCC | R temp fac | Max R single (ohm/km) | Runs needed | Size by CCC | Size by VD | Rec size | Max size | Max runs
1 | PV Array | 16 | 1 | Free Air (single) | 55 | 18 | 50 | 900 |  | 900 | 20 | 1 | 6 | 70 | 7.6078 | 0.8453% | 25 | OK | TRUE | 1 | 1.25 | 1.25 | 0.01 | 1 | 1 | 20 | 16 | 20 | 25 | 25 | 1.2751 | 4.0104 | 1 | 1.5 | 6 | 6 | 10 | 1
2 | PV String | 16 | 1 | Free Air (single) | 100 | 18 | 50 | 900 |  | 900 | 20 | 1 | 10 | 98 | 7.9566 | 0.8841% | 25 | OK | TRUE | 1 | 1.25 | 1.5 | 0.01 | 1 | 1 | 20 | 16 | 24 | 25 | 25 | 1.2751 | 2.2057 | 1 | 1.5 | 10 | 10 | 10 | 1
3
4
5
6
7
8
9
10
Notes / Assumptions:
• PV cable ratings: single-core tinned Cu, 120°C conductor at 60°C ambient (EN 50618 Table A.3). VERIFY on 'SANS Data' against manufacturer data and SANS 10142-1-2 / IEC 62548.
• Ib = current input x strings x multiplier (PV: 1.25 x Isc; Battery/General: 1.0). Multipliers, minimum protection and VD limits per circuit type are editable on 'SANS Data'.
• Protection = smallest standard DC rating > Ib and ≥ minimum (PV string ≥ 1.5 x Isc). Check it does not exceed the module's max series fuse rating.
• Recommended size = smallest size whose derated CCC > protection rating AND meets the VD limit, so Ib < In < Iz.
• Volt drop = 2 x one-way length x current x R, with R corrected to the conductor temp on 'SANS Data' (default 90°C). VD current = input x strings (no 1.25 factor). VD % uses Total System Voltage.
• Ratings are for one cable per circuit pole. Use the Derating column for conduit, grouping, buried runs or parallel cables.
• Battery / General DC: parallel cables are used automatically when no single size meets CCC or volt drop (max runs on 'SANS Data').
• Status: FAIL = invalid inputs, out of range, volt drop over limit, protection not > Ib, or CCC not > protection.
• Total System Voltage = Modules per String x Module Vmp when both are entered; otherwise the manual System Voltage. FAIL if above the max DC voltage on 'SANS Data' (check Voc at min. temperature separately).
• PV String / PV Array: single cable only, max 10 mm² (manufacturer limit). If 10 mm² can't meet the VD limit, Status shows FAIL – volt drop (shorten route or re-string). Limits per circuit type are on 'SANS Data'.

## SANS Data
SANS 10142-1 / IEC 60364-5-52 Reference Data
VERIFY all values against your official SANS 10142-1 copy. Every cell is editable; the calculator references these.
Factors / Assumptions
XLPE CCC factor (x PVC 70C) | 1.28
Aluminium CCC factor (x Cu) | 0.78
Aluminium mV.A.m factor (x Cu) | 1.64
Default other derating Ca (ambient/soil/other circuits) if circuit cell blank | 1
Voltage drop limit (%) | 3%
Max cables in parallel (practical; ≤ 6 = IEC grouping table limit) | 6
Max cable size per run (mm2) | 630
Rubber factor (not used – superseded by 'Cable Data') | 0.87
CCC base table: PVC insulated, Copper, multicore (Amps) - ref method ¦ loaded conductors | [19 empty] | Grouping factor Cg for parallel runs / circuits – IEC 60364-5-52 Tables B.52.17 (in air), B.52.18 (direct in ground), B.52.19 (in ducts). Multicore cables. VERIFY against SANS 10142-1.
Size (mm2) | B¦2 | B¦3 | C¦2 | C¦3 | E¦2 | E¦3 | D¦2 | D¦3 | Size (mm2) | 1ph mV/A/m | 3ph mV/A/m | Std Breaker (A) | Device Type | Install Method | Ref Method | Grouping Scheme |  | Loaded | Single-core | Key | Scheme | Spacing | 1 | 2 | 3 | 4 | 5 | 6 | Runs x Cg → | 1 | 2 | 3 | 4 | 5 | 6 | Spacing options
1.5 | 16.5 | 15 | 19.5 | 17.5 | 22 | 18.5 | 22 | 18 | 1.5 | 29 | 25.1147 | 6 | MCB | Free Air | E | AIR-LADDER | Two | 2 | 0 | AIR-BUNCH¦Touching | AIR-BUNCH | Touching | 1 | 0.8 | 0.7 | 0.65 | 0.6 | 0.57 |  | 1 | 1.6 | 2.1 | 2.6 | 3 | 3.42 | Touching
2.5 | 23 | 20 | 27 | 24 | 30 | 25 | 29 | 24 | 2.5 | 18 | 15.5885 | 10 | MCB | On Tray/Ladder | E | AIR-TRAY | Three | 3 | 0 | AIR-WALL¦Touching | AIR-WALL | Touching | 1 | 0.85 | 0.79 | 0.75 | 0.73 | 0.72 |  | 1 | 1.7 | 2.37 | 3 | 3.65 | 4.32 | 1 cable dia
4 | 30 | 27 | 36 | 32 | 40 | 34 | 38 | 31 | 4 | 11 | 9.5263 | 16 | MCB | Clipped Direct | C | AIR-WALL | Four | 3 | 0 | AIR-WALL¦2 cable dia | AIR-WALL | 2 cable dia | 1 | 1 | 1 | 1 | 1 | 1 |  | 1 | 2 | 3 | 4 | 5 | 6 | 2 cable dia
6 | 38 | 34 | 46 | 41 | 51 | 43 | 47 | 39 | 6 | 7.3 | 6.322 | 20 | MCB | Surface | C | AIR-WALL | Single-core (1ph) | 2 | 1 | AIR-TRAY¦Touching | AIR-TRAY | Touching | 1 | 0.88 | 0.82 | 0.77 | 0.75 | 0.73 |  | 1 | 1.76 | 2.46 | 3.08 | 3.75 | 4.38 | 0.125 m
10 | 52 | 46 | 63 | 57 | 70 | 60 | 63 | 52 | 10 | 4.4 | 3.8105 | 25 | MCB | In Conduit | B | AIR-BUNCH | Single-core (3ph trefoil) | 3 | 1 | AIR-TRAY¦2 cable dia | AIR-TRAY | 2 cable dia | 1 | 1 | 1 | 1 | 1 | 1 |  | 1 | 2 | 3 | 4 | 5 | 6 | 0.25 m
16 | 69 | 62 | 85 | 76 | 94 | 80 | 81 | 67 | 16 | 2.8 | 2.4249 | 32 | MCB | In Trunking | B | AIR-BUNCH |  |  |  | AIR-LADDER¦Touching | AIR-LADDER | Touching | 1 | 0.87 | 0.82 | 0.8 | 0.8 | 0.79 |  | 1 | 1.74 | 2.46 | 3.2 | 4 | 4.74 | 0.5 m
25 | 90 | 80 | 112 | 96 | 119 | 101 | 104 | 86 | 25 | 1.75 | 1.5155 | 40 | MCB | Buried | D | GND-DIRECT |  |  |  | AIR-LADDER¦2 cable dia | AIR-LADDER | 2 cable dia | 1 | 1 | 1 | 1 | 1 | 1 |  | 1 | 2 | 3 | 4 | 5 | 6 | 1.0 m
35 | 111 | 99 | 138 | 119 | 148 | 126 | 125 | 103 | 35 | 1.25 | 1.0825 | 50 | MCB | In Ground Duct | D | GND-DUCT |  |  |  | GND-DIRECT¦Touching | GND-DIRECT | Touching | 1 | 0.75 | 0.65 | 0.6 | 0.55 | 0.5 |  | 1 | 1.5 | 1.95 | 2.4 | 2.75 | 3
50 | 133 | 118 | 168 | 144 | 180 | 153 | 148 | 122 | 50 | 0.94 | 0.81406 | 63 | MCB | [6 empty] | GND-DIRECT¦1 cable dia | GND-DIRECT | 1 cable dia | 1 | 0.8 | 0.7 | 0.6 | 0.55 | 0.55 |  | 1 | 1.6 | 2.1 | 2.4 | 2.75 | 3.3
70 | 168 | 149 | 213 | 184 | 232 | 196 | 183 | 151 | 70 | 0.63 | 0.5456 | 80 | MCCB | [6 empty] | GND-DIRECT¦0.125 m | GND-DIRECT | 0.125 m | 1 | 0.85 | 0.75 | 0.7 | 0.65 | 0.6 |  | 1 | 1.7 | 2.25 | 2.8 | 3.25 | 3.6
95 | 201 | 179 | 258 | 223 | 282 | 238 | 216 | 179 | 95 | 0.47 | 0.40703 | 100 | MCCB | [6 empty] | GND-DIRECT¦0.25 m | GND-DIRECT | 0.25 m | 1 | 0.9 | 0.8 | 0.75 | 0.7 | 0.7 |  | 1 | 1.8 | 2.4 | 3 | 3.5 | 4.2
120 | 232 | 206 | 299 | 259 | 328 | 276 | 246 | 203 | 120 | 0.38 | 0.32909 | 125 | MCCB | [6 empty] | GND-DIRECT¦0.5 m | GND-DIRECT | 0.5 m | 1 | 0.9 | 0.85 | 0.8 | 0.8 | 0.8 |  | 1 | 1.8 | 2.55 | 3.2 | 4 | 4.8
150 | 266 | 236 | 344 | 299 | 379 | 319 | 278 | 230 | 150 | 0.3 | 0.25981 | 160 | MCCB | [6 empty] | GND-DUCT¦Touching | GND-DUCT | Touching | 1 | 0.85 | 0.75 | 0.7 | 0.65 | 0.6 |  | 1 | 1.7 | 2.25 | 2.8 | 3.25 | 3.6
185 | 303 | 268 | 392 | 341 | 434 | 364 | 312 | 258 | 185 | 0.25 | 0.21651 | 200 | MCCB | [6 empty] | GND-DUCT¦0.25 m | GND-DUCT | 0.25 m | 1 | 0.9 | 0.85 | 0.8 | 0.8 | 0.8 |  | 1 | 1.8 | 2.55 | 3.2 | 4 | 4.8
240 | 356 | 315 | 461 | 403 | 514 | 430 | 361 | 297 | 240 | 0.195 | 0.16887 | 250 | MCCB | [6 empty] | GND-DUCT¦0.5 m | GND-DUCT | 0.5 m | 1 | 0.95 | 0.9 | 0.85 | 0.85 | 0.8 |  | 1 | 1.9 | 2.7 | 3.4 | 4.25 | 4.8
300 | 409 | 361 | 530 | 464 | 593 | 497 | 408 | 336 | 300 | 0.16 | 0.13856 | 315 | MCCB | [6 empty] | GND-DUCT¦1.0 m | GND-DUCT | 1.0 m | 1 | 0.95 | 0.95 | 0.9 | 0.9 | 0.9 |  | 1 | 1.9 | 2.85 | 3.6 | 4.5 | 5.4
[12 empty] | 400 | MCCB
SUPERSEDED – not used by the calculator. Rubber ratings now from H07RN-F manufacturer data on 'Cable Data'. | [11 empty] | 500 | MCCB | [6 empty] | Short-circuit k factor (A·√s/mm²) – IEC 60364-4-43 Table 43A, line conductors ≤ 300 mm². VERIFY.
Size (mm2) | B¦2 | B¦3 | C¦2 | C¦3 | E¦2 | E¦3 | D¦2 | D¦3 |  |  |  | 630 | MCCB | [6 empty] | Key | Conductor | Insulation | k
1.5 | 14.4 | 13.1 | 17 | 15.2 | 19.1 | 16.1 | 19.1 | 15.7 |  |  |  | 800 | MCCB | [6 empty] | Copper¦PVC | Copper | PVC | 115
2.5 | 20 | 17.4 | 23.5 | 20.9 | 26.1 | 21.8 | 25.2 | 20.9 |  |  |  | 1000 | MCCB | [6 empty] | Copper¦XLPE | Copper | XLPE | 143
4 | 26.1 | 23.5 | 31.3 | 27.8 | 34.8 | 29.6 | 33.1 | 27 |  |  |  | 1250 | MCCB | [6 empty] | Copper¦Rubber | Copper | Rubber | 141
6 | 33.1 | 29.6 | 40 | 35.7 | 44.4 | 37.4 | 40.9 | 33.9 |  |  |  | 1600 | ACB | [6 empty] | Aluminium¦PVC | Aluminium | PVC | 76
10 | 45.2 | 40 | 54.8 | 49.6 | 60.9 | 52.2 | 54.8 | 45.2 |  |  |  | 2000 | ACB | [6 empty] | Aluminium¦XLPE | Aluminium | XLPE | 94
16 | 60 | 53.9 | 74 | 66.1 | 81.8 | 69.6 | 70.5 | 58.3 |  |  |  | 2500 | ACB | [6 empty] | Aluminium¦Rubber | Aluminium | Rubber | 93
25 | 78.3 | 69.6 | 97.4 | 83.5 | 103.5 | 87.9 | 90.5 | 74.8 |  |  |  | 3200 | ACB
35 | 96.6 | 86.1 | 120.1 | 103.5 | 128.8 | 109.6 | 108.8 | 89.6 |  |  |  | 4000 | ACB | [6 empty] | Default fault clearing time t (s) by device – used when circuit cell blank. Adiabatic S ≥ Ik·√t / k valid 0.1–5 s; below 0.1 s, 0.1 s is used (conservative) – or check device I²t let-through.
50 | 115.7 | 102.7 | 146.2 | 125.3 | 156.6 | 133.1 | 128.8 | 106.1 |  |  |  | 5000 | ACB | [6 empty] | Device | Default t (s)
70 | 146.2 | 129.6 | 185.3 | 160.1 | 201.8 | 170.5 | 159.2 | 131.4 |  |  |  | 6300 | ACB | [6 empty] | MCB | 0.1
95 | 174.9 | 155.7 | 224.5 | 194 | 245.3 | 207.1 | 187.9 | 155.7 | [11 empty] | MCCB | 0.1
120 | 201.8 | 179.2 | 260.1 | 225.3 | 285.4 | 240.1 | 214 | 176.6 |  |  |  | Device type per IEC 60898-1 (MCB ≤ 63 A) / IEC 60947-2 (MCCB 80–1250 A, ACB 1600–6300 A). MCCB also available to 1600 A – edit column P to suit. ACB rating = frame/rating plug; set Ir ≤ Iz. | [7 empty] | ACB | 0.4 | ACB with short-time delay for selectivity (typ. 0.1–0.5 s)
150 | 231.4 | 205.3 | 299.3 | 260.1 | 329.7 | 277.5 | 241.9 | 200.1
185 | 263.6 | 233.2 | 341 | 296.7 | 377.6 | 316.7 | 271.4 | 224.5 | [11 empty] | Trip-unit current setting Ir by device – Ir = smallest setting ≥ Ib (Ib ≤ Ir ≤ In); cable sized to Ir (IEC 60364-4-43 cl. 433.1). Edit to match chosen breakers.
240 | 309.7 | 274.1 | 401.1 | 350.6 | 447.2 | 374.1 | 314.1 | 258.4 | [11 empty] | Device | Ir min (× In) | Ir step (× In) | Basis
300 | 355.8 | 314.1 | 461.1 | 403.7 | 515.9 | 432.4 | 355 | 292.3 | [11 empty] | MCB | 1 | 1 | Fixed – Ir = In
[20 empty] | MCCB | 0.7 | 0.05 | Thermal-magnetic, adjustable 0.7–1.0 In (typical)
[20 empty] | ACB | 0.4 | 0.01 | Electronic trip unit, 0.4–1.0 In (typical)
DC / SOLAR PV REFERENCE DATA (used by 'DC Cable Sizes')
VERIFY against SANS 10142-1-2 / IEC 62548 / EN 50618 and the cable manufacturer's data. | [19 empty] | Breaker safety factor (× Ib) | 1.25 | Breaker frame In and trip setting Ir must be ≥ Ib × this factor (1.25 = 80% continuous loading). Set 1.00 for none.
DC Factors / Assumptions
Default DC derating (if circuit cell blank) | 1
Conductor temp for VD resistance (°C) | 90
Copper resistance temp coefficient (/°C) | 0.00393
Max DC cables in parallel | 4
Max DC system voltage (V) | 1500
DC circuit types
Circuit Type | Ib multiplier (x current input) | Min protection (x current input) | VD limit (%) | Basis | Max cable size (mm2) | Max cables in parallel
PV String | 1.25 | 1.5 | 1% | Input = string Isc(STC). IEC 62548: Iz ≥ 1.25 Isc; string fuse ≥ 1.5 Isc | 10 | 1
PV Array | 1.25 | 1.25 | 1% | Input = string Isc x strings. Iz ≥ 1.25 Isc array | 10 | 1
Battery | 1 | 1 | 1% | Input = max battery charge/discharge current | 240 | 4
General DC | 1 | 1 | 3% | Input = design current Ib | 240 | 4
Solar PV cable CCC (A) – single-core, tinned Cu, 120°C conductor, 60°C ambient (EN 50618 Table A.3) + DC resistance at 20°C (IEC 60228 class 5)
Size (mm2) | Free Air (single) | On Surface (single) | On Surface (2 adjacent) | R20 (ohm/km) |  | Std DC Fuse/Breaker (A)
1.5 | 30 | 29 | 24 | 13.7 |  | 1
2.5 | 41 | 39 | 33 | 8.21 |  | 2
4 | 55 | 52 | 44 | 5.09 |  | 3
6 | 70 | 67 | 57 | 3.39 |  | 4
10 | 98 | 93 | 79 | 1.95 |  | 5
16 | 132 | 125 | 107 | 1.24 |  | 6
25 | 176 | 167 | 142 | 0.795 |  | 8
35 | 218 | 207 | 176 | 0.565 |  | 10
50 | 276 | 262 | 221 | 0.393 |  | 12
70 | 347 | 330 | 278 | 0.277 |  | 15
95 | 416 | 395 | 333 | 0.21 |  | 16
120 | 488 | 464 | 390 | 0.164 |  | 20
150 | 566 | 538 | 453 | 0.132 |  | 25
185 | 644 | 612 | 515 | 0.108 |  | 30
240 | 775 | 736 | 620 | 0.0817 |  | 32
40
50
63
80
100
125
160
200
250
315
400
500
630
800
1000
1250
1600

## Cable Data
Cable Lookup Tables – used by the AC calculator ('Cables Sizes')
PVC values link to 'SANS Data' (edit them there). Rubber values: H07RN-F manufacturer data (60°C conductor, 30°C ambient, free air / on surface). VERIFY against SANS 10142-1.
Current-carrying capacity It (A) – key = Ref method ¦ loaded conductors (F = single-core in air/on surface) | [20 empty] | Voltage drop (mV/A/m) – used by the calculator
| PVC 70°C copper (XLPE via factor on 'SANS Data') | [9 empty] | Rubber 60°C H07RN-F copper (EN 50525-2-21) | [9 empty] | PVC / XLPE (from 'SANS Data') |  |  |  | Rubber 60°C H07RN-F
Size (mm2) | B¦2 | B¦3 | C¦2 | C¦3 | E¦2 | E¦3 | D¦2 | D¦3 | F¦2 | F¦3 | B¦2 | B¦3 | C¦2 | C¦3 | E¦2 | E¦3 | D¦2 | D¦3 | F¦2 | F¦3 | Multi 1ph | Multi 3ph | 1-core 1ph | 1-core 3ph | Multi 1ph | Multi 3ph | 1-core 1ph | 1-core 3ph
1.5 | 16.5 | 15 | 19.5 | 17.5 | 22 | 18.5 | 22 | 18 |  |  |  |  | 16 | 16 | 16 | 16 |  |  |  |  | 29 | 25.1147 |  |  | 32 | 27
2.5 | 23 | 20 | 27 | 24 | 30 | 25 | 29 | 24 |  |  |  |  | 25 | 20 | 25 | 20 |  |  |  |  | 18 | 15.5885 |  |  | 19 | 16
4 | 30 | 27 | 36 | 32 | 40 | 34 | 38 | 31 |  |  |  |  | 30 | 26 | 30 | 26 |  |  |  |  | 11 | 9.5263 |  |  | 12 | 10
6 | 38 | 34 | 46 | 41 | 51 | 43 | 47 | 39 |  |  |  |  | 39 | 34 | 39 | 34 |  |  |  |  | 7.3 | 6.322 |  |  | 7.8 | 6.7
10 | 52 | 46 | 63 | 57 | 70 | 60 | 63 | 52 |  |  |  |  | 51 | 47 | 51 | 47 |  |  |  |  | 4.4 | 3.8105 |  |  | 4.6 | 4
16 | 69 | 62 | 85 | 76 | 94 | 80 | 81 | 67 |  |  |  |  | 73 | 63 | 73 | 63 |  |  |  |  | 2.8 | 2.4249 |  |  | 2.9 | 2.5
25 | 90 | 80 | 112 | 96 | 119 | 101 | 104 | 86 | 131 | 110 |  |  | 97 | 83 | 97 | 83 |  |  |  |  | 1.75 | 1.5155 | 1.8 | 1.5 | 1.85 | 1.55
35 | 111 | 99 | 138 | 119 | 148 | 126 | 125 | 103 | 162 | 137 |  |  |  | 102 |  | 102 |  |  | 140 | 119 | 1.25 | 1.0825 | 1.3 | 1.1 |  | 1.15 | 1.32 | 1.1432
50 | 133 | 118 | 168 | 144 | 180 | 153 | 148 | 122 | 196 | 167 |  |  |  | 124 |  | 124 |  |  | 175 | 149 | 0.94 | 0.81406 | 0.95 | 0.8 |  | 0.84 | 0.93 | 0.8054
70 | 168 | 149 | 213 | 184 | 232 | 196 | 183 | 151 | 251 | 216 |  |  |  | 158 |  | 158 |  |  | 216 | 184 | 0.63 | 0.5456 | 0.65 | 0.55 |  | 0.58 | 0.67 | 0.58024
95 | 201 | 179 | 258 | 223 | 282 | 238 | 216 | 179 | 304 | 264 |  |  |  | 192 |  | 192 |  |  | 258 | 219 | 0.47 | 0.40703 | 0.49 | 0.41 |  | 0.44 | 0.53 | 0.45899
120 | 232 | 206 | 299 | 259 | 328 | 276 | 246 | 203 | 352 | 308 |  |  |  | 222 |  | 222 |  |  | 302 | 257 | 0.38 | 0.32909 | 0.39 | 0.33 |  | 0.36 | 0.43 | 0.37239
150 | 266 | 236 | 344 | 299 | 379 | 319 | 278 | 230 | 406 | 356 |  |  |  | 255 |  | 255 |  |  | 347 | 295 | 0.3 | 0.25981 | 0.33 | 0.29 |  | 0.3 | 0.36 | 0.31177
185 | 303 | 268 | 392 | 341 | 434 | 364 | 312 | 258 | 463 | 409 |  |  |  | 291 |  | 291 |  |  | 394 | 335 | 0.25 | 0.21651 | 0.28 | 0.25 |  | 0.26 | 0.32 | 0.27713
240 | 356 | 315 | 461 | 403 | 514 | 430 | 361 | 297 | 546 | 485 |  |  |  | 343 |  | 343 |  |  | 471 | 400 | 0.195 | 0.16887 | 0.24 | 0.21 |  | 0.21 | 0.27 | 0.23383
300 | 409 | 361 | 530 | 464 | 593 | 497 | 408 | 336 | 629 | 561 |  |  |  | 394 |  | 394 |  |  | 541 | 460 | 0.16 | 0.13856 | 0.21 | 0.185 |  | 0.185 | 0.24 | 0.20785
400 | [8 empty] | 754 | 656 | [8 empty] | 644 | 547 |  |  | 0.195 | 0.17 |  |  | 0.21 | 0.18187
500 | [8 empty] | 868 | 749 | [8 empty] | 738 | 627 |  |  | 0.18 | 0.155 |  |  | 0.2 | 0.17321
630 | [8 empty] | 1005 | 855 | [8 empty] | 861 | 732 |  |  | 0.17 | 0.145 |  |  | 0.185 | 0.16021
Factors
| 0.85 | Single-core 3-phase trefoil rating factor (x 2-cable single-phase rating). DERIVED ASSUMPTION – datasheet gives single-phase only. Replace F¦3 with manufacturer 3-phase trefoil ratings when available.
Notes: H07RN-F (EN 50525-2-21) is a flexible cable for free air / on surface / tray (ref methods C, E, F). No ratings are given for conduit (B) or buried (D) – the calculator blocks those. Copper only. Datasheet ratings per BS 7671 Table 4F1A / IEC 60364-5-52. Ambient derating (datasheet): 35°C 0.95, 40°C 0.91, 45°C 0.86, 50°C 0.82 – enter in column L on 'Cables Sizes'.
Note on J6: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Source: IEC 60364-5-52 Table B.52.10 (PVC 70°C, copper, single-core, method F: 2 loaded touching / 3 loaded trefoil), 30°C air. Typed from standard – VERIFY against SANS 10142-1 Annex / IEC copy. XLPE = these × Fac_XLPE (checks to within ~1% of Table B.52.12).
Note on L6: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Source: h07rn-f-en-50525-2-21-flexible-rubber-cable (1).pdf (Eland Cables H07RN-F technical specification), uploaded 2026-10-28. Uploaded file. CCC: 'Electrical characteristics (4mm2 and above)' 60°C table + 1–2.5mm2 table; F¦3 derived via Fac_Trefoil.
Note on Y6: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Source: BS 7671 Table 4D1B (PVC 70°C single-core copper, impedance z, 1ph 2 cables touching / 3ph trefoil touching). Typed from standard – VERIFY. XLPE uses same values (slightly optimistic at 90°C).
Note on AA6: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Source: h07rn-f-en-50525-2-21-flexible-rubber-cable (1).pdf (Eland Cables H07RN-F technical specification), uploaded 2026-10-28. Uploaded file. Voltage drop table, impedance z at 60°C; 1-core 3ph = 1ph x √3/2 (trefoil).